127 | 2 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 2 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 2 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 2 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 2 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 2 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 2 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 2 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 2 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 2 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 2 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 2 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 2 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 2 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 2 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 2 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 2 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 2 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 2 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 2 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 2 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 2 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 2 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 2 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 2 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 2 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 2 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 2 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 2 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 2 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 2 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 3 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 3 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 3 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 3 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 3 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 3 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 3 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 3 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 3 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 3 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 3 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 3 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 3 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 3 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 3 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 3 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 3 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 3 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 3 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 3 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 3 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 3 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 3 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 3 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 3 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 3 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 3 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 3 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 3 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 3 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 3 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 3 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 3 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 3 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 3 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 3 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 4 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 4 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 4 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 4 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 4 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 4 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 4 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 4 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 4 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 4 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 4 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 4 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 4 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 4 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 4 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 4 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 4 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 4 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 4 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 4 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 4 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 4 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 4 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 4 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 4 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 4 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 4 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 4 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 4 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 4 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 4 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 4 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 4 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 4 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 4 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 4 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 5 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 5 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 5 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 5 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 5 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 5 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 5 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 5 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 5 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 5 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 5 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 5 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 5 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 5 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 5 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 5 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 5 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 5 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 5 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 5 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 5 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 5 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 5 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 5 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 5 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 5 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 5 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 5 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 5 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 5 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 5 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 5 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 5 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 5 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 5 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 5 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 6 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 6 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 6 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 6 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 6 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 6 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 6 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 6 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 6 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 6 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 6 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 6 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 6 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 6 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 6 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 6 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 6 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 6 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 6 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 6 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 6 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 6 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 6 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 6 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 6 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 6 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 6 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 6 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 6 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 6 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 6 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 6 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 6 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 6 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 6 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 6 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 7 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 7 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 7 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 7 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 7 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 7 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 7 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 7 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 7 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 7 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 7 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 7 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 7 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 7 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 7 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 7 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 7 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 7 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 7 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 7 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 7 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 7 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 7 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 7 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 7 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 7 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 7 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 7 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 7 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 7 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 7 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 7 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 7 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 7 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 7 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 7 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 8 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 8 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 8 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 8 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 8 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 8 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 8 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 8 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 8 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 8 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 8 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 8 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 8 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 8 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 8 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 8 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 8 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 8 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 8 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 8 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 8 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 8 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 8 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 8 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 8 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 8 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 8 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 8 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 8 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 8 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 8 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 8 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 8 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 8 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 8 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 8 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 9 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 9 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 9 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 9 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 9 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 9 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 9 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 9 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 9 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 9 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 9 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 9 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 9 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 9 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 9 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 9 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 9 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 9 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 9 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 9 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 9 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 9 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 9 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 9 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 9 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 9 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 9 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 9 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 9 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 9 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 9 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 9 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 9 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 9 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 9 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 9 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 10 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 10 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 10 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 10 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 10 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 10 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 10 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 10 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 10 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 10 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 10 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 10 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 10 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 10 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 10 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 10 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 10 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 10 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 10 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 10 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 10 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 10 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 10 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 10 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 10 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 10 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 10 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 10 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 10 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 10 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 10 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 10 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 10 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 10 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 10 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 10 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 11 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 11 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 11 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 11 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 11 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 11 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 11 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 11 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 11 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 11 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 11 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 11 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 11 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 11 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 11 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 11 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 11 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 11 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 11 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 11 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 11 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 11 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 11 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 11 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 11 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 11 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 11 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 11 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 11 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 11 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 11 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 11 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 11 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 11 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 11 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 11 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 12 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 12 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 12 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 12 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 12 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 12 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 12 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 12 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 12 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 12 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 12 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 12 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 12 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 12 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 12 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 12 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 12 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 12 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 12 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 12 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 12 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 12 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 12 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 12 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 12 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 12 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 12 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 12 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 12 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 12 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 12 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 12 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 12 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 12 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 12 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 12 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 13 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 13 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 13 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 13 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 13 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 13 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 13 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 13 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 13 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 13 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 13 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 13 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 13 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 13 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 13 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 13 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 13 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 13 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 13 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 13 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 13 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 13 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 13 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 13 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 13 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 13 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 13 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 13 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 13 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 13 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 13 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 13 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 13 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 13 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 13 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 13 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 14 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 14 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 14 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 14 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 14 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 14 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 14 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 14 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 14 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 14 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 14 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 14 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 14 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 14 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 14 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 14 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 14 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 14 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 14 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 14 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 14 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 14 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 14 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 14 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 14 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 14 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 14 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 14 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 14 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 14 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 14 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 14 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 14 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 14 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 14 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 14 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 15 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 15 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 15 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 15 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 15 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 15 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 15 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 15 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 15 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 15 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 15 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 15 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 15 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 15 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 15 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 15 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 15 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 15 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 15 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 15 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 15 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 15 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 15 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 15 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 15 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 15 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 15 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 15 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 15 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 15 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 15 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 15 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 15 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 15 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 15 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 15 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 16 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 16 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 16 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 16 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 16 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 16 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 16 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 16 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 16 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 16 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 16 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 16 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 16 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 16 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 16 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 16 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 16 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 16 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 16 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 16 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 16 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 16 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 16 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 16 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 16 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 16 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 16 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 16 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 16 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 16 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 16 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 16 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 16 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 16 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 16 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 16 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 17 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 17 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 17 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 17 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 17 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 17 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 17 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 17 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 17 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 17 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 17 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 17 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 17 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 17 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 17 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 17 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 17 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 17 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 17 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 17 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 17 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 17 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 17 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 17 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 17 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 17 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 17 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 17 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 17 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 17 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 17 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 17 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 17 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 17 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 17 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 17 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 18 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 18 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 18 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 18 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 18 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 18 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 18 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 18 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 18 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 18 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 18 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 18 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 18 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 18 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 18 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 18 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 18 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 18 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 18 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 18 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 18 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 18 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 18 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 18 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 18 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 18 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 18 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 18 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 18 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 18 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 18 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 18 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 18 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 18 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 18 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 18 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 19 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 19 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 19 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 19 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 19 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 19 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 19 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 19 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 19 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 19 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 19 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 19 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 19 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 19 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 19 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 19 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 19 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 19 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 19 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 19 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 19 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 19 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 19 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 19 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 19 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 19 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 19 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 19 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 19 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 19 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 19 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 19 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 19 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 19 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 19 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 19 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 20 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 20 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 20 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 20 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 20 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 20 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 20 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 20 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 20 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 20 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 20 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 20 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 20 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 20 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 20 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 20 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 20 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 20 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 20 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 20 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 20 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 20 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 20 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 20 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 20 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 20 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 20 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 20 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 20 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 20 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 20 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 20 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 20 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 20 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 20 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 20 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 21 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 21 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 21 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 21 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 21 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 21 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 21 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 21 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 21 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 21 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 21 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 21 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 21 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 21 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 21 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 21 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 21 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 21 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 21 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 21 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 21 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 21 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 21 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 21 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 21 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 21 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 21 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 21 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 21 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 21 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 21 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 21 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 21 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 21 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 21 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 21 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 22 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 22 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 22 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 22 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 22 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 22 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 22 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 22 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 22 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 22 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 22 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 22 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 22 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 22 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 22 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 22 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 22 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 22 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 22 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 22 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 22 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 22 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 22 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 22 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 22 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 22 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 22 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 22 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 22 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 22 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 22 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 22 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 22 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 22 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 22 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 22 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 23 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 23 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 23 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 23 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 23 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 23 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 23 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 23 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 23 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 23 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 23 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 23 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 23 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 23 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 23 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 23 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 23 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 23 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 23 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 23 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 23 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 23 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 23 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 23 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 23 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 23 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 23 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 23 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 23 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 23 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 23 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 23 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 23 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 23 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 23 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 23 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 24 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 24 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 24 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 24 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 24 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 24 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 24 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 24 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 24 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 24 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 24 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 24 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 24 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 24 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 24 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 24 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 24 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 24 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 24 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 24 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 24 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 24 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 24 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 24 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 24 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 24 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 24 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 24 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 24 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 24 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 24 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 24 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 24 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 24 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 24 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 24 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
128 | 1 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 1 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 1 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 1 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 1 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 1 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 1 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 16 | No
128 | 1 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 16 | No
128 | 1 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | UINT | R/W | 16 | Yes
128 | 1 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | UINT | R | 16 | Yes
128 | 1 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | REAL | R/W | 16 | Yes
128 | 1 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 16 | Yes
128 | 1 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
128 | 2 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 2 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 2 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 2 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 2 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 2 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 2 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 16 | No
128 | 2 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 16 | No
128 | 2 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | UINT | R/W | 16 | Yes
128 | 2 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | UINT | R | 16 | Yes
128 | 2 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | REAL | R/W | 16 | Yes
128 | 2 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 16 | Yes
128 | 2 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
128 | 3 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 3 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 3 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 3 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 3 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 3 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 3 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 16 | No
128 | 3 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 16 | No
128 | 3 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | UINT | R/W | 16 | Yes
128 | 3 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | UINT | R | 16 | Yes
128 | 3 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | REAL | R/W | 16 | Yes
128 | 3 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 16 | Yes
128 | 3 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
128 | 4 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 4 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 4 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 4 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 4 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 4 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 4 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 16 | No
128 | 4 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 16 | No
128 | 4 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | UINT | R/W | 16 | Yes
128 | 4 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | UINT | R | 16 | Yes
128 | 4 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | REAL | R/W | 16 | Yes
128 | 4 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 16 | Yes
128 | 4 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
128 | 5 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 5 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 5 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 5 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 5 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 5 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 5 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 16 | No
128 | 5 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 16 | No
128 | 5 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | UINT | R/W | 16 | Yes
128 | 5 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | UINT | R | 16 | Yes
128 | 5 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | REAL | R/W | 16 | Yes
128 | 5 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 16 | Yes
128 | 5 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
128 | 6 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 6 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 6 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 6 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 6 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 6 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 6 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 16 | No
128 | 6 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 16 | No
128 | 6 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | UINT | R/W | 16 | Yes
128 | 6 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | UINT | R | 16 | Yes
128 | 6 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | REAL | R/W | 16 | Yes
128 | 6 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 16 | Yes
128 | 6 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
128 | 7 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 7 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 7 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 7 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 7 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 7 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 7 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 16 | No
128 | 7 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 16 | No
128 | 7 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | UINT | R/W | 16 | Yes
128 | 7 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | UINT | R | 16 | Yes
128 | 7 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | REAL | R/W | 16 | Yes
128 | 7 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 16 | Yes
128 | 7 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
128 | 8 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 8 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 8 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 8 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 8 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 8 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 8 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 16 | No
128 | 8 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 16 | No
128 | 8 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | UINT | R/W | 16 | Yes
128 | 8 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | UINT | R | 16 | Yes
128 | 8 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | REAL | R/W | 16 | Yes
128 | 8 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 16 | Yes
128 | 8 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
128 | 9 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 9 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 9 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 9 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 9 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 9 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 9 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 16 | No
128 | 9 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 16 | No
128 | 9 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | UINT | R/W | 16 | Yes
128 | 9 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | UINT | R | 16 | Yes
128 | 9 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | REAL | R/W | 16 | Yes
128 | 9 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 16 | Yes
128 | 9 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
128 | 10 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 10 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 10 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 10 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 10 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 10 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 10 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 16 | No
128 | 10 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 16 | No
128 | 10 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | UINT | R/W | 16 | Yes
128 | 10 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | UINT | R | 16 | Yes
128 | 10 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | REAL | R/W | 16 | Yes
128 | 10 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 16 | Yes
128 | 10 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
128 | 11 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 11 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 11 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 11 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 11 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 11 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 11 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 16 | No
128 | 11 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 16 | No
128 | 11 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | UINT | R/W | 16 | Yes
128 | 11 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | UINT | R | 16 | Yes
128 | 11 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | REAL | R/W | 16 | Yes
128 | 11 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 16 | Yes
128 | 11 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
128 | 12 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 12 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 12 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 12 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 12 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 12 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 12 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 16 | No
128 | 12 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 16 | No
128 | 12 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | UINT | R/W | 16 | Yes
128 | 12 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | UINT | R | 16 | Yes
128 | 12 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | REAL | R/W | 16 | Yes
128 | 12 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 16 | Yes
128 | 12 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
128 | 13 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 13 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 13 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 13 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 13 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 13 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 13 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 16 | No
128 | 13 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 16 | No
128 | 13 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | UINT | R/W | 16 | Yes
128 | 13 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | UINT | R | 16 | Yes
128 | 13 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | REAL | R/W | 16 | Yes
128 | 13 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 16 | Yes
128 | 13 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
128 | 14 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 14 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 14 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 14 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 14 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 14 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 14 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 16 | No
128 | 14 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 16 | No
128 | 14 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | UINT | R/W | 16 | Yes
128 | 14 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | UINT | R | 16 | Yes
128 | 14 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | REAL | R/W | 16 | Yes
128 | 14 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 16 | Yes
128 | 14 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
128 | 15 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 15 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 15 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 15 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 15 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 15 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 15 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 16 | No
128 | 15 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 16 | No
128 | 15 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | UINT | R/W | 16 | Yes
128 | 15 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | UINT | R | 16 | Yes
128 | 15 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | REAL | R/W | 16 | Yes
128 | 15 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 16 | Yes
128 | 15 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
128 | 16 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 16 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 16 | No
128 | 16 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 16 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | USINT | R/W | 16 | No
128 | 16 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 16 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | USINT | R/W | 16 | No
128 | 16 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 16 | No
128 | 16 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 16 | No
128 | 16 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | UINT | R/W | 16 | Yes
128 | 16 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | UINT | R | 16 | Yes
128 | 16 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | REAL | R/W | 16 | Yes
128 | 16 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 16 | Yes
128 | 16 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 1 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 1 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 1 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 1 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 1 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 1 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 1 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 1 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 1 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | UINT | R/W | 16 | Yes
130 | 1 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | UINT | R | 16 | Yes
130 | 1 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | UINT | R/W | 16 | Yes
130 | 1 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
130 | 1 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | UINT | R/W | 16 | Yes
130 | 1 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | UINT | R/W | 16 | Yes
130 | 1 | 15 | Counter | Base | Count | Monitor the count value. |  |  | UINT | R | 16 | Yes
130 | 1 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 1 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | UINT | R/W | 16 | Yes
130 | 2 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 2 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 2 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 2 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 2 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 2 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 2 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 2 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 2 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | UINT | R/W | 16 | Yes
130 | 2 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | UINT | R | 16 | Yes
130 | 2 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | UINT | R/W | 16 | Yes
130 | 2 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
130 | 2 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | UINT | R/W | 16 | Yes
130 | 2 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | UINT | R/W | 16 | Yes
130 | 2 | 15 | Counter | Base | Count | Monitor the count value. |  |  | UINT | R | 16 | Yes
130 | 2 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 2 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | UINT | R/W | 16 | Yes
130 | 3 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 3 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 3 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 3 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 3 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 3 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 3 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 3 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 3 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | UINT | R/W | 16 | Yes
130 | 3 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | UINT | R | 16 | Yes
130 | 3 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | UINT | R/W | 16 | Yes
130 | 3 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
130 | 3 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | UINT | R/W | 16 | Yes
130 | 3 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | UINT | R/W | 16 | Yes
130 | 3 | 15 | Counter | Base | Count | Monitor the count value. |  |  | UINT | R | 16 | Yes
130 | 3 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 3 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | UINT | R/W | 16 | Yes
130 | 4 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 4 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 4 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 4 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 4 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 4 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 4 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 4 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 4 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | UINT | R/W | 16 | Yes
130 | 4 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | UINT | R | 16 | Yes
130 | 4 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | UINT | R/W | 16 | Yes
130 | 4 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
130 | 4 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | UINT | R/W | 16 | Yes
130 | 4 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | UINT | R/W | 16 | Yes
130 | 4 | 15 | Counter | Base | Count | Monitor the count value. |  |  | UINT | R | 16 | Yes
130 | 4 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 4 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | UINT | R/W | 16 | Yes
130 | 5 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 5 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 5 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 5 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 5 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 5 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 5 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 5 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 5 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | UINT | R/W | 16 | Yes
130 | 5 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | UINT | R | 16 | Yes
130 | 5 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | UINT | R/W | 16 | Yes
130 | 5 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
130 | 5 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | UINT | R/W | 16 | Yes
130 | 5 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | UINT | R/W | 16 | Yes
130 | 5 | 15 | Counter | Base | Count | Monitor the count value. |  |  | UINT | R | 16 | Yes
130 | 5 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 5 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | UINT | R/W | 16 | Yes
130 | 6 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 6 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 6 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 6 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 6 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 6 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 6 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 6 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 6 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | UINT | R/W | 16 | Yes
130 | 6 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | UINT | R | 16 | Yes
130 | 6 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | UINT | R/W | 16 | Yes
130 | 6 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
130 | 6 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | UINT | R/W | 16 | Yes
130 | 6 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | UINT | R/W | 16 | Yes
130 | 6 | 15 | Counter | Base | Count | Monitor the count value. |  |  | UINT | R | 16 | Yes
130 | 6 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 6 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | UINT | R/W | 16 | Yes
130 | 7 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 7 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 7 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 7 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 7 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 7 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 7 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 7 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 7 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | UINT | R/W | 16 | Yes
130 | 7 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | UINT | R | 16 | Yes
130 | 7 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | UINT | R/W | 16 | Yes
130 | 7 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
130 | 7 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | UINT | R/W | 16 | Yes
130 | 7 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | UINT | R/W | 16 | Yes
130 | 7 | 15 | Counter | Base | Count | Monitor the count value. |  |  | UINT | R | 16 | Yes
130 | 7 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 7 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | UINT | R/W | 16 | Yes
130 | 8 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 8 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 8 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 8 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 8 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 8 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 8 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 8 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 8 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | UINT | R/W | 16 | Yes
130 | 8 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | UINT | R | 16 | Yes
130 | 8 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | UINT | R/W | 16 | Yes
130 | 8 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
130 | 8 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | UINT | R/W | 16 | Yes
130 | 8 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | UINT | R/W | 16 | Yes
130 | 8 | 15 | Counter | Base | Count | Monitor the count value. |  |  | UINT | R | 16 | Yes
130 | 8 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 8 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | UINT | R/W | 16 | Yes
130 | 9 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 9 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 9 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 9 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 9 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 9 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 9 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 9 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 9 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | UINT | R/W | 16 | Yes
130 | 9 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | UINT | R | 16 | Yes
130 | 9 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | UINT | R/W | 16 | Yes
130 | 9 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
130 | 9 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | UINT | R/W | 16 | Yes
130 | 9 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | UINT | R/W | 16 | Yes
130 | 9 | 15 | Counter | Base | Count | Monitor the count value. |  |  | UINT | R | 16 | Yes
130 | 9 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 9 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | UINT | R/W | 16 | Yes
130 | 10 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 10 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 10 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 10 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 10 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 10 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 10 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 10 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 10 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | UINT | R/W | 16 | Yes
130 | 10 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | UINT | R | 16 | Yes
130 | 10 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | UINT | R/W | 16 | Yes
130 | 10 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
130 | 10 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | UINT | R/W | 16 | Yes
130 | 10 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | UINT | R/W | 16 | Yes
130 | 10 | 15 | Counter | Base | Count | Monitor the count value. |  |  | UINT | R | 16 | Yes
130 | 10 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 10 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | UINT | R/W | 16 | Yes
130 | 11 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 11 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 11 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 11 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 11 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 11 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 11 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 11 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 11 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | UINT | R/W | 16 | Yes
130 | 11 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | UINT | R | 16 | Yes
130 | 11 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | UINT | R/W | 16 | Yes
130 | 11 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
130 | 11 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | UINT | R/W | 16 | Yes
130 | 11 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | UINT | R/W | 16 | Yes
130 | 11 | 15 | Counter | Base | Count | Monitor the count value. |  |  | UINT | R | 16 | Yes
130 | 11 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 11 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | UINT | R/W | 16 | Yes
130 | 12 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 12 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 12 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 12 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 12 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 12 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 12 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 12 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 12 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | UINT | R/W | 16 | Yes
130 | 12 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | UINT | R | 16 | Yes
130 | 12 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | UINT | R/W | 16 | Yes
130 | 12 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
130 | 12 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | UINT | R/W | 16 | Yes
130 | 12 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | UINT | R/W | 16 | Yes
130 | 12 | 15 | Counter | Base | Count | Monitor the count value. |  |  | UINT | R | 16 | Yes
130 | 12 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 12 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | UINT | R/W | 16 | Yes
130 | 13 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 13 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 13 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 13 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 13 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 13 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 13 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 13 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 13 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | UINT | R/W | 16 | Yes
130 | 13 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | UINT | R | 16 | Yes
130 | 13 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | UINT | R/W | 16 | Yes
130 | 13 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
130 | 13 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | UINT | R/W | 16 | Yes
130 | 13 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | UINT | R/W | 16 | Yes
130 | 13 | 15 | Counter | Base | Count | Monitor the count value. |  |  | UINT | R | 16 | Yes
130 | 13 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 13 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | UINT | R/W | 16 | Yes
130 | 14 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 14 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 14 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 14 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 14 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 14 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 14 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 14 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 14 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | UINT | R/W | 16 | Yes
130 | 14 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | UINT | R | 16 | Yes
130 | 14 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | UINT | R/W | 16 | Yes
130 | 14 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
130 | 14 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | UINT | R/W | 16 | Yes
130 | 14 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | UINT | R/W | 16 | Yes
130 | 14 | 15 | Counter | Base | Count | Monitor the count value. |  |  | UINT | R | 16 | Yes
130 | 14 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 14 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | UINT | R/W | 16 | Yes
130 | 15 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 15 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 15 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 15 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 15 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 15 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 15 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 15 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 15 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | UINT | R/W | 16 | Yes
130 | 15 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | UINT | R | 16 | Yes
130 | 15 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | UINT | R/W | 16 | Yes
130 | 15 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
130 | 15 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | UINT | R/W | 16 | Yes
130 | 15 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | UINT | R/W | 16 | Yes
130 | 15 | 15 | Counter | Base | Count | Monitor the count value. |  |  | UINT | R | 16 | Yes
130 | 15 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 15 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | UINT | R/W | 16 | Yes
130 | 16 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 16 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
130 | 16 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 16 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | USINT | R/W | 16 | No
130 | 16 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 16 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | USINT | R/W | 16 | No
130 | 16 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 16 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | UINT | R | 16 | No
130 | 16 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | UINT | R/W | 16 | Yes
130 | 16 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | UINT | R | 16 | Yes
130 | 16 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | UINT | R/W | 16 | Yes
130 | 16 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
130 | 16 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | UINT | R/W | 16 | Yes
130 | 16 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | UINT | R/W | 16 | Yes
130 | 16 | 15 | Counter | Base | Count | Monitor the count value. |  |  | UINT | R | 16 | Yes
130 | 16 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
130 | 16 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | UINT | R/W | 16 | Yes
131 | 1 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 1 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 1 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 1 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 1 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 1 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 1 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 1 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 1 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | UINT | R/W | 16 | Yes
131 | 1 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | UINT | R | 16 | Yes
131 | 1 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 1 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 1 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | REAL | R/W | 16 | Yes
131 | 1 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 1 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 1 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | REAL | R | 16 | Yes
131 | 1 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 1 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
131 | 2 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 2 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 2 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 2 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 2 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 2 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 2 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 2 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 2 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | UINT | R/W | 16 | Yes
131 | 2 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | UINT | R | 16 | Yes
131 | 2 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 2 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 2 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | REAL | R/W | 16 | Yes
131 | 2 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 2 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 2 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | REAL | R | 16 | Yes
131 | 2 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 2 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
131 | 3 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 3 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 3 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 3 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 3 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 3 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 3 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 3 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 3 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | UINT | R/W | 16 | Yes
131 | 3 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | UINT | R | 16 | Yes
131 | 3 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 3 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 3 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | REAL | R/W | 16 | Yes
131 | 3 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 3 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 3 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | REAL | R | 16 | Yes
131 | 3 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 3 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
131 | 4 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 4 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 4 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 4 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 4 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 4 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 4 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 4 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 4 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | UINT | R/W | 16 | Yes
131 | 4 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | UINT | R | 16 | Yes
131 | 4 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 4 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 4 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | REAL | R/W | 16 | Yes
131 | 4 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 4 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 4 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | REAL | R | 16 | Yes
131 | 4 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 4 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
131 | 5 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 5 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 5 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 5 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 5 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 5 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 5 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 5 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 5 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | UINT | R/W | 16 | Yes
131 | 5 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | UINT | R | 16 | Yes
131 | 5 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 5 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 5 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | REAL | R/W | 16 | Yes
131 | 5 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 5 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 5 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | REAL | R | 16 | Yes
131 | 5 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 5 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
131 | 6 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 6 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 6 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 6 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 6 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 6 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 6 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 6 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 6 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | UINT | R/W | 16 | Yes
131 | 6 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | UINT | R | 16 | Yes
131 | 6 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 6 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 6 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | REAL | R/W | 16 | Yes
131 | 6 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 6 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 6 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | REAL | R | 16 | Yes
131 | 6 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 6 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
131 | 7 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 7 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 7 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 7 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 7 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 7 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 7 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 7 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 7 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | UINT | R/W | 16 | Yes
131 | 7 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | UINT | R | 16 | Yes
131 | 7 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 7 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 7 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | REAL | R/W | 16 | Yes
131 | 7 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 7 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 7 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | REAL | R | 16 | Yes
131 | 7 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 7 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
131 | 8 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 8 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 8 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 8 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 8 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 8 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 8 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 8 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 8 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | UINT | R/W | 16 | Yes
131 | 8 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | UINT | R | 16 | Yes
131 | 8 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 8 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 8 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | REAL | R/W | 16 | Yes
131 | 8 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 8 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 8 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | REAL | R | 16 | Yes
131 | 8 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 8 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
131 | 9 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 9 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 9 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 9 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 9 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 9 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 9 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 9 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 9 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | UINT | R/W | 16 | Yes
131 | 9 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | UINT | R | 16 | Yes
131 | 9 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 9 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 9 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | REAL | R/W | 16 | Yes
131 | 9 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 9 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 9 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | REAL | R | 16 | Yes
131 | 9 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 9 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
131 | 10 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 10 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 10 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 10 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 10 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 10 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 10 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 10 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 10 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | UINT | R/W | 16 | Yes
131 | 10 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | UINT | R | 16 | Yes
131 | 10 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 10 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 10 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | REAL | R/W | 16 | Yes
131 | 10 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 10 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 10 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | REAL | R | 16 | Yes
131 | 10 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 10 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
131 | 11 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 11 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 11 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 11 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 11 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 11 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 11 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 11 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 11 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | UINT | R/W | 16 | Yes
131 | 11 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | UINT | R | 16 | Yes
131 | 11 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 11 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 11 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | REAL | R/W | 16 | Yes
131 | 11 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 11 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 11 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | REAL | R | 16 | Yes
131 | 11 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 11 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
131 | 12 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 12 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 12 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 12 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 12 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 12 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 12 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 12 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 12 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | UINT | R/W | 16 | Yes
131 | 12 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | UINT | R | 16 | Yes
131 | 12 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 12 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 12 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | REAL | R/W | 16 | Yes
131 | 12 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 12 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 12 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | REAL | R | 16 | Yes
131 | 12 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 12 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
131 | 13 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 13 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 13 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 13 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 13 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 13 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 13 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 13 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 13 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | UINT | R/W | 16 | Yes
131 | 13 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | UINT | R | 16 | Yes
131 | 13 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 13 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 13 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | REAL | R/W | 16 | Yes
131 | 13 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 13 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 13 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | REAL | R | 16 | Yes
131 | 13 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 13 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
131 | 14 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 14 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 14 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 14 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 14 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 14 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 14 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 14 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 14 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | UINT | R/W | 16 | Yes
131 | 14 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | UINT | R | 16 | Yes
131 | 14 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 14 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 14 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | REAL | R/W | 16 | Yes
131 | 14 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 14 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 14 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | REAL | R | 16 | Yes
131 | 14 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 14 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
131 | 15 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 15 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 15 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 15 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 15 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 15 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 15 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 15 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 15 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | UINT | R/W | 16 | Yes
131 | 15 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | UINT | R | 16 | Yes
131 | 15 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 15 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 15 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | REAL | R/W | 16 | Yes
131 | 15 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 15 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 15 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | REAL | R | 16 | Yes
131 | 15 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 15 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
131 | 16 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 16 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 16 | No
131 | 16 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 16 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | USINT | R/W | 16 | No
131 | 16 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 16 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | USINT | R/W | 16 | No
131 | 16 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 16 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | UINT | R | 16 | No
131 | 16 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | UINT | R/W | 16 | Yes
131 | 16 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | UINT | R | 16 | Yes
131 | 16 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 16 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 16 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | REAL | R/W | 16 | Yes
131 | 16 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | UINT | R/W | 16 | Yes
131 | 16 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 16 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | REAL | R | 16 | Yes
131 | 16 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | UINT | R | 16 | No
131 | 16 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 16 | No
134 | 1 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 8 | No
134 | 1 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | USINT | R/W | 8 | No
134 | 1 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | USINT | R/W | 8 | No
134 | 1 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | REAL | R | 8 | No
134 | 1 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | UINT | R/W | 8 | Yes
134 | 1 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 1 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | REAL | R | 8 | Yes
134 | 1 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 1 | 9 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 8 | Yes
134 | 1 | 10 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | REAL | R/W | 8 | Yes
134 | 1 | 11 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | REAL | R/W | 8 | Yes
134 | 1 | 12 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | REAL | R/W | 8 | Yes
134 | 1 | 13 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | REAL | R/W | 8 | Yes
134 | 1 | 14 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | REAL | R/W | 8 | Yes
134 | 1 | 15 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | REAL | R/W | 8 | Yes
134 | 1 | 16 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | REAL | R/W | 8 | Yes
134 | 1 | 17 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | REAL | R/W | 8 | Yes
134 | 1 | 18 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 1 | 19 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 8 | Yes
134 | 1 | 20 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | REAL | R/W | 8 | Yes
134 | 1 | 21 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | REAL | R/W | 8 | Yes
134 | 1 | 22 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | REAL | R/W | 8 | Yes
134 | 1 | 23 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | REAL | R/W | 8 | Yes
134 | 1 | 24 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | REAL | R/W | 8 | Yes
134 | 1 | 25 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | REAL | R/W | 8 | Yes
134 | 1 | 26 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | REAL | R/W | 8 | Yes
134 | 1 | 27 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | REAL | R/W | 8 | Yes
134 | 1 | 28 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 8 | No
134 | 1 | 29 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 8 | Yes
134 | 2 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 8 | No
134 | 2 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | USINT | R/W | 8 | No
134 | 2 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | USINT | R/W | 8 | No
134 | 2 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | REAL | R | 8 | No
134 | 2 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | UINT | R/W | 8 | Yes
134 | 2 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 2 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | REAL | R | 8 | Yes
134 | 2 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 2 | 9 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 8 | Yes
134 | 2 | 10 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | REAL | R/W | 8 | Yes
134 | 2 | 11 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | REAL | R/W | 8 | Yes
134 | 2 | 12 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | REAL | R/W | 8 | Yes
134 | 2 | 13 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | REAL | R/W | 8 | Yes
134 | 2 | 14 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | REAL | R/W | 8 | Yes
134 | 2 | 15 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | REAL | R/W | 8 | Yes
134 | 2 | 16 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | REAL | R/W | 8 | Yes
134 | 2 | 17 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | REAL | R/W | 8 | Yes
134 | 2 | 18 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 2 | 19 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 8 | Yes
134 | 2 | 20 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | REAL | R/W | 8 | Yes
134 | 2 | 21 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | REAL | R/W | 8 | Yes
134 | 2 | 22 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | REAL | R/W | 8 | Yes
134 | 2 | 23 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | REAL | R/W | 8 | Yes
134 | 2 | 24 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | REAL | R/W | 8 | Yes
134 | 2 | 25 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | REAL | R/W | 8 | Yes
134 | 2 | 26 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | REAL | R/W | 8 | Yes
134 | 2 | 27 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | REAL | R/W | 8 | Yes
134 | 2 | 28 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 8 | No
134 | 2 | 29 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 8 | Yes
134 | 3 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 8 | No
134 | 3 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | USINT | R/W | 8 | No
134 | 3 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | USINT | R/W | 8 | No
134 | 3 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | REAL | R | 8 | No
134 | 3 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | UINT | R/W | 8 | Yes
134 | 3 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 3 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | REAL | R | 8 | Yes
134 | 3 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 3 | 9 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 8 | Yes
134 | 3 | 10 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | REAL | R/W | 8 | Yes
134 | 3 | 11 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | REAL | R/W | 8 | Yes
134 | 3 | 12 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | REAL | R/W | 8 | Yes
134 | 3 | 13 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | REAL | R/W | 8 | Yes
134 | 3 | 14 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | REAL | R/W | 8 | Yes
134 | 3 | 15 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | REAL | R/W | 8 | Yes
134 | 3 | 16 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | REAL | R/W | 8 | Yes
134 | 3 | 17 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | REAL | R/W | 8 | Yes
134 | 3 | 18 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 3 | 19 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 8 | Yes
134 | 3 | 20 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | REAL | R/W | 8 | Yes
134 | 3 | 21 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | REAL | R/W | 8 | Yes
134 | 3 | 22 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | REAL | R/W | 8 | Yes
134 | 3 | 23 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | REAL | R/W | 8 | Yes
134 | 3 | 24 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | REAL | R/W | 8 | Yes
134 | 3 | 25 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | REAL | R/W | 8 | Yes
134 | 3 | 26 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | REAL | R/W | 8 | Yes
134 | 3 | 27 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | REAL | R/W | 8 | Yes
134 | 3 | 28 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 8 | No
134 | 3 | 29 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 8 | Yes
134 | 4 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 8 | No
134 | 4 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | USINT | R/W | 8 | No
134 | 4 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | USINT | R/W | 8 | No
134 | 4 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | REAL | R | 8 | No
134 | 4 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | UINT | R/W | 8 | Yes
134 | 4 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 4 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | REAL | R | 8 | Yes
134 | 4 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 4 | 9 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 8 | Yes
134 | 4 | 10 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | REAL | R/W | 8 | Yes
134 | 4 | 11 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | REAL | R/W | 8 | Yes
134 | 4 | 12 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | REAL | R/W | 8 | Yes
134 | 4 | 13 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | REAL | R/W | 8 | Yes
134 | 4 | 14 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | REAL | R/W | 8 | Yes
134 | 4 | 15 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | REAL | R/W | 8 | Yes
134 | 4 | 16 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | REAL | R/W | 8 | Yes
134 | 4 | 17 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | REAL | R/W | 8 | Yes
134 | 4 | 18 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 4 | 19 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 8 | Yes
134 | 4 | 20 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | REAL | R/W | 8 | Yes
134 | 4 | 21 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | REAL | R/W | 8 | Yes
134 | 4 | 22 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | REAL | R/W | 8 | Yes
134 | 4 | 23 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | REAL | R/W | 8 | Yes
134 | 4 | 24 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | REAL | R/W | 8 | Yes
134 | 4 | 25 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | REAL | R/W | 8 | Yes
134 | 4 | 26 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | REAL | R/W | 8 | Yes
134 | 4 | 27 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | REAL | R/W | 8 | Yes
134 | 4 | 28 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 8 | No
134 | 4 | 29 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 8 | Yes
134 | 5 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 8 | No
134 | 5 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | USINT | R/W | 8 | No
134 | 5 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | USINT | R/W | 8 | No
134 | 5 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | REAL | R | 8 | No
134 | 5 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | UINT | R/W | 8 | Yes
134 | 5 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 5 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | REAL | R | 8 | Yes
134 | 5 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 5 | 9 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 8 | Yes
134 | 5 | 10 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | REAL | R/W | 8 | Yes
134 | 5 | 11 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | REAL | R/W | 8 | Yes
134 | 5 | 12 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | REAL | R/W | 8 | Yes
134 | 5 | 13 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | REAL | R/W | 8 | Yes
134 | 5 | 14 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | REAL | R/W | 8 | Yes
134 | 5 | 15 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | REAL | R/W | 8 | Yes
134 | 5 | 16 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | REAL | R/W | 8 | Yes
134 | 5 | 17 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | REAL | R/W | 8 | Yes
134 | 5 | 18 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 5 | 19 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 8 | Yes
134 | 5 | 20 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | REAL | R/W | 8 | Yes
134 | 5 | 21 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | REAL | R/W | 8 | Yes
134 | 5 | 22 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | REAL | R/W | 8 | Yes
134 | 5 | 23 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | REAL | R/W | 8 | Yes
134 | 5 | 24 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | REAL | R/W | 8 | Yes
134 | 5 | 25 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | REAL | R/W | 8 | Yes
134 | 5 | 26 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | REAL | R/W | 8 | Yes
134 | 5 | 27 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | REAL | R/W | 8 | Yes
134 | 5 | 28 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 8 | No
134 | 5 | 29 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 8 | Yes
134 | 6 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 8 | No
134 | 6 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | USINT | R/W | 8 | No
134 | 6 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | USINT | R/W | 8 | No
134 | 6 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | REAL | R | 8 | No
134 | 6 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | UINT | R/W | 8 | Yes
134 | 6 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 6 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | REAL | R | 8 | Yes
134 | 6 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 6 | 9 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 8 | Yes
134 | 6 | 10 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | REAL | R/W | 8 | Yes
134 | 6 | 11 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | REAL | R/W | 8 | Yes
134 | 6 | 12 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | REAL | R/W | 8 | Yes
134 | 6 | 13 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | REAL | R/W | 8 | Yes
134 | 6 | 14 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | REAL | R/W | 8 | Yes
134 | 6 | 15 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | REAL | R/W | 8 | Yes
134 | 6 | 16 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | REAL | R/W | 8 | Yes
134 | 6 | 17 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | REAL | R/W | 8 | Yes
134 | 6 | 18 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 6 | 19 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 8 | Yes
134 | 6 | 20 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | REAL | R/W | 8 | Yes
134 | 6 | 21 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | REAL | R/W | 8 | Yes
134 | 6 | 22 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | REAL | R/W | 8 | Yes
134 | 6 | 23 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | REAL | R/W | 8 | Yes
134 | 6 | 24 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | REAL | R/W | 8 | Yes
134 | 6 | 25 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | REAL | R/W | 8 | Yes
134 | 6 | 26 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | REAL | R/W | 8 | Yes
134 | 6 | 27 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | REAL | R/W | 8 | Yes
134 | 6 | 28 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 8 | No
134 | 6 | 29 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 8 | Yes
134 | 7 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 8 | No
134 | 7 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | USINT | R/W | 8 | No
134 | 7 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | USINT | R/W | 8 | No
134 | 7 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | REAL | R | 8 | No
134 | 7 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | UINT | R/W | 8 | Yes
134 | 7 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 7 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | REAL | R | 8 | Yes
134 | 7 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 7 | 9 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 8 | Yes
134 | 7 | 10 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | REAL | R/W | 8 | Yes
134 | 7 | 11 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | REAL | R/W | 8 | Yes
134 | 7 | 12 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | REAL | R/W | 8 | Yes
134 | 7 | 13 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | REAL | R/W | 8 | Yes
134 | 7 | 14 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | REAL | R/W | 8 | Yes
134 | 7 | 15 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | REAL | R/W | 8 | Yes
134 | 7 | 16 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | REAL | R/W | 8 | Yes
134 | 7 | 17 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | REAL | R/W | 8 | Yes
134 | 7 | 18 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 7 | 19 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 8 | Yes
134 | 7 | 20 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | REAL | R/W | 8 | Yes
134 | 7 | 21 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | REAL | R/W | 8 | Yes
134 | 7 | 22 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | REAL | R/W | 8 | Yes
134 | 7 | 23 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | REAL | R/W | 8 | Yes
134 | 7 | 24 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | REAL | R/W | 8 | Yes
134 | 7 | 25 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | REAL | R/W | 8 | Yes
134 | 7 | 26 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | REAL | R/W | 8 | Yes
134 | 7 | 27 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | REAL | R/W | 8 | Yes
134 | 7 | 28 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 8 | No
134 | 7 | 29 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 8 | Yes
134 | 8 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 8 | No
134 | 8 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | USINT | R/W | 8 | No
134 | 8 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | USINT | R/W | 8 | No
134 | 8 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | REAL | R | 8 | No
134 | 8 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | UINT | R/W | 8 | Yes
134 | 8 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 8 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | REAL | R | 8 | Yes
134 | 8 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 8 | 9 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 8 | Yes
134 | 8 | 10 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | REAL | R/W | 8 | Yes
134 | 8 | 11 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | REAL | R/W | 8 | Yes
134 | 8 | 12 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | REAL | R/W | 8 | Yes
134 | 8 | 13 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | REAL | R/W | 8 | Yes
134 | 8 | 14 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | REAL | R/W | 8 | Yes
134 | 8 | 15 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | REAL | R/W | 8 | Yes
134 | 8 | 16 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | REAL | R/W | 8 | Yes
134 | 8 | 17 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | REAL | R/W | 8 | Yes
134 | 8 | 18 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
134 | 8 | 19 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 8 | Yes
134 | 8 | 20 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | REAL | R/W | 8 | Yes
134 | 8 | 21 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | REAL | R/W | 8 | Yes
134 | 8 | 22 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | REAL | R/W | 8 | Yes
134 | 8 | 23 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | REAL | R/W | 8 | Yes
134 | 8 | 24 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | REAL | R/W | 8 | Yes
134 | 8 | 25 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | REAL | R/W | 8 | Yes
134 | 8 | 26 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | REAL | R/W | 8 | Yes
134 | 8 | 27 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | REAL | R/W | 8 | Yes
134 | 8 | 28 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 8 | No
134 | 8 | 29 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 8 | Yes
135 | 1 | 1 | Function | Base | Source Function A | Set the Source A for the receiver in the Special Output Function block. | None (61), Analog Input (142), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | UINT | R/W | 4 | No
135 | 1 | 2 | Function | Base | Source Function B | Set the Source B for the receiver in the Special Output Function block. | None (61), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | UINT | R/W | 4 | No
135 | 1 | 3 | Function | Base | Source Instance A | Set the Source Instance A for the receiver in the Special Output Function block. | 1 to 250 | 1 | USINT | R/W | 4 | No
135 | 1 | 4 | Function | Base | Source Instance B | Set the Source Instance B for the receiver in the Special Output Function block. | 1 to 250 | 1 | USINT | R/W | 4 | No
135 | 1 | 5 | Function | Base | Source Zone A | Set the Source Zone A for the receiver in the Special Output Function block. | 0 to 24 | 0 | USINT | R/W | 4 | No
135 | 1 | 6 | Function | Base | Source Zone B | Set the Source Zone B for the receiver in the Special Output Function block. | 0 to 24 | 0 | USINT | R/W | 4 | No
135 | 1 | 7 | Function | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 4 | No
135 | 1 | 8 | Function | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 4 | No
135 | 1 | 9 | Function | Base | Function | Set the Special Output Function block's purpose. | Off (62), Compressor Control (1506), Sequencer (1507), Motorized Valve (1508) | Off (62) | UINT | R/W | 4 | Yes
135 | 1 | 10 | Function | Base | Output Value 1 | Monitor the output value of the Special Output Function block transmitter 1. |  |  | REAL | R | 4 | Yes
135 | 1 | 11 | Function | Base | Error | Monitor the error status for transmitter 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
135 | 1 | 12 | Function | Base | Output Value 2 | Monitor the output value of the Special Output Function block transmitter 2. |  |  | REAL | R | 4 | Yes
135 | 1 | 13 | Function | Base | Error | Monitor the error status for transmitter 2. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
135 | 1 | 14 | Function | Base | Output Value 3 | Monitor the output value of the Special Output Function block transmitter 3. |  |  | REAL | R | 4 | Yes
135 | 1 | 15 | Function | Base | Error | Monitor the error status for transmitter 3. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
135 | 1 | 16 | Function | Base | Output Value 4 | Monitor the output value of the Special Output Function block transmitter 4. |  |  | REAL | R | 4 | Yes
135 | 1 | 17 | Function | Base | Error | Monitor the error status for transmitter 4. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
135 | 1 | 18 | Function | Base | Input A Turn On | Set the value of the signal at receiver A that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | REAL | R/W | 4 | Yes
135 | 1 | 19 | Function | Base | Input A Turn Off | Set the value of the signal at receiver A that indicates there is no demand for the compressor to be on. | -100.00 to 100.00 | 5.0 | REAL | R/W | 4 | Yes
135 | 1 | 20 | Function | Base | Input B Turn On | Set the value of the signal at receiver B that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | REAL | R/W | 4 | Yes
135 | 1 | 21 | Function | Base | Input B Turn Off | Set the value of the signal at receiver B that indicates there is no demand for the compressor | -100.00 to 100.00 | 5.0 | REAL | R/W | 4 | Yes
135 | 1 | 22 | Function | Base | Minimum On Time | Set the minimum amount of time the compressor must be on before it can be turned off again. | 0 to 9,999 | 20 | UINT | R/W | 4 | Yes
135 | 1 | 23 | Function | Base | Minimum Off Time | Set the minimum amount of time the compressor is kept off before it can be turned on again. | 0 to 9,999 | 20 | UINT | R/W | 4 | Yes
135 | 1 | 24 | Function | Base | Valve Travel Time | Set when used for motorized valve the time the valve takes to travel between fully closed and fully open. | 10 to 9,999 | 120 | UINT | R/W | 4 | Yes
135 | 1 | 25 | Function | Base | Dead Band | Set when used for motorized valve the minimum amount for a single adjustment to the valve position. | 1.0 to 100.0 | 2.0 | REAL | R/W | 4 | Yes
135 | 1 | 26 | Function | Base | Time Delay | Set when used for sequencer control minimum amount of time to wait between turning on one on-off output and the next. | 0 to 9,999 | 0 | UINT | R/W | 4 | Yes
135 | 1 | 27 | Function | Base | Output Order | Set when sequencer the method by which outputs 2, 3 and 4 are sequenced. | Linear (1509), Progressive (1510) | Linear (1509) | UINT | R/W | 4 | Yes
135 | 1 | 28 | Function | Base | Output 1 Size | Set when sequencer the proportion of the total power that is controlled by the proportional (vernier) output. | 0 to 99,999.0 | 10.0 | REAL | R/W | 4 | Yes
135 | 1 | 29 | Function | Base | Output 2 Size | Set when sequencer the proportion of the total power that is switched by on-off output 2. | 0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
135 | 1 | 30 | Function | Base | Output 3 Size | Set when sequencer the proportion of the total power that is switched by on-off output 3. | 0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
135 | 1 | 31 | Function | Base | Output 4 Size | Set when sequencer the proportion of the total power that is switched by on-off output 4. | 0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
135 | 1 | 32 | Function | Base | Value | Monitor the Special Output Function value. | 0.000 to 100.000 |  | REAL | R | 4 | Yes
135 | 1 | 35 | Function | Base | Off Delay | Set when used for compressor control an amount of time the output signal remains on after the Minimum On Time is satisfied and the signals at A and B indicate the compressor is no longer needed. | 0 to 9,999 | 0 | UINT | R/W | 4 | Yes
135 | 2 | 1 | Function | Base | Source Function A | Set the Source A for the receiver in the Special Output Function block. | None (61), Analog Input (142), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | UINT | R/W | 4 | No
135 | 2 | 2 | Function | Base | Source Function B | Set the Source B for the receiver in the Special Output Function block. | None (61), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | UINT | R/W | 4 | No
135 | 2 | 3 | Function | Base | Source Instance A | Set the Source Instance A for the receiver in the Special Output Function block. | 1 to 250 | 1 | USINT | R/W | 4 | No
135 | 2 | 4 | Function | Base | Source Instance B | Set the Source Instance B for the receiver in the Special Output Function block. | 1 to 250 | 1 | USINT | R/W | 4 | No
135 | 2 | 5 | Function | Base | Source Zone A | Set the Source Zone A for the receiver in the Special Output Function block. | 0 to 24 | 0 | USINT | R/W | 4 | No
135 | 2 | 6 | Function | Base | Source Zone B | Set the Source Zone B for the receiver in the Special Output Function block. | 0 to 24 | 0 | USINT | R/W | 4 | No
135 | 2 | 7 | Function | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 4 | No
135 | 2 | 8 | Function | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 4 | No
135 | 2 | 9 | Function | Base | Function | Set the Special Output Function block's purpose. | Off (62), Compressor Control (1506), Sequencer (1507), Motorized Valve (1508) | Off (62) | UINT | R/W | 4 | Yes
135 | 2 | 10 | Function | Base | Output Value 1 | Monitor the output value of the Special Output Function block transmitter 1. |  |  | REAL | R | 4 | Yes
135 | 2 | 11 | Function | Base | Error | Monitor the error status for transmitter 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
135 | 2 | 12 | Function | Base | Output Value 2 | Monitor the output value of the Special Output Function block transmitter 2. |  |  | REAL | R | 4 | Yes
135 | 2 | 13 | Function | Base | Error | Monitor the error status for transmitter 2. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
135 | 2 | 14 | Function | Base | Output Value 3 | Monitor the output value of the Special Output Function block transmitter 3. |  |  | REAL | R | 4 | Yes
135 | 2 | 15 | Function | Base | Error | Monitor the error status for transmitter 3. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
135 | 2 | 16 | Function | Base | Output Value 4 | Monitor the output value of the Special Output Function block transmitter 4. |  |  | REAL | R | 4 | Yes
135 | 2 | 17 | Function | Base | Error | Monitor the error status for transmitter 4. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
135 | 2 | 18 | Function | Base | Input A Turn On | Set the value of the signal at receiver A that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | REAL | R/W | 4 | Yes
135 | 2 | 19 | Function | Base | Input A Turn Off | Set the value of the signal at receiver A that indicates there is no demand for the compressor to be on. | -100.00 to 100.00 | 5.0 | REAL | R/W | 4 | Yes
135 | 2 | 20 | Function | Base | Input B Turn On | Set the value of the signal at receiver B that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | REAL | R/W | 4 | Yes
135 | 2 | 21 | Function | Base | Input B Turn Off | Set the value of the signal at receiver B that indicates there is no demand for the compressor | -100.00 to 100.00 | 5.0 | REAL | R/W | 4 | Yes
135 | 2 | 22 | Function | Base | Minimum On Time | Set the minimum amount of time the compressor must be on before it can be turned off again. | 0 to 9,999 | 20 | UINT | R/W | 4 | Yes
135 | 2 | 23 | Function | Base | Minimum Off Time | Set the minimum amount of time the compressor is kept off before it can be turned on again. | 0 to 9,999 | 20 | UINT | R/W | 4 | Yes
135 | 2 | 24 | Function | Base | Valve Travel Time | Set when used for motorized valve the time the valve takes to travel between fully closed and fully open. | 10 to 9,999 | 120 | UINT | R/W | 4 | Yes
135 | 2 | 25 | Function | Base | Dead Band | Set when used for motorized valve the minimum amount for a single adjustment to the valve position. | 1.0 to 100.0 | 2.0 | REAL | R/W | 4 | Yes
135 | 2 | 26 | Function | Base | Time Delay | Set when used for sequencer control minimum amount of time to wait between turning on one on-off output and the next. | 0 to 9,999 | 0 | UINT | R/W | 4 | Yes
135 | 2 | 27 | Function | Base | Output Order | Set when sequencer the method by which outputs 2, 3 and 4 are sequenced. | Linear (1509), Progressive (1510) | Linear (1509) | UINT | R/W | 4 | Yes
135 | 2 | 28 | Function | Base | Output 1 Size | Set when sequencer the proportion of the total power that is controlled by the proportional (vernier) output. | 0 to 99,999.0 | 10.0 | REAL | R/W | 4 | Yes
135 | 2 | 29 | Function | Base | Output 2 Size | Set when sequencer the proportion of the total power that is switched by on-off output 2. | 0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
135 | 2 | 30 | Function | Base | Output 3 Size | Set when sequencer the proportion of the total power that is switched by on-off output 3. | 0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
135 | 2 | 31 | Function | Base | Output 4 Size | Set when sequencer the proportion of the total power that is switched by on-off output 4. | 0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
135 | 2 | 32 | Function | Base | Value | Monitor the Special Output Function value. | 0.000 to 100.000 |  | REAL | R | 4 | Yes
135 | 2 | 35 | Function | Base | Off Delay | Set when used for compressor control an amount of time the output signal remains on after the Minimum On Time is satisfied and the signals at A and B indicate the compressor is no longer needed. | 0 to 9,999 | 0 | UINT | R/W | 4 | Yes
135 | 3 | 1 | Function | Base | Source Function A | Set the Source A for the receiver in the Special Output Function block. | None (61), Analog Input (142), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | UINT | R/W | 4 | No
135 | 3 | 2 | Function | Base | Source Function B | Set the Source B for the receiver in the Special Output Function block. | None (61), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | UINT | R/W | 4 | No
135 | 3 | 3 | Function | Base | Source Instance A | Set the Source Instance A for the receiver in the Special Output Function block. | 1 to 250 | 1 | USINT | R/W | 4 | No
135 | 3 | 4 | Function | Base | Source Instance B | Set the Source Instance B for the receiver in the Special Output Function block. | 1 to 250 | 1 | USINT | R/W | 4 | No
135 | 3 | 5 | Function | Base | Source Zone A | Set the Source Zone A for the receiver in the Special Output Function block. | 0 to 24 | 0 | USINT | R/W | 4 | No
135 | 3 | 6 | Function | Base | Source Zone B | Set the Source Zone B for the receiver in the Special Output Function block. | 0 to 24 | 0 | USINT | R/W | 4 | No
135 | 3 | 7 | Function | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 4 | No
135 | 3 | 8 | Function | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 4 | No
135 | 3 | 9 | Function | Base | Function | Set the Special Output Function block's purpose. | Off (62), Compressor Control (1506), Sequencer (1507), Motorized Valve (1508) | Off (62) | UINT | R/W | 4 | Yes
135 | 3 | 10 | Function | Base | Output Value 1 | Monitor the output value of the Special Output Function block transmitter 1. |  |  | REAL | R | 4 | Yes
135 | 3 | 11 | Function | Base | Error | Monitor the error status for transmitter 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
135 | 3 | 12 | Function | Base | Output Value 2 | Monitor the output value of the Special Output Function block transmitter 2. |  |  | REAL | R | 4 | Yes
135 | 3 | 13 | Function | Base | Error | Monitor the error status for transmitter 2. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
135 | 3 | 14 | Function | Base | Output Value 3 | Monitor the output value of the Special Output Function block transmitter 3. |  |  | REAL | R | 4 | Yes
135 | 3 | 15 | Function | Base | Error | Monitor the error status for transmitter 3. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
135 | 3 | 16 | Function | Base | Output Value 4 | Monitor the output value of the Special Output Function block transmitter 4. |  |  | REAL | R | 4 | Yes
135 | 3 | 17 | Function | Base | Error | Monitor the error status for transmitter 4. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
135 | 3 | 18 | Function | Base | Input A Turn On | Set the value of the signal at receiver A that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | REAL | R/W | 4 | Yes
135 | 3 | 19 | Function | Base | Input A Turn Off | Set the value of the signal at receiver A that indicates there is no demand for the compressor to be on. | -100.00 to 100.00 | 5.0 | REAL | R/W | 4 | Yes
135 | 3 | 20 | Function | Base | Input B Turn On | Set the value of the signal at receiver B that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | REAL | R/W | 4 | Yes
135 | 3 | 21 | Function | Base | Input B Turn Off | Set the value of the signal at receiver B that indicates there is no demand for the compressor | -100.00 to 100.00 | 5.0 | REAL | R/W | 4 | Yes
135 | 3 | 22 | Function | Base | Minimum On Time | Set the minimum amount of time the compressor must be on before it can be turned off again. | 0 to 9,999 | 20 | UINT | R/W | 4 | Yes
135 | 3 | 23 | Function | Base | Minimum Off Time | Set the minimum amount of time the compressor is kept off before it can be turned on again. | 0 to 9,999 | 20 | UINT | R/W | 4 | Yes
135 | 3 | 24 | Function | Base | Valve Travel Time | Set when used for motorized valve the time the valve takes to travel between fully closed and fully open. | 10 to 9,999 | 120 | UINT | R/W | 4 | Yes
135 | 3 | 25 | Function | Base | Dead Band | Set when used for motorized valve the minimum amount for a single adjustment to the valve position. | 1.0 to 100.0 | 2.0 | REAL | R/W | 4 | Yes
135 | 3 | 26 | Function | Base | Time Delay | Set when used for sequencer control minimum amount of time to wait between turning on one on-off output and the next. | 0 to 9,999 | 0 | UINT | R/W | 4 | Yes
135 | 3 | 27 | Function | Base | Output Order | Set when sequencer the method by which outputs 2, 3 and 4 are sequenced. | Linear (1509), Progressive (1510) | Linear (1509) | UINT | R/W | 4 | Yes
135 | 3 | 28 | Function | Base | Output 1 Size | Set when sequencer the proportion of the total power that is controlled by the proportional (vernier) output. | 0 to 99,999.0 | 10.0 | REAL | R/W | 4 | Yes
135 | 3 | 29 | Function | Base | Output 2 Size | Set when sequencer the proportion of the total power that is switched by on-off output 2. | 0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
135 | 3 | 30 | Function | Base | Output 3 Size | Set when sequencer the proportion of the total power that is switched by on-off output 3. | 0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
135 | 3 | 31 | Function | Base | Output 4 Size | Set when sequencer the proportion of the total power that is switched by on-off output 4. | 0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
135 | 3 | 32 | Function | Base | Value | Monitor the Special Output Function value. | 0.000 to 100.000 |  | REAL | R | 4 | Yes
135 | 3 | 35 | Function | Base | Off Delay | Set when used for compressor control an amount of time the output signal remains on after the Minimum On Time is satisfied and the signals at A and B indicate the compressor is no longer needed. | 0 to 9,999 | 0 | UINT | R/W | 4 | Yes
135 | 4 | 1 | Function | Base | Source Function A | Set the Source A for the receiver in the Special Output Function block. | None (61), Analog Input (142), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | UINT | R/W | 4 | No
135 | 4 | 2 | Function | Base | Source Function B | Set the Source B for the receiver in the Special Output Function block. | None (61), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | UINT | R/W | 4 | No
135 | 4 | 3 | Function | Base | Source Instance A | Set the Source Instance A for the receiver in the Special Output Function block. | 1 to 250 | 1 | USINT | R/W | 4 | No
135 | 4 | 4 | Function | Base | Source Instance B | Set the Source Instance B for the receiver in the Special Output Function block. | 1 to 250 | 1 | USINT | R/W | 4 | No
135 | 4 | 5 | Function | Base | Source Zone A | Set the Source Zone A for the receiver in the Special Output Function block. | 0 to 24 | 0 | USINT | R/W | 4 | No
135 | 4 | 6 | Function | Base | Source Zone B | Set the Source Zone B for the receiver in the Special Output Function block. | 0 to 24 | 0 | USINT | R/W | 4 | No
135 | 4 | 7 | Function | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 4 | No
135 | 4 | 8 | Function | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 4 | No
135 | 4 | 9 | Function | Base | Function | Set the Special Output Function block's purpose. | Off (62), Compressor Control (1506), Sequencer (1507), Motorized Valve (1508) | Off (62) | UINT | R/W | 4 | Yes
135 | 4 | 10 | Function | Base | Output Value 1 | Monitor the output value of the Special Output Function block transmitter 1. |  |  | REAL | R | 4 | Yes
135 | 4 | 11 | Function | Base | Error | Monitor the error status for transmitter 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
135 | 4 | 12 | Function | Base | Output Value 2 | Monitor the output value of the Special Output Function block transmitter 2. |  |  | REAL | R | 4 | Yes
135 | 4 | 13 | Function | Base | Error | Monitor the error status for transmitter 2. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
135 | 4 | 14 | Function | Base | Output Value 3 | Monitor the output value of the Special Output Function block transmitter 3. |  |  | REAL | R | 4 | Yes
135 | 4 | 15 | Function | Base | Error | Monitor the error status for transmitter 3. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
135 | 4 | 16 | Function | Base | Output Value 4 | Monitor the output value of the Special Output Function block transmitter 4. |  |  | REAL | R | 4 | Yes
135 | 4 | 17 | Function | Base | Error | Monitor the error status for transmitter 4. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
135 | 4 | 18 | Function | Base | Input A Turn On | Set the value of the signal at receiver A that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | REAL | R/W | 4 | Yes
135 | 4 | 19 | Function | Base | Input A Turn Off | Set the value of the signal at receiver A that indicates there is no demand for the compressor to be on. | -100.00 to 100.00 | 5.0 | REAL | R/W | 4 | Yes
135 | 4 | 20 | Function | Base | Input B Turn On | Set the value of the signal at receiver B that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | REAL | R/W | 4 | Yes
135 | 4 | 21 | Function | Base | Input B Turn Off | Set the value of the signal at receiver B that indicates there is no demand for the compressor | -100.00 to 100.00 | 5.0 | REAL | R/W | 4 | Yes
135 | 4 | 22 | Function | Base | Minimum On Time | Set the minimum amount of time the compressor must be on before it can be turned off again. | 0 to 9,999 | 20 | UINT | R/W | 4 | Yes
135 | 4 | 23 | Function | Base | Minimum Off Time | Set the minimum amount of time the compressor is kept off before it can be turned on again. | 0 to 9,999 | 20 | UINT | R/W | 4 | Yes
135 | 4 | 24 | Function | Base | Valve Travel Time | Set when used for motorized valve the time the valve takes to travel between fully closed and fully open. | 10 to 9,999 | 120 | UINT | R/W | 4 | Yes
135 | 4 | 25 | Function | Base | Dead Band | Set when used for motorized valve the minimum amount for a single adjustment to the valve position. | 1.0 to 100.0 | 2.0 | REAL | R/W | 4 | Yes
135 | 4 | 26 | Function | Base | Time Delay | Set when used for sequencer control minimum amount of time to wait between turning on one on-off output and the next. | 0 to 9,999 | 0 | UINT | R/W | 4 | Yes
135 | 4 | 27 | Function | Base | Output Order | Set when sequencer the method by which outputs 2, 3 and 4 are sequenced. | Linear (1509), Progressive (1510) | Linear (1509) | UINT | R/W | 4 | Yes
135 | 4 | 28 | Function | Base | Output 1 Size | Set when sequencer the proportion of the total power that is controlled by the proportional (vernier) output. | 0 to 99,999.0 | 10.0 | REAL | R/W | 4 | Yes
135 | 4 | 29 | Function | Base | Output 2 Size | Set when sequencer the proportion of the total power that is switched by on-off output 2. | 0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
135 | 4 | 30 | Function | Base | Output 3 Size | Set when sequencer the proportion of the total power that is switched by on-off output 3. | 0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
135 | 4 | 31 | Function | Base | Output 4 Size | Set when sequencer the proportion of the total power that is switched by on-off output 4. | 0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
135 | 4 | 32 | Function | Base | Value | Monitor the Special Output Function value. | 0.000 to 100.000 |  | REAL | R | 4 | Yes
135 | 4 | 35 | Function | Base | Off Delay | Set when used for compressor control an amount of time the output signal remains on after the Minimum On Time is satisfied and the signals at A and B indicate the compressor is no longer needed. | 0 to 9,999 | 0 | UINT | R/W | 4 | Yes
136 | 1 | 1 | Real Time Clock | Base | Time of Day | Monitor the time of day in seconds. | 0 to 86,399 |  | UDINT | R | 1 | No
136 | 1 | 3 | Real Time Clock | Base | Hours | Set the time of day (hours portion). | 0 to 23 |  | USINT | R/W | 1 | No
136 | 1 | 4 | Real Time Clock | Base | Minutes | Set the time of day (minutes portion). | 0 to 59 |  | USINT | R/W | 1 | No
136 | 1 | 5 | Real Time Clock | Base | Seconds | Set the time of day (seconds portion). | 0 to 59 |  | USINT | R/W | 1 | No
136 | 1 | 6 | Real Time Clock | Base | Month | Set the time of day (month portion). | 1 to 12 |  | USINT | R/W | 1 | No
136 | 1 | 7 | Real Time Clock | Base | Date | Set the time of day (date portion). | 1 to 31 |  | USINT | R/W | 1 | No
136 | 1 | 8 | Real Time Clock | Base | Year | Set the time of day (year portion). | 2,008 to 2,100 |  | UINT | R/W | 1 | No
136 | 1 | 17 | Real Time Clock | Base | Time Zone |  | -14 to 14 | 0 | SINT | R/W | 1 | No
136 | 1 | 20 | Real Time Clock | Base | Time Zone Minutes |  | 0 to 59 | 0 | USINT | R/W | 1 | No
137 | 1 | 3 | Data Logging | Base | Memory Full Action | Set action to take when memory is full. | Stop (1638), Overwrite (1639) | Stop (1638) | UINT | R/W | 1 | No
137 | 1 | 4 | Data Logging | Base | Available Logging Memory (MB) | Monitor the available memory usable for datalogging. | 0 to 4,294,967,295 |  | UDINT | R | 1 | No
137 | 1 | 5 | Data Logging | Base | Available Logging Time (Hours) | Monitor the time remaining before memory is full. | 0 to 4,294,967,295 |  | UDINT | R | 1 | No
137 | 1 | 6 | Data Logging | Base | Source Function A | Set source to trigger logging action. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 1 | No
137 | 1 | 7 | Data Logging | Base | Source Instance A | Set source instance to trigger logging action. | 1 to 24 | 1 | USINT | R/W | 1 | No
137 | 1 | 9 | Data Logging | Base | Source Value A | Monitor state of trigger for logging action. | Off (62), On (63) |  | UINT | R | 1 | No
137 | 1 | 12 | Data Logging | Base | Logging Status | Monitor data log action. | Recording (1990), Not Recording (1991) | Not Recording (1991) | UINT | R | 1 | No
137 | 1 | 14 | Data Logging | Base | File Size Limit (MB) | Set size of data log file. | 1 to 4,294,967,295 | 0 | UDINT | R/W | 1 | No
137 | 1 | 19 | Data Logging | Base | Date Format | Set date format recorded on each record. | MM/DD/YYYY (1631), DD/MM/YYYY (1632) | MM/DD/YYYY (1631) | UINT | R/W | 1 | No
137 | 1 | 20 | Data Logging | Base | Time Format | Set time format recorded on each record. | 12 Hour (1966), 24 Hour (1967) | 12 Hour (1966) | UINT | R/W | 1 | No
137 | 1 | 21 | Data Logging | Base | Log Action | Set data log action. | None (61), Start (1782), Stop (1638) |  | UINT | R/W | 1 | No
137 | 1 | 22 | Data Logging | Base | Log Interval | Set the interval at which to log data. | 0.1 sec (1971), 0.2 sec (1972), 0.5 sec (1973), 1 sec (1974), 2 sec (1975), 5 sec (1976), 10 sec (1977), 15 sec (1978), 30 sec (1979), 1 min (1980), 2 min (1985), 5 min (1981), 10 min (1986), 15 min (1987), 30 min (1988), 60 min (1989) | 5 min (1981) | UINT | R/W | 1 | No
137 | 1 | 23 | Data Logging | Base | Log To | Set location to store the data log file. | Internal (2057), USB Device (2058) | Internal (2057) | UINT | R/W | 1 | No
137 | 1 | 24 | Data Logging | Base | File Type | Set file type of the data log file. | Encrypted (2064), CSV (2063), Both (13) | Encrypted (2064) | UINT | R/W | 1 | No
137 | 1 | 25 | Data Logging | Base | Create Encrypted |  | No (59), Yes (106) | No (59) | UINT | R/W | 1 | No
137 | 1 | 28 | Data Logging | Base | Annotation |  | 250 bytes (UTF-8) | none | SHORT_STRING | R/W | 1 | No
137 | 1 | 29 | Data Logging | Base | File Name |  | 63 bytes (UTF-8) | Log | SHORT_STRING | R/W | 1 | No
137 | 1 | 30 | Data Logging | Base | Samba User Name |  | 32 bytes (UTF-8) |  | SHORT_STRING | R/W | 1 | No
137 | 1 | 32 | Data Logging | Base | Remote Transfer Interval In Hours | Set time before auto transfer occurs. | 0 to 65,535 | 0 | UINT | R/W | 1 | No
137 | 1 | 33 | Data Logging | Base | Remote Transfer on Percent full | Set when to perform auto transfer based on memory fill. | 0 to 255 | 0 | USINT | R/W | 1 | No
137 | 1 | 34 | Data Logging | Base | Transfer Files Now by | Set to trigger data log transfer from internal memory to remote location.. | None (61), TFTP (2085), Samba (2086) | None (61) | UINT | R/W | 1 | No
137 | 1 | 35 | Data Logging | Base | Test Connection |  | None (61), TFTP (2085), Samba (2086) | None (61) | UINT | R/W | 1 | No
137 | 1 | 36 | Data Logging | Base | Transfer Results |  | 128 bytes (UTF-8) |  | SHORT_STRING | R/W | 1 | No
137 | 1 | 37 | Data Logging | Base | Samba Path |  | 63 bytes (UTF-8) |  | SHORT_STRING | R/W | 1 | No
137 | 1 | 38 | Data Logging | Base | Auto Transfer Type | Set where auto transfer should store files. | None (61), TFTP (2085), Samba (2086), USB (1653) | None (61) | UINT | R/W | 1 | No
137 | 1 | 39 | Data Logging | Base | Transfer When Complete |  | No (59), Yes (106) | No (59) | UINT | R/W | 1 | No
137 | 1 | 40 | Data Logging | Base | Transfer Progress |  | 0 to 255 | 0 | USINT | R/W | 1 | No
137 | 1 | 41 | Data Logging | Base | Delete All Log Points |  | No (59), Yes (106) | No (59) | UINT | R/W | 1 | No
137 | 1 | 42 | Data Logging | Base | Log Point Actions |  | None (61), Enable All (2128), Disable All (2129) | None (61) | UINT | R/W | 1 | No
137 | 1 | 43 | Data Logging | Base | Transfer Results |  | (1236), Transfer Starting (2167.0), Server Down (2168.0), Need Host IP (2169.0), No Files to Transfer (2170.0), No Files Transferred (2171.0), No Files Found (2172.0), Server is Down. Stopped Transfer. (2173.0), Server is Down. Stopping Transfer. (2174.0), Need Host Name and IP Address (2175.0), Check Directory Permissions, Host Name and IP Address. (2176.0), Transfer Complete (2177.0), Transferring Files (2178.0) | (1236) | UINT | R | 1 | No
137 | 1 | 44 | Data Logging | Base | Busy |  | No (59), Yes (106) | No (59) | UINT | R/W | 1 | No
144 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 2 | No
144 | 1 | 4 | Cascade | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | UINT | R/W | 2 | Yes
144 | 1 | 5 | Cascade | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | UINT | R | 2 | Yes
144 | 1 | 6 | Cascade | Base | Control Action | Set the heat/cool control method. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | UINT | R/W | 2 | Yes
144 | 1 | 7 | Cascade | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | UINT | R/W | 2 | Yes
144 | 1 | 8 | Cascade | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | REAL | R/W | 2 | Yes
144 | 1 | 9 | Cascade | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | UINT | R/W | 2 | Yes
144 | 1 | 10 | Cascade | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | UINT | R | 2 | Yes
144 | 1 | 11 | Cascade | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | UINT | R/W | 2 | Yes
144 | 1 | 12 | Cascade | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | UINT | R/W | 2 | Yes
144 | 1 | 13 | Cascade | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | REAL | R/W | 2 | Yes
144 | 1 | 14 | Cascade | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | UINT | R | 2 | Yes
144 | 1 | 15 | Cascade | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 2 | Yes
144 | 1 | 16 | Cascade | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | REAL | R/W | 2 | Yes
144 | 1 | 17 | Cascade | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | REAL | R/W | 2 | Yes
144 | 1 | 18 | Cascade | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | REAL | R/W | 2 | Yes
144 | 1 | 19 | Cascade | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | REAL | R/W | 2 | Yes
144 | 1 | 20 | Cascade | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | REAL | R/W | 2 | Yes
144 | 1 | 21 | Cascade | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | REAL | R/W | 2 | Yes
144 | 1 | 22 | Cascade | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | REAL | R/W | 2 | Yes
144 | 1 | 23 | Cascade | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | UINT | R/W | 2 | Yes
144 | 1 | 24 | Cascade | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | UINT | R/W | 2 | Yes
144 | 1 | 25 | Cascade | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | REAL | R/W | 2 | Yes
144 | 1 | 26 | Cascade | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 2 | Yes
144 | 1 | 27 | Cascade | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | UINT | R/W | 2 | Yes
144 | 1 | 28 | Cascade | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | REAL | R/W | 2 | Yes
144 | 1 | 29 | Cascade | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | UINT | R/W | 2 | Yes
144 | 1 | 30 | Cascade | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | UINT | R/W | 2 | Yes
144 | 1 | 31 | Cascade | Base | Working Manual Source |  | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) |  | UINT | R | 2 | No
144 | 1 | 32 | Cascade | Base | Set Point Bumpless |  |  |  | REAL | R | 2 | No
144 | 1 | 33 | Cascade | Base | Ramp Set Point |  |  |  | REAL | R | 2 | No
144 | 1 | 34 | Cascade | Base | Idle Set Point |  |  |  | REAL | R | 2 | No
144 | 1 | 35 | Cascade | Base | Ramp Set Point |  |  |  | REAL | R | 2 | No
144 | 1 | 36 | Cascade | Base | Profile End Action | Set profile end action for control loop when end step is not specified. | User (100), Off (62), Hold (47) | User (100) | UINT | R/W | 2 | Yes
144 | 1 | 37 | Cascade | Base | Function | Set the type of cascade to implement. | Process (75), Deviation (1807) | Process (75) | UINT | R/W | 2 | Yes
144 | 1 | 38 | Cascade | Base | Scale Low |  | -99,999.0 to 99,999.0 | 0.0 | REAL | R | 2 | No
144 | 1 | 39 | Cascade | Base | Scale High |  | -99,999.0 to 99,999.0 | 1.0 | REAL | R | 2 | No
144 | 1 | 40 | Cascade | Base | Range Low | Set the value represented for low power converted to a temperature set point for the inner loop. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 1 | 41 | Cascade | Base | Range High | Set the value represented for high power converted to a temperature set point for the inner loop. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 2 | Yes
144 | 1 | 43 | Cascade | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | UINT | R/W | 2 | Yes
144 | 1 | 50 | Cascade | Base | Inner Loop Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | UINT | R/W | 2 | Yes
144 | 1 | 51 | Cascade | Base | Inner Loop Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | UINT | R/W | 2 | Yes
144 | 1 | 52 | Cascade | Base | PID Set Crossover |  | Process Value (241), Set Point (85) | Process Value (241) | UINT | R | 2 | No
144 | 1 | 53 | Cascade | Base | PID Set 1 to 2 Crossover |  |  |  | REAL | R | 2 | No
144 | 1 | 54 | Cascade | Base | PID Set 2 to 3 Crossover |  |  |  | REAL | R | 2 | No
144 | 1 | 55 | Cascade | Base | PID Set 3 to 4 Crossover |  |  |  | REAL | R | 2 | No
144 | 1 | 56 | Cascade | Base | PID Set 4 to 5 Crossover |  |  |  | REAL | R | 2 | No
144 | 1 | 57 | Cascade | Base | Inner Loop PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | USINT | R | 2 | No
144 | 1 | 58 | Cascade | Base | Heat Proportional Band Inner Loop 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 59 | Cascade | Base | Cool Proportional Band Inner Loop 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 60 | Cascade | Base | Integral Inner Loop 1 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 1 | 61 | Cascade | Base | Derivative Inner Loop 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 1 | 62 | Cascade | Base | Heat Proportional Band Inner Loop 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 63 | Cascade | Base | Cool Proportional Band Inner Loop 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 64 | Cascade | Base | Integral Inner Loop 2 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 1 | 65 | Cascade | Base | Derivative Inner Loop 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 1 | 66 | Cascade | Base | Heat Proportional Band Inner Loop 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 67 | Cascade | Base | Cool Proportional Band Inner Loop 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 68 | Cascade | Base | Integral Inner Loop 3 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 1 | 69 | Cascade | Base | Derivative Inner Loop 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 1 | 70 | Cascade | Base | Heat Proportional Band Inner Loop 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 71 | Cascade | Base | Cool Proportional Band Inner Loop 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 72 | Cascade | Base | Integral Inner Loop 4 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 1 | 73 | Cascade | Base | Derivative Inner Loop 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 1 | 74 | Cascade | Base | Heat Proportional Band Inner Loop 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 75 | Cascade | Base | Cool Proportional Band Inner Loop 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 76 | Cascade | Base | Integral Inner Loop 5 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 1 | 77 | Cascade | Base | Derivative Inner Loop 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 1 | 78 | Cascade | Base | Inner Loop Deadband | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 1 | 79 | Cascade | Base | Inner Loop On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | REAL | R/W | 2 | Yes
144 | 1 | 80 | Cascade | Base | Inner Loop On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | REAL | R/W | 2 | Yes
144 | 1 | 81 | Cascade | Base | Inner Loop Set Point Closed | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | REAL | R | 2 | Yes
144 | 1 | 82 | Cascade | Base | Inner Loop Set Point Open |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 1 | 83 | Cascade | Base | Inner Loop Heat Proportional Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 1 | 84 | Cascade | Base | Inner Loop Heat Integral Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 1 | 85 | Cascade | Base | Inner Loop Heat Derivative Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 1 | 86 | Cascade | Base | Inner Loop Cool Proportional Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 1 | 87 | Cascade | Base | Inner Loop Cool Integral Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 1 | 88 | Cascade | Base | Inner Loop Cool Derivative Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 1 | 89 | Cascade | Base | Inner Loop Active Input Error |  | None (61), Error (28) |  | UINT | R | 2 | No
144 | 1 | 91 | Cascade | Base | Inner Loop PID Set Number Of |  |  | 1 | USINT | R | 2 | No
144 | 1 | 100 | Cascade | Base | Outer Loop Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | UINT | R/W | 2 | No
144 | 1 | 101 | Cascade | Base | Outer Loop Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | UINT | R/W | 2 | No
144 | 1 | 102 | Cascade | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | UINT | R/W | 2 | Yes
144 | 1 | 103 | Cascade | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. |  |  | REAL | R/W | 2 | Yes
144 | 1 | 104 | Cascade | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. |  |  | REAL | R/W | 2 | Yes
144 | 1 | 105 | Cascade | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. |  |  | REAL | R/W | 2 | Yes
144 | 1 | 106 | Cascade | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. |  |  | REAL | R/W | 2 | Yes
144 | 1 | 107 | Cascade | Base | Outer Loop PID Set Active |  | 1 to 5 |  | USINT | R | 2 | Yes
144 | 1 | 108 | Cascade | Base | Heat Proportional Band Outer Loop 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 109 | Cascade | Base | Cool Proportional Band Outer Loop 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 110 | Cascade | Base | Integral Outer Loop 1 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 1 | 111 | Cascade | Base | Derivative Outer Loop 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 1 | 112 | Cascade | Base | Heat Proportional Band Outer Loop 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 113 | Cascade | Base | Cool Proportional Band Outer Loop 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 114 | Cascade | Base | Integral Outer Loop 2 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 1 | 115 | Cascade | Base | Derivative Outer Loop 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 1 | 116 | Cascade | Base | Heat Proportional Band Outer Loop 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 117 | Cascade | Base | Cool Proportional Band Outer Loop 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 118 | Cascade | Base | Integral Outer Loop 3 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 1 | 119 | Cascade | Base | Derivative Outer Loop 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 1 | 120 | Cascade | Base | Heat Proportional Band Outer Loop 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 121 | Cascade | Base | Cool Proportional Band Outer Loop 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 122 | Cascade | Base | Integral Outer Loop 4 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 1 | 123 | Cascade | Base | Derivative Outer Loop 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 1 | 124 | Cascade | Base | Heat Proportional Band Outer Loop 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 125 | Cascade | Base | Cool Proportional Band Outer Loop 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 1 | 126 | Cascade | Base | Integral Outer Loop 5 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 1 | 127 | Cascade | Base | Derivative Outer Loop 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 1 | 128 | Cascade | Base | Outer Loop Deadband | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 1 | 129 | Cascade | Base | Outer Loop On/Off Heat Hysteresis |  | 0.001 to 99,999.0 | 3.0 | REAL | R/W | 2 | No
144 | 1 | 130 | Cascade | Base | Outer Loop On/Off Cool Hysteresis |  | 0.001 to 99,999.0 | 3.0 | REAL | R/W | 2 | No
144 | 1 | 131 | Cascade | Base | Outer Loop Set Point Closed | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | REAL | R | 2 | No
144 | 1 | 132 | Cascade | Base | Outer Loop Set Point Open |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 1 | 133 | Cascade | Base | Outer Loop Heat Proportional Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 1 | 134 | Cascade | Base | Outer Loop Heat Integral Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 1 | 135 | Cascade | Base | Outer Loop Heat Derivative Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 1 | 136 | Cascade | Base | Outer Loop Cool Proportional Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 1 | 137 | Cascade | Base | Outer Loop Cool Integral Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 1 | 138 | Cascade | Base | Outer Loop Cool Derivative Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 1 | 139 | Cascade | Base | Outer Loop Active Input Error |  | None (61), Error (28) |  | UINT | R | 2 | No
144 | 1 | 140 | Cascade | Base | Outer Loop Power |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 1 | 141 | Cascade | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | USINT | R/W | 2 | Yes
144 | 1 | 150 | Cascade | Base | Cascade Heat Power | Monitor the requested PID heat power. | 0.0 to 100.0 |  | REAL | R | 2 | Yes
144 | 1 | 151 | Cascade | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 2 | No
144 | 1 | 152 | Cascade | Base | Cascade Cool Power | Monitor the requested PID cool power. | -100.0 to 0.0 |  | REAL | R | 2 | Yes
144 | 1 | 153 | Cascade | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 2 | No
144 | 1 | 154 | Cascade | Base | Cascade Power | Monitor the requested PID total power. | -100.0 to 100.0 |  | REAL | R | 2 | Yes
144 | 1 | 155 | Cascade | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 2 | No
144 | 1 | 156 | Cascade | Base | Cascade Set Point Closed |  |  |  | REAL | R | 2 | Yes
144 | 1 | 157 | Cascade | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 2 | No
144 | 1 | 158 | Cascade | Base | Cascade Set Point Open |  |  |  | REAL | R | 2 | Yes
144 | 1 | 159 | Cascade | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 2 | No
144 | 1 | 160 | Cascade | Base | Source Function A |  | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 2 | No
144 | 1 | 161 | Cascade | Base | Source Instance A |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 1 | 162 | Cascade | Base | Source Zone A |  | 0 to 0 | 0 | USINT | R/W | 2 | No
144 | 1 | 163 | Cascade | Base | Source Value A | Monitor process value feedback for the outer loop while in auto mode. |  |  | REAL | R | 2 | No
144 | 1 | 164 | Cascade | Base | Source Function B |  | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 2 | No
144 | 1 | 165 | Cascade | Base | Source Instance B |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 1 | 166 | Cascade | Base | Source Zone B |  | 0 to 0 | 0 | USINT | R/W | 2 | No
144 | 1 | 167 | Cascade | Base | Source Value B | Monitor the source input value used by the inner control loop while in auto mode. |  |  | REAL | R | 2 | No
144 | 1 | 168 | Cascade | Base | Source Function C |  | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 2 | No
144 | 1 | 169 | Cascade | Base | Source Instance C |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 1 | 170 | Cascade | Base | Source Zone C |  | 0 to 24 | 0 | USINT | R/W | 2 | No
144 | 1 | 171 | Cascade | Base | Source Value C | Monitor the remote set point value. |  |  | REAL | R | 2 | No
144 | 1 | 172 | Cascade | Base | Source Function D |  | None (61), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778) | None (61) | UINT | R/W | 2 | No
144 | 1 | 173 | Cascade | Base | Source Instance D |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 1 | 174 | Cascade | Base | Source Zone D |  | 0 to 24 | 0 | USINT | R/W | 2 | No
144 | 1 | 175 | Cascade | Base | Source Value D | Monitor set point from the profile engine when profiling is used. |  |  | REAL | R | 2 | No
144 | 1 | 176 | Cascade | Base | Source Function E |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 2 | No
144 | 1 | 177 | Cascade | Base | Source Instance E |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 1 | 178 | Cascade | Base | Source Zone E |  | 0 to 24 | 0 | USINT | R/W | 2 | No
144 | 1 | 179 | Cascade | Base | Source Value E |  | On (63), Off (62) |  | UINT | R | 2 | No
144 | 1 | 180 | Cascade | Base | Use Remote SP Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 2 | Yes
144 | 1 | 181 | Cascade | Base | Source Function F |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 2 | No
144 | 1 | 182 | Cascade | Base | Source Instance F |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 1 | 183 | Cascade | Base | Source Zone F |  | 0 to 24 | 0 | USINT | R/W | 2 | No
144 | 1 | 184 | Cascade | Base | Source Value F |  | On (63), Off (62) |  | UINT | R | 2 | No
144 | 1 | 185 | Cascade | Base | Use Idle SP Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 2 | Yes
144 | 1 | 186 | Cascade | Base | Source Function G |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 2 | No
144 | 1 | 187 | Cascade | Base | Source Instance G |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 1 | 188 | Cascade | Base | Source Zone G |  | 0 to 24 | 0 | USINT | R/W | 2 | No
144 | 1 | 189 | Cascade | Base | Source Value G |  | On (63), Off (62) |  | UINT | R | 2 | No
144 | 1 | 190 | Cascade | Base | Off Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 2 | Yes
144 | 1 | 191 | Cascade | Base | Source Function H |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 2 | No
144 | 1 | 192 | Cascade | Base | Source Instance H |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 1 | 193 | Cascade | Base | Source Zone H |  | 0 to 24 | 0 | USINT | R/W | 2 | No
144 | 1 | 194 | Cascade | Base | Source Value H |  | On (63), Off (62) |  | UINT | R | 2 | No
144 | 1 | 195 | Cascade | Base | Manual Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 2 | Yes
144 | 1 | 196 | Cascade | Base | Source Function A |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 2 | No
144 | 1 | 197 | Cascade | Base | Source Instance A |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 1 | 198 | Cascade | Base | Source Zone A |  | 0 to 24 | 0 | USINT | R/W | 2 | No
144 | 1 | 199 | Cascade | Base | Source Value A |  | On (63), Off (62) |  | UINT | R | 2 | No
144 | 1 | 200 | Cascade | Base | Initiate Autotune Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 2 | Yes
144 | 1 | 201 | Cascade | Base | Source Function B |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 2 | No
144 | 1 | 202 | Cascade | Base | Source Instance B |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 1 | 203 | Cascade | Base | Source Zone B |  | 0 to 24 | 0 | USINT | R/W | 2 | No
144 | 1 | 204 | Cascade | Base | Source Value B |  | On (63), Off (62) | None | UINT | R | 2 | No
144 | 1 | 205 | Cascade | Base | Disable Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 2 | Yes
144 | 1 | 206 | Cascade | Base | Simple Set Point Enable | Set to switch off cascade feature. | On (63), Off (62) | Off (62) | UINT | R/W | 2 | Yes
144 | 1 | 207 | Cascade | Base | Cascade Control Mode Is Off | Monitor Cascade Control Mode is Off | On (63), Off (62) |  | UINT | R | 2 | Yes
144 | 1 | 208 | Cascade | Base | Set Point | Monitor Closed Loop Set Point |  |  | REAL | R | 2 | No
144 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 2 | No
144 | 2 | 4 | Cascade | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | UINT | R/W | 2 | Yes
144 | 2 | 5 | Cascade | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | UINT | R | 2 | Yes
144 | 2 | 6 | Cascade | Base | Control Action | Set the heat/cool control method. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | UINT | R/W | 2 | Yes
144 | 2 | 7 | Cascade | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | UINT | R/W | 2 | Yes
144 | 2 | 8 | Cascade | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | REAL | R/W | 2 | Yes
144 | 2 | 9 | Cascade | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | UINT | R/W | 2 | Yes
144 | 2 | 10 | Cascade | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | UINT | R | 2 | Yes
144 | 2 | 11 | Cascade | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | UINT | R/W | 2 | Yes
144 | 2 | 12 | Cascade | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | UINT | R/W | 2 | Yes
144 | 2 | 13 | Cascade | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | REAL | R/W | 2 | Yes
144 | 2 | 14 | Cascade | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | UINT | R | 2 | Yes
144 | 2 | 15 | Cascade | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 2 | Yes
144 | 2 | 16 | Cascade | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | REAL | R/W | 2 | Yes
144 | 2 | 17 | Cascade | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | REAL | R/W | 2 | Yes
144 | 2 | 18 | Cascade | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | REAL | R/W | 2 | Yes
144 | 2 | 19 | Cascade | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | REAL | R/W | 2 | Yes
144 | 2 | 20 | Cascade | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | REAL | R/W | 2 | Yes
144 | 2 | 21 | Cascade | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | REAL | R/W | 2 | Yes
144 | 2 | 22 | Cascade | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | REAL | R/W | 2 | Yes
144 | 2 | 23 | Cascade | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | UINT | R/W | 2 | Yes
144 | 2 | 24 | Cascade | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | UINT | R/W | 2 | Yes
144 | 2 | 25 | Cascade | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | REAL | R/W | 2 | Yes
144 | 2 | 26 | Cascade | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 2 | Yes
144 | 2 | 27 | Cascade | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | UINT | R/W | 2 | Yes
144 | 2 | 28 | Cascade | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | REAL | R/W | 2 | Yes
144 | 2 | 29 | Cascade | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | UINT | R/W | 2 | Yes
144 | 2 | 30 | Cascade | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | UINT | R/W | 2 | Yes
144 | 2 | 31 | Cascade | Base | Working Manual Source |  | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) |  | UINT | R | 2 | No
144 | 2 | 32 | Cascade | Base | Set Point Bumpless |  |  |  | REAL | R | 2 | No
144 | 2 | 33 | Cascade | Base | Ramp Set Point |  |  |  | REAL | R | 2 | No
144 | 2 | 34 | Cascade | Base | Idle Set Point |  |  |  | REAL | R | 2 | No
144 | 2 | 35 | Cascade | Base | Ramp Set Point |  |  |  | REAL | R | 2 | No
144 | 2 | 36 | Cascade | Base | Profile End Action | Set profile end action for control loop when end step is not specified. | User (100), Off (62), Hold (47) | User (100) | UINT | R/W | 2 | Yes
144 | 2 | 37 | Cascade | Base | Function | Set the type of cascade to implement. | Process (75), Deviation (1807) | Process (75) | UINT | R/W | 2 | Yes
144 | 2 | 38 | Cascade | Base | Scale Low |  | -99,999.0 to 99,999.0 | 0.0 | REAL | R | 2 | No
144 | 2 | 39 | Cascade | Base | Scale High |  | -99,999.0 to 99,999.0 | 1.0 | REAL | R | 2 | No
144 | 2 | 40 | Cascade | Base | Range Low | Set the value represented for low power converted to a temperature set point for the inner loop. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 2 | 41 | Cascade | Base | Range High | Set the value represented for high power converted to a temperature set point for the inner loop. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 2 | Yes
144 | 2 | 43 | Cascade | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | UINT | R/W | 2 | Yes
144 | 2 | 50 | Cascade | Base | Inner Loop Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | UINT | R/W | 2 | Yes
144 | 2 | 51 | Cascade | Base | Inner Loop Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | UINT | R/W | 2 | Yes
144 | 2 | 52 | Cascade | Base | PID Set Crossover |  | Process Value (241), Set Point (85) | Process Value (241) | UINT | R | 2 | No
144 | 2 | 53 | Cascade | Base | PID Set 1 to 2 Crossover |  |  |  | REAL | R | 2 | No
144 | 2 | 54 | Cascade | Base | PID Set 2 to 3 Crossover |  |  |  | REAL | R | 2 | No
144 | 2 | 55 | Cascade | Base | PID Set 3 to 4 Crossover |  |  |  | REAL | R | 2 | No
144 | 2 | 56 | Cascade | Base | PID Set 4 to 5 Crossover |  |  |  | REAL | R | 2 | No
144 | 2 | 57 | Cascade | Base | Inner Loop PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | USINT | R | 2 | No
144 | 2 | 58 | Cascade | Base | Heat Proportional Band Inner Loop 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 59 | Cascade | Base | Cool Proportional Band Inner Loop 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 60 | Cascade | Base | Integral Inner Loop 1 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 2 | 61 | Cascade | Base | Derivative Inner Loop 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 2 | 62 | Cascade | Base | Heat Proportional Band Inner Loop 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 63 | Cascade | Base | Cool Proportional Band Inner Loop 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 64 | Cascade | Base | Integral Inner Loop 2 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 2 | 65 | Cascade | Base | Derivative Inner Loop 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 2 | 66 | Cascade | Base | Heat Proportional Band Inner Loop 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 67 | Cascade | Base | Cool Proportional Band Inner Loop 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 68 | Cascade | Base | Integral Inner Loop 3 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 2 | 69 | Cascade | Base | Derivative Inner Loop 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 2 | 70 | Cascade | Base | Heat Proportional Band Inner Loop 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 71 | Cascade | Base | Cool Proportional Band Inner Loop 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 72 | Cascade | Base | Integral Inner Loop 4 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 2 | 73 | Cascade | Base | Derivative Inner Loop 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 2 | 74 | Cascade | Base | Heat Proportional Band Inner Loop 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 75 | Cascade | Base | Cool Proportional Band Inner Loop 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 76 | Cascade | Base | Integral Inner Loop 5 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 2 | 77 | Cascade | Base | Derivative Inner Loop 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 2 | 78 | Cascade | Base | Inner Loop Deadband | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 2 | 79 | Cascade | Base | Inner Loop On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | REAL | R/W | 2 | Yes
144 | 2 | 80 | Cascade | Base | Inner Loop On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | REAL | R/W | 2 | Yes
144 | 2 | 81 | Cascade | Base | Inner Loop Set Point Closed | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | REAL | R | 2 | Yes
144 | 2 | 82 | Cascade | Base | Inner Loop Set Point Open |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 2 | 83 | Cascade | Base | Inner Loop Heat Proportional Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 2 | 84 | Cascade | Base | Inner Loop Heat Integral Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 2 | 85 | Cascade | Base | Inner Loop Heat Derivative Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 2 | 86 | Cascade | Base | Inner Loop Cool Proportional Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 2 | 87 | Cascade | Base | Inner Loop Cool Integral Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 2 | 88 | Cascade | Base | Inner Loop Cool Derivative Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 2 | 89 | Cascade | Base | Inner Loop Active Input Error |  | None (61), Error (28) |  | UINT | R | 2 | No
144 | 2 | 91 | Cascade | Base | Inner Loop PID Set Number Of |  |  | 1 | USINT | R | 2 | No
144 | 2 | 100 | Cascade | Base | Outer Loop Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | UINT | R/W | 2 | No
144 | 2 | 101 | Cascade | Base | Outer Loop Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | UINT | R/W | 2 | No
144 | 2 | 102 | Cascade | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | UINT | R/W | 2 | Yes
144 | 2 | 103 | Cascade | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. |  |  | REAL | R/W | 2 | Yes
144 | 2 | 104 | Cascade | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. |  |  | REAL | R/W | 2 | Yes
144 | 2 | 105 | Cascade | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. |  |  | REAL | R/W | 2 | Yes
144 | 2 | 106 | Cascade | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. |  |  | REAL | R/W | 2 | Yes
144 | 2 | 107 | Cascade | Base | Outer Loop PID Set Active |  | 1 to 5 |  | USINT | R | 2 | Yes
144 | 2 | 108 | Cascade | Base | Heat Proportional Band Outer Loop 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 109 | Cascade | Base | Cool Proportional Band Outer Loop 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 110 | Cascade | Base | Integral Outer Loop 1 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 2 | 111 | Cascade | Base | Derivative Outer Loop 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 2 | 112 | Cascade | Base | Heat Proportional Band Outer Loop 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 113 | Cascade | Base | Cool Proportional Band Outer Loop 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 114 | Cascade | Base | Integral Outer Loop 2 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 2 | 115 | Cascade | Base | Derivative Outer Loop 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 2 | 116 | Cascade | Base | Heat Proportional Band Outer Loop 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 117 | Cascade | Base | Cool Proportional Band Outer Loop 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 118 | Cascade | Base | Integral Outer Loop 3 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 2 | 119 | Cascade | Base | Derivative Outer Loop 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 2 | 120 | Cascade | Base | Heat Proportional Band Outer Loop 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 121 | Cascade | Base | Cool Proportional Band Outer Loop 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 122 | Cascade | Base | Integral Outer Loop 4 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 2 | 123 | Cascade | Base | Derivative Outer Loop 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 2 | 124 | Cascade | Base | Heat Proportional Band Outer Loop 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 125 | Cascade | Base | Cool Proportional Band Outer Loop 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 2 | Yes
144 | 2 | 126 | Cascade | Base | Integral Outer Loop 5 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 2 | Yes
144 | 2 | 127 | Cascade | Base | Derivative Outer Loop 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 2 | 128 | Cascade | Base | Outer Loop Deadband | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | REAL | R/W | 2 | Yes
144 | 2 | 129 | Cascade | Base | Outer Loop On/Off Heat Hysteresis |  | 0.001 to 99,999.0 | 3.0 | REAL | R/W | 2 | No
144 | 2 | 130 | Cascade | Base | Outer Loop On/Off Cool Hysteresis |  | 0.001 to 99,999.0 | 3.0 | REAL | R/W | 2 | No
144 | 2 | 131 | Cascade | Base | Outer Loop Set Point Closed | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | REAL | R | 2 | No
144 | 2 | 132 | Cascade | Base | Outer Loop Set Point Open |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 2 | 133 | Cascade | Base | Outer Loop Heat Proportional Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 2 | 134 | Cascade | Base | Outer Loop Heat Integral Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 2 | 135 | Cascade | Base | Outer Loop Heat Derivative Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 2 | 136 | Cascade | Base | Outer Loop Cool Proportional Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 2 | 137 | Cascade | Base | Outer Loop Cool Integral Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 2 | 138 | Cascade | Base | Outer Loop Cool Derivative Term |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 2 | 139 | Cascade | Base | Outer Loop Active Input Error |  | None (61), Error (28) |  | UINT | R | 2 | No
144 | 2 | 140 | Cascade | Base | Outer Loop Power |  | -100.0 to 100.0 |  | REAL | R | 2 | No
144 | 2 | 141 | Cascade | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | USINT | R/W | 2 | Yes
144 | 2 | 150 | Cascade | Base | Cascade Heat Power | Monitor the requested PID heat power. | 0.0 to 100.0 |  | REAL | R | 2 | Yes
144 | 2 | 151 | Cascade | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 2 | No
144 | 2 | 152 | Cascade | Base | Cascade Cool Power | Monitor the requested PID cool power. | -100.0 to 0.0 |  | REAL | R | 2 | Yes
144 | 2 | 153 | Cascade | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 2 | No
144 | 2 | 154 | Cascade | Base | Cascade Power | Monitor the requested PID total power. | -100.0 to 100.0 |  | REAL | R | 2 | Yes
144 | 2 | 155 | Cascade | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 2 | No
144 | 2 | 156 | Cascade | Base | Cascade Set Point Closed |  |  |  | REAL | R | 2 | Yes
144 | 2 | 157 | Cascade | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 2 | No
144 | 2 | 158 | Cascade | Base | Cascade Set Point Open |  |  |  | REAL | R | 2 | Yes
144 | 2 | 159 | Cascade | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 2 | No
144 | 2 | 160 | Cascade | Base | Source Function A |  | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 2 | No
144 | 2 | 161 | Cascade | Base | Source Instance A |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 2 | 162 | Cascade | Base | Source Zone A |  | 0 to 0 | 0 | USINT | R/W | 2 | No
144 | 2 | 163 | Cascade | Base | Source Value A | Monitor process value feedback for the outer loop while in auto mode. |  |  | REAL | R | 2 | No
144 | 2 | 164 | Cascade | Base | Source Function B |  | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 2 | No
144 | 2 | 165 | Cascade | Base | Source Instance B |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 2 | 166 | Cascade | Base | Source Zone B |  | 0 to 0 | 0 | USINT | R/W | 2 | No
144 | 2 | 167 | Cascade | Base | Source Value B | Monitor the source input value used by the inner control loop while in auto mode. |  |  | REAL | R | 2 | No
144 | 2 | 168 | Cascade | Base | Source Function C |  | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 2 | No
144 | 2 | 169 | Cascade | Base | Source Instance C |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 2 | 170 | Cascade | Base | Source Zone C |  | 0 to 24 | 0 | USINT | R/W | 2 | No
144 | 2 | 171 | Cascade | Base | Source Value C | Monitor the remote set point value. |  |  | REAL | R | 2 | No
144 | 2 | 172 | Cascade | Base | Source Function D |  | None (61), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778) | None (61) | UINT | R/W | 2 | No
144 | 2 | 173 | Cascade | Base | Source Instance D |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 2 | 174 | Cascade | Base | Source Zone D |  | 0 to 24 | 0 | USINT | R/W | 2 | No
144 | 2 | 175 | Cascade | Base | Source Value D | Monitor the set point used by the control loop while a profile is active. |  |  | REAL | R | 2 | No
144 | 2 | 176 | Cascade | Base | Source Function E |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 2 | No
144 | 2 | 177 | Cascade | Base | Source Instance E |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 2 | 178 | Cascade | Base | Source Zone E |  | 0 to 24 | 0 | USINT | R/W | 2 | No
144 | 2 | 179 | Cascade | Base | Source Value E |  | On (63), Off (62) |  | UINT | R | 2 | No
144 | 2 | 180 | Cascade | Base | Use Remote SP Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 2 | Yes
144 | 2 | 181 | Cascade | Base | Source Function F |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 2 | No
144 | 2 | 182 | Cascade | Base | Source Instance F |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 2 | 183 | Cascade | Base | Source Zone F |  | 0 to 24 | 0 | USINT | R/W | 2 | No
144 | 2 | 184 | Cascade | Base | Source Value F |  | On (63), Off (62) |  | UINT | R | 2 | No
144 | 2 | 185 | Cascade | Base | Use Idle SP Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 2 | Yes
144 | 2 | 186 | Cascade | Base | Source Function G |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 2 | No
144 | 2 | 187 | Cascade | Base | Source Instance G |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 2 | 188 | Cascade | Base | Source Zone G |  | 0 to 24 | 0 | USINT | R/W | 2 | No
144 | 2 | 189 | Cascade | Base | Source Value G |  | On (63), Off (62) |  | UINT | R | 2 | No
144 | 2 | 190 | Cascade | Base | Off Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 2 | Yes
144 | 2 | 191 | Cascade | Base | Source Function H |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 2 | No
144 | 2 | 192 | Cascade | Base | Source Instance H |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 2 | 193 | Cascade | Base | Source Zone H |  | 0 to 24 | 0 | USINT | R/W | 2 | No
144 | 2 | 194 | Cascade | Base | Source Value H |  | On (63), Off (62) |  | UINT | R | 2 | No
144 | 2 | 195 | Cascade | Base | Manual Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 2 | Yes
144 | 2 | 196 | Cascade | Base | Source Function A |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 2 | No
144 | 2 | 197 | Cascade | Base | Source Instance A |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 2 | 198 | Cascade | Base | Source Zone A |  | 0 to 24 | 0 | USINT | R/W | 2 | No
144 | 2 | 199 | Cascade | Base | Source Value A |  | On (63), Off (62) |  | UINT | R | 2 | No
144 | 2 | 200 | Cascade | Base | Initiate Autotune Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 2 | Yes
144 | 2 | 201 | Cascade | Base | Source Function B |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 2 | No
144 | 2 | 202 | Cascade | Base | Source Instance B |  | 1 to 250 | 1 | USINT | R/W | 2 | No
144 | 2 | 203 | Cascade | Base | Source Zone B |  | 0 to 24 | 0 | USINT | R/W | 2 | No
144 | 2 | 204 | Cascade | Base | Source Value B |  | On (63), Off (62) | None | UINT | R | 2 | No
144 | 2 | 205 | Cascade | Base | Disable Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 2 | Yes
144 | 2 | 206 | Cascade | Base | Simple Set Point Enable | Set to switch off cascade feature. | On (63), Off (62) | Off (62) | UINT | R/W | 2 | Yes
144 | 2 | 207 | Cascade | Base | Cascade Control Mode Is Off | Monitor Cascade Control Mode is Off | On (63), Off (62) |  | UINT | R | 2 | Yes
144 | 2 | 208 | Cascade | Base | Set Point | Monitor Closed Loop Set Point |  |  | REAL | R | 2 | No
146 | 1 | 1 | Function Key | Base | Function | Set the soft key action. | Momentary (1714), Toggle (1713), On Pulse (1471) | Momentary (1714) | UINT | R/W | 4 | Yes
146 | 1 | 2 | Function Key | Base | Time | Set the pulse time If function is On Pulse. | 0 to 99,999.0 | 1.0 | REAL | R/W | 4 | Yes
146 | 1 | 3 | Function Key | Base | Input State | Monitor the key state. | On (63), Off (62) |  | UINT | R | 4 | Yes
146 | 1 | 6 | Function Key | Base | Key Action | Set when the action occurs. | Down (1457), Up (1456) | Up (1456) | UINT | R/W | 4 | No
146 | 1 | 7 | Function Key | Base | Error | Monitor the error for key actions. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 4 | No
146 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 4 | No
146 | 2 | 1 | Function Key | Base | Function | Set the soft key action. | Momentary (1714), Toggle (1713), On Pulse (1471) | Momentary (1714) | UINT | R/W | 4 | Yes
146 | 2 | 2 | Function Key | Base | Time | Set the pulse time If function is On Pulse. | 0 to 99,999.0 | 1.0 | REAL | R/W | 4 | Yes
146 | 2 | 3 | Function Key | Base | Input State | Monitor the key state. | On (63), Off (62) |  | UINT | R | 4 | Yes
146 | 2 | 6 | Function Key | Base | Key Action | Set when the action occurs. | Down (1457), Up (1456) | Up (1456) | UINT | R/W | 4 | No
146 | 2 | 7 | Function Key | Base | Error | Monitor the error for key actions. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 4 | No
146 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 4 | No
146 | 3 | 1 | Function Key | Base | Function | Set the soft key action. | Momentary (1714), Toggle (1713), On Pulse (1471) | Momentary (1714) | UINT | R/W | 4 | Yes
146 | 3 | 2 | Function Key | Base | Time | Set the pulse time If function is On Pulse. | 0 to 99,999.0 | 1.0 | REAL | R/W | 4 | Yes
146 | 3 | 3 | Function Key | Base | Input State | Monitor the key state. | On (63), Off (62) |  | UINT | R | 4 | Yes
146 | 3 | 6 | Function Key | Base | Key Action | Set when the action occurs. | Down (1457), Up (1456) | Up (1456) | UINT | R/W | 4 | No
146 | 3 | 7 | Function Key | Base | Error | Monitor the error for key actions. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 4 | No
146 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 4 | No
146 | 4 | 1 | Function Key | Base | Function | Set the soft key action. | Momentary (1714), Toggle (1713), On Pulse (1471) | Momentary (1714) | UINT | R/W | 4 | Yes
146 | 4 | 2 | Function Key | Base | Time | Set the pulse time If function is On Pulse. | 0 to 99,999.0 | 1.0 | REAL | R/W | 4 | Yes
146 | 4 | 3 | Function Key | Base | Input State | Monitor the key state. | On (63), Off (62) |  | UINT | R | 4 | Yes
146 | 4 | 6 | Function Key | Base | Key Action | Set when the action occurs. | Down (1457), Up (1456) | Up (1456) | UINT | R/W | 4 | No
146 | 4 | 7 | Function Key | Base | Error | Monitor the error for key actions. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 4 | No
146 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 4 | No
155 | 1 | 1 | Universal Input | 1 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 1 | 2 | Universal Input | 1 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 1 | 3 | Universal Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 1 | 4 | Universal Input | 1 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 1 | 5 | Universal Input | 1 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 1 | 6 | Universal Input | 1 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 1 | 7 | Universal Input | 1 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 1 | 8 | Universal Input | 1 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 1 | 9 | Universal Input | 1 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 1 | 10 | Universal Input | 1 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 1 | 11 | Universal Input | 1 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 1 | 12 | Universal Input | 1 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 1 | 13 | Universal Input | 1 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 1 | 14 | Universal Input | 1 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 1 | 15 | Universal Input | 1 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 1 | 16 | Universal Input | 1 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 1 | 17 | Universal Input | 1 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 1 | 18 | Universal Input | 1 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 1 | 27 | Universal Input | 1 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 1 | 28 | Universal Input | 1 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 1 | 29 | Universal Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 1 | 30 | Universal Input | 1 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 1 | 31 | Universal Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 1 | 32 | Universal Input | 1 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 1 | 33 | Universal Input | 1 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 1 | 34 | Universal Input | 1 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 1 | 35 | Universal Input | 1 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 1 | 36 | Universal Input | 1 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 1 | 37 | Universal Input | 1 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 1 | 38 | Universal Input | 1 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 1 | 46 | Universal Input | 1 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 1 | 48 | Universal Input | 1 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 1 | 49 | Universal Input | 1 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 1 | 50 | Universal Input | 1 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 1 | 51 | Universal Input | 1 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 1 | 52 | Universal Input | 1 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 1 | 53 | Universal Input | 1 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 2 | 1 | Universal Input | 1 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 2 | 2 | Universal Input | 1 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 2 | 3 | Universal Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 2 | 4 | Universal Input | 1 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 2 | 5 | Universal Input | 1 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 2 | 6 | Universal Input | 1 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 2 | 7 | Universal Input | 1 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 2 | 8 | Universal Input | 1 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 2 | 9 | Universal Input | 1 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 2 | 10 | Universal Input | 1 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 2 | 11 | Universal Input | 1 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 2 | 12 | Universal Input | 1 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 2 | 13 | Universal Input | 1 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 2 | 14 | Universal Input | 1 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 2 | 15 | Universal Input | 1 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 2 | 16 | Universal Input | 1 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 2 | 17 | Universal Input | 1 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 2 | 18 | Universal Input | 1 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 2 | 27 | Universal Input | 1 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 2 | 28 | Universal Input | 1 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 2 | 29 | Universal Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 2 | 30 | Universal Input | 1 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 2 | 31 | Universal Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 2 | 32 | Universal Input | 1 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 2 | 33 | Universal Input | 1 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 2 | 34 | Universal Input | 1 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 2 | 35 | Universal Input | 1 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 2 | 36 | Universal Input | 1 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 2 | 37 | Universal Input | 1 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 2 | 38 | Universal Input | 1 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 2 | 46 | Universal Input | 1 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 2 | 48 | Universal Input | 1 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 2 | 49 | Universal Input | 1 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 2 | 50 | Universal Input | 1 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 2 | 51 | Universal Input | 1 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 2 | 52 | Universal Input | 1 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 2 | 53 | Universal Input | 1 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 3 | 1 | Universal Input | 1 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 3 | 2 | Universal Input | 1 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 3 | 3 | Universal Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 3 | 4 | Universal Input | 1 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 3 | 5 | Universal Input | 1 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 3 | 6 | Universal Input | 1 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 3 | 7 | Universal Input | 1 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 3 | 8 | Universal Input | 1 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 3 | 9 | Universal Input | 1 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 3 | 10 | Universal Input | 1 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 3 | 11 | Universal Input | 1 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 3 | 12 | Universal Input | 1 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 3 | 13 | Universal Input | 1 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 3 | 14 | Universal Input | 1 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 3 | 15 | Universal Input | 1 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 3 | 16 | Universal Input | 1 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 3 | 17 | Universal Input | 1 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 3 | 18 | Universal Input | 1 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 3 | 27 | Universal Input | 1 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 3 | 28 | Universal Input | 1 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 3 | 29 | Universal Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 3 | 30 | Universal Input | 1 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 3 | 31 | Universal Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 3 | 32 | Universal Input | 1 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 3 | 33 | Universal Input | 1 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 3 | 34 | Universal Input | 1 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 3 | 35 | Universal Input | 1 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 3 | 36 | Universal Input | 1 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 3 | 37 | Universal Input | 1 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 3 | 38 | Universal Input | 1 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 3 | 46 | Universal Input | 1 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 3 | 48 | Universal Input | 1 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 3 | 49 | Universal Input | 1 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 3 | 50 | Universal Input | 1 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 3 | 51 | Universal Input | 1 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 3 | 52 | Universal Input | 1 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 3 | 53 | Universal Input | 1 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 4 | 1 | Universal Input | 1 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 4 | 2 | Universal Input | 1 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 4 | 3 | Universal Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 4 | 4 | Universal Input | 1 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 4 | 5 | Universal Input | 1 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 4 | 6 | Universal Input | 1 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 4 | 7 | Universal Input | 1 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 4 | 8 | Universal Input | 1 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 4 | 9 | Universal Input | 1 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 4 | 10 | Universal Input | 1 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 4 | 11 | Universal Input | 1 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 4 | 12 | Universal Input | 1 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 4 | 13 | Universal Input | 1 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 4 | 14 | Universal Input | 1 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 4 | 15 | Universal Input | 1 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 4 | 16 | Universal Input | 1 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 4 | 17 | Universal Input | 1 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 4 | 18 | Universal Input | 1 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 4 | 27 | Universal Input | 1 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 4 | 28 | Universal Input | 1 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 4 | 29 | Universal Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 4 | 30 | Universal Input | 1 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 4 | 31 | Universal Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 4 | 32 | Universal Input | 1 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 4 | 33 | Universal Input | 1 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 4 | 34 | Universal Input | 1 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 4 | 35 | Universal Input | 1 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 4 | 36 | Universal Input | 1 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 4 | 37 | Universal Input | 1 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 4 | 38 | Universal Input | 1 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 4 | 46 | Universal Input | 1 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 4 | 48 | Universal Input | 1 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 4 | 49 | Universal Input | 1 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 4 | 50 | Universal Input | 1 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 4 | 51 | Universal Input | 1 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 4 | 52 | Universal Input | 1 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 4 | 53 | Universal Input | 1 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 11 | 1 | Universal Input | 2 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 11 | 2 | Universal Input | 2 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 11 | 3 | Universal Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 11 | 4 | Universal Input | 2 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 11 | 5 | Universal Input | 2 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 11 | 6 | Universal Input | 2 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 11 | 7 | Universal Input | 2 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 11 | 8 | Universal Input | 2 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 11 | 9 | Universal Input | 2 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 11 | 10 | Universal Input | 2 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 11 | 11 | Universal Input | 2 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 11 | 12 | Universal Input | 2 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 11 | 13 | Universal Input | 2 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 11 | 14 | Universal Input | 2 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 11 | 15 | Universal Input | 2 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 11 | 16 | Universal Input | 2 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 11 | 17 | Universal Input | 2 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 11 | 18 | Universal Input | 2 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 11 | 27 | Universal Input | 2 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 11 | 28 | Universal Input | 2 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 11 | 29 | Universal Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 11 | 30 | Universal Input | 2 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 11 | 31 | Universal Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 11 | 32 | Universal Input | 2 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 11 | 33 | Universal Input | 2 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 11 | 34 | Universal Input | 2 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 11 | 35 | Universal Input | 2 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 11 | 36 | Universal Input | 2 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 11 | 37 | Universal Input | 2 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 11 | 38 | Universal Input | 2 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 11 | 46 | Universal Input | 2 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 11 | 48 | Universal Input | 2 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 11 | 49 | Universal Input | 2 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 11 | 50 | Universal Input | 2 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 11 | 51 | Universal Input | 2 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 11 | 52 | Universal Input | 2 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 11 | 53 | Universal Input | 2 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 12 | 1 | Universal Input | 2 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 12 | 2 | Universal Input | 2 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 12 | 3 | Universal Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 12 | 4 | Universal Input | 2 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 12 | 5 | Universal Input | 2 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 12 | 6 | Universal Input | 2 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 12 | 7 | Universal Input | 2 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 12 | 8 | Universal Input | 2 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 12 | 9 | Universal Input | 2 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 12 | 10 | Universal Input | 2 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 12 | 11 | Universal Input | 2 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 12 | 12 | Universal Input | 2 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 12 | 13 | Universal Input | 2 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 12 | 14 | Universal Input | 2 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 12 | 15 | Universal Input | 2 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 12 | 16 | Universal Input | 2 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 12 | 17 | Universal Input | 2 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 12 | 18 | Universal Input | 2 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 12 | 27 | Universal Input | 2 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 12 | 28 | Universal Input | 2 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 12 | 29 | Universal Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 12 | 30 | Universal Input | 2 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 12 | 31 | Universal Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 12 | 32 | Universal Input | 2 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 12 | 33 | Universal Input | 2 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 12 | 34 | Universal Input | 2 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 12 | 35 | Universal Input | 2 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 12 | 36 | Universal Input | 2 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 12 | 37 | Universal Input | 2 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 12 | 38 | Universal Input | 2 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 12 | 46 | Universal Input | 2 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 12 | 48 | Universal Input | 2 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 12 | 49 | Universal Input | 2 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 12 | 50 | Universal Input | 2 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 12 | 51 | Universal Input | 2 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 12 | 52 | Universal Input | 2 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 12 | 53 | Universal Input | 2 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 13 | 1 | Universal Input | 2 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 13 | 2 | Universal Input | 2 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 13 | 3 | Universal Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 13 | 4 | Universal Input | 2 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 13 | 5 | Universal Input | 2 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 13 | 6 | Universal Input | 2 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 13 | 7 | Universal Input | 2 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 13 | 8 | Universal Input | 2 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 13 | 9 | Universal Input | 2 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 13 | 10 | Universal Input | 2 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 13 | 11 | Universal Input | 2 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 13 | 12 | Universal Input | 2 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 13 | 13 | Universal Input | 2 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 13 | 14 | Universal Input | 2 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 13 | 15 | Universal Input | 2 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 13 | 16 | Universal Input | 2 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 13 | 17 | Universal Input | 2 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 13 | 18 | Universal Input | 2 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 13 | 27 | Universal Input | 2 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 13 | 28 | Universal Input | 2 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 13 | 29 | Universal Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 13 | 30 | Universal Input | 2 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 13 | 31 | Universal Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 13 | 32 | Universal Input | 2 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 13 | 33 | Universal Input | 2 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 13 | 34 | Universal Input | 2 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 13 | 35 | Universal Input | 2 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 13 | 36 | Universal Input | 2 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 13 | 37 | Universal Input | 2 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 13 | 38 | Universal Input | 2 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 13 | 46 | Universal Input | 2 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 13 | 48 | Universal Input | 2 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 13 | 49 | Universal Input | 2 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 13 | 50 | Universal Input | 2 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 13 | 51 | Universal Input | 2 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 13 | 52 | Universal Input | 2 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 13 | 53 | Universal Input | 2 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 14 | 1 | Universal Input | 2 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 14 | 2 | Universal Input | 2 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 14 | 3 | Universal Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 14 | 4 | Universal Input | 2 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 14 | 5 | Universal Input | 2 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 14 | 6 | Universal Input | 2 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 14 | 7 | Universal Input | 2 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 14 | 8 | Universal Input | 2 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 14 | 9 | Universal Input | 2 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 14 | 10 | Universal Input | 2 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 14 | 11 | Universal Input | 2 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 14 | 12 | Universal Input | 2 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 14 | 13 | Universal Input | 2 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 14 | 14 | Universal Input | 2 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 14 | 15 | Universal Input | 2 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 14 | 16 | Universal Input | 2 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 14 | 17 | Universal Input | 2 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 14 | 18 | Universal Input | 2 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 14 | 27 | Universal Input | 2 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 14 | 28 | Universal Input | 2 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 14 | 29 | Universal Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 14 | 30 | Universal Input | 2 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 14 | 31 | Universal Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 14 | 32 | Universal Input | 2 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 14 | 33 | Universal Input | 2 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 14 | 34 | Universal Input | 2 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 14 | 35 | Universal Input | 2 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 14 | 36 | Universal Input | 2 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 14 | 37 | Universal Input | 2 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 14 | 38 | Universal Input | 2 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 14 | 46 | Universal Input | 2 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 14 | 48 | Universal Input | 2 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 14 | 49 | Universal Input | 2 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 14 | 50 | Universal Input | 2 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 14 | 51 | Universal Input | 2 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 14 | 52 | Universal Input | 2 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 14 | 53 | Universal Input | 2 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 21 | 1 | Universal Input | 3 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 21 | 2 | Universal Input | 3 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 21 | 3 | Universal Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 21 | 4 | Universal Input | 3 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 21 | 5 | Universal Input | 3 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 21 | 6 | Universal Input | 3 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 21 | 7 | Universal Input | 3 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 21 | 8 | Universal Input | 3 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 21 | 9 | Universal Input | 3 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 21 | 10 | Universal Input | 3 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 21 | 11 | Universal Input | 3 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 21 | 12 | Universal Input | 3 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 21 | 13 | Universal Input | 3 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 21 | 14 | Universal Input | 3 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 21 | 15 | Universal Input | 3 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 21 | 16 | Universal Input | 3 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 21 | 17 | Universal Input | 3 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 21 | 18 | Universal Input | 3 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 21 | 27 | Universal Input | 3 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 21 | 28 | Universal Input | 3 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 21 | 29 | Universal Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 21 | 30 | Universal Input | 3 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 21 | 31 | Universal Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 21 | 32 | Universal Input | 3 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 21 | 33 | Universal Input | 3 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 21 | 34 | Universal Input | 3 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 21 | 35 | Universal Input | 3 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 21 | 36 | Universal Input | 3 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 21 | 37 | Universal Input | 3 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 21 | 38 | Universal Input | 3 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 21 | 46 | Universal Input | 3 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 21 | 48 | Universal Input | 3 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 21 | 49 | Universal Input | 3 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 21 | 50 | Universal Input | 3 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 21 | 51 | Universal Input | 3 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 21 | 52 | Universal Input | 3 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 21 | 53 | Universal Input | 3 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 22 | 1 | Universal Input | 3 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 22 | 2 | Universal Input | 3 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 22 | 3 | Universal Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 22 | 4 | Universal Input | 3 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 22 | 5 | Universal Input | 3 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 22 | 6 | Universal Input | 3 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 22 | 7 | Universal Input | 3 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 22 | 8 | Universal Input | 3 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 22 | 9 | Universal Input | 3 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 22 | 10 | Universal Input | 3 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 22 | 11 | Universal Input | 3 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 22 | 12 | Universal Input | 3 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 22 | 13 | Universal Input | 3 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 22 | 14 | Universal Input | 3 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 22 | 15 | Universal Input | 3 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 22 | 16 | Universal Input | 3 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 22 | 17 | Universal Input | 3 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 22 | 18 | Universal Input | 3 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 22 | 27 | Universal Input | 3 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 22 | 28 | Universal Input | 3 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 22 | 29 | Universal Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 22 | 30 | Universal Input | 3 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 22 | 31 | Universal Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 22 | 32 | Universal Input | 3 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 22 | 33 | Universal Input | 3 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 22 | 34 | Universal Input | 3 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 22 | 35 | Universal Input | 3 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 22 | 36 | Universal Input | 3 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 22 | 37 | Universal Input | 3 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 22 | 38 | Universal Input | 3 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 22 | 46 | Universal Input | 3 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 22 | 48 | Universal Input | 3 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 22 | 49 | Universal Input | 3 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 22 | 50 | Universal Input | 3 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 22 | 51 | Universal Input | 3 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 22 | 52 | Universal Input | 3 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 22 | 53 | Universal Input | 3 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 23 | 1 | Universal Input | 3 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 23 | 2 | Universal Input | 3 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 23 | 3 | Universal Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 23 | 4 | Universal Input | 3 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 23 | 5 | Universal Input | 3 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 23 | 6 | Universal Input | 3 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 23 | 7 | Universal Input | 3 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 23 | 8 | Universal Input | 3 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 23 | 9 | Universal Input | 3 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 23 | 10 | Universal Input | 3 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 23 | 11 | Universal Input | 3 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 23 | 12 | Universal Input | 3 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 23 | 13 | Universal Input | 3 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 23 | 14 | Universal Input | 3 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 23 | 15 | Universal Input | 3 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 23 | 16 | Universal Input | 3 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 23 | 17 | Universal Input | 3 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 23 | 18 | Universal Input | 3 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 23 | 27 | Universal Input | 3 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 23 | 28 | Universal Input | 3 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 23 | 29 | Universal Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 23 | 30 | Universal Input | 3 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 23 | 31 | Universal Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 23 | 32 | Universal Input | 3 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 23 | 33 | Universal Input | 3 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 23 | 34 | Universal Input | 3 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 23 | 35 | Universal Input | 3 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 23 | 36 | Universal Input | 3 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 23 | 37 | Universal Input | 3 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 23 | 38 | Universal Input | 3 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 23 | 46 | Universal Input | 3 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 23 | 48 | Universal Input | 3 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 23 | 49 | Universal Input | 3 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 23 | 50 | Universal Input | 3 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 23 | 51 | Universal Input | 3 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 23 | 52 | Universal Input | 3 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 23 | 53 | Universal Input | 3 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 24 | 1 | Universal Input | 3 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 24 | 2 | Universal Input | 3 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 24 | 3 | Universal Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 24 | 4 | Universal Input | 3 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 24 | 5 | Universal Input | 3 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 24 | 6 | Universal Input | 3 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 24 | 7 | Universal Input | 3 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 24 | 8 | Universal Input | 3 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 24 | 9 | Universal Input | 3 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 24 | 10 | Universal Input | 3 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 24 | 11 | Universal Input | 3 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 24 | 12 | Universal Input | 3 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 24 | 13 | Universal Input | 3 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 24 | 14 | Universal Input | 3 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 24 | 15 | Universal Input | 3 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 24 | 16 | Universal Input | 3 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 24 | 17 | Universal Input | 3 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 24 | 18 | Universal Input | 3 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 24 | 27 | Universal Input | 3 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 24 | 28 | Universal Input | 3 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 24 | 29 | Universal Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 24 | 30 | Universal Input | 3 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 24 | 31 | Universal Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 24 | 32 | Universal Input | 3 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 24 | 33 | Universal Input | 3 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 24 | 34 | Universal Input | 3 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 24 | 35 | Universal Input | 3 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 24 | 36 | Universal Input | 3 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 24 | 37 | Universal Input | 3 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 24 | 38 | Universal Input | 3 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 24 | 46 | Universal Input | 3 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 24 | 48 | Universal Input | 3 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 24 | 49 | Universal Input | 3 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 24 | 50 | Universal Input | 3 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 24 | 51 | Universal Input | 3 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 24 | 52 | Universal Input | 3 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 24 | 53 | Universal Input | 3 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 31 | 1 | Universal Input | 4 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 31 | 2 | Universal Input | 4 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 31 | 3 | Universal Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 31 | 4 | Universal Input | 4 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 31 | 5 | Universal Input | 4 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 31 | 6 | Universal Input | 4 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 31 | 7 | Universal Input | 4 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 31 | 8 | Universal Input | 4 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 31 | 9 | Universal Input | 4 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 31 | 10 | Universal Input | 4 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 31 | 11 | Universal Input | 4 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 31 | 12 | Universal Input | 4 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 31 | 13 | Universal Input | 4 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 31 | 14 | Universal Input | 4 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 31 | 15 | Universal Input | 4 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 31 | 16 | Universal Input | 4 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 31 | 17 | Universal Input | 4 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 31 | 18 | Universal Input | 4 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 31 | 27 | Universal Input | 4 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 31 | 28 | Universal Input | 4 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 31 | 29 | Universal Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 31 | 30 | Universal Input | 4 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 31 | 31 | Universal Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 31 | 32 | Universal Input | 4 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 31 | 33 | Universal Input | 4 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 31 | 34 | Universal Input | 4 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 31 | 35 | Universal Input | 4 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 31 | 36 | Universal Input | 4 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 31 | 37 | Universal Input | 4 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 31 | 38 | Universal Input | 4 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 31 | 46 | Universal Input | 4 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 31 | 48 | Universal Input | 4 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 31 | 49 | Universal Input | 4 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 31 | 50 | Universal Input | 4 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 31 | 51 | Universal Input | 4 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 31 | 52 | Universal Input | 4 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 31 | 53 | Universal Input | 4 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 32 | 1 | Universal Input | 4 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 32 | 2 | Universal Input | 4 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 32 | 3 | Universal Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 32 | 4 | Universal Input | 4 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 32 | 5 | Universal Input | 4 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 32 | 6 | Universal Input | 4 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 32 | 7 | Universal Input | 4 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 32 | 8 | Universal Input | 4 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 32 | 9 | Universal Input | 4 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 32 | 10 | Universal Input | 4 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 32 | 11 | Universal Input | 4 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 32 | 12 | Universal Input | 4 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 32 | 13 | Universal Input | 4 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 32 | 14 | Universal Input | 4 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 32 | 15 | Universal Input | 4 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 32 | 16 | Universal Input | 4 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 32 | 17 | Universal Input | 4 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 32 | 18 | Universal Input | 4 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 32 | 27 | Universal Input | 4 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 32 | 28 | Universal Input | 4 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 32 | 29 | Universal Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 32 | 30 | Universal Input | 4 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 32 | 31 | Universal Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 32 | 32 | Universal Input | 4 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 32 | 33 | Universal Input | 4 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 32 | 34 | Universal Input | 4 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 32 | 35 | Universal Input | 4 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 32 | 36 | Universal Input | 4 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 32 | 37 | Universal Input | 4 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 32 | 38 | Universal Input | 4 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 32 | 46 | Universal Input | 4 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 32 | 48 | Universal Input | 4 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 32 | 49 | Universal Input | 4 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 32 | 50 | Universal Input | 4 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 32 | 51 | Universal Input | 4 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 32 | 52 | Universal Input | 4 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 32 | 53 | Universal Input | 4 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 33 | 1 | Universal Input | 4 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 33 | 2 | Universal Input | 4 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 33 | 3 | Universal Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 33 | 4 | Universal Input | 4 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 33 | 5 | Universal Input | 4 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 33 | 6 | Universal Input | 4 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 33 | 7 | Universal Input | 4 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 33 | 8 | Universal Input | 4 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 33 | 9 | Universal Input | 4 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 33 | 10 | Universal Input | 4 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 33 | 11 | Universal Input | 4 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 33 | 12 | Universal Input | 4 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 33 | 13 | Universal Input | 4 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 33 | 14 | Universal Input | 4 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 33 | 15 | Universal Input | 4 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 33 | 16 | Universal Input | 4 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 33 | 17 | Universal Input | 4 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 33 | 18 | Universal Input | 4 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 33 | 27 | Universal Input | 4 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 33 | 28 | Universal Input | 4 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 33 | 29 | Universal Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 33 | 30 | Universal Input | 4 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 33 | 31 | Universal Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 33 | 32 | Universal Input | 4 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 33 | 33 | Universal Input | 4 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 33 | 34 | Universal Input | 4 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 33 | 35 | Universal Input | 4 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 33 | 36 | Universal Input | 4 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 33 | 37 | Universal Input | 4 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 33 | 38 | Universal Input | 4 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 33 | 46 | Universal Input | 4 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 33 | 48 | Universal Input | 4 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 33 | 49 | Universal Input | 4 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 33 | 50 | Universal Input | 4 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 33 | 51 | Universal Input | 4 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 33 | 52 | Universal Input | 4 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 33 | 53 | Universal Input | 4 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 34 | 1 | Universal Input | 4 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 34 | 2 | Universal Input | 4 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 34 | 3 | Universal Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 34 | 4 | Universal Input | 4 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 34 | 5 | Universal Input | 4 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 34 | 6 | Universal Input | 4 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 34 | 7 | Universal Input | 4 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 34 | 8 | Universal Input | 4 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 34 | 9 | Universal Input | 4 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 34 | 10 | Universal Input | 4 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 34 | 11 | Universal Input | 4 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 34 | 12 | Universal Input | 4 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 34 | 13 | Universal Input | 4 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 34 | 14 | Universal Input | 4 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 34 | 15 | Universal Input | 4 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 34 | 16 | Universal Input | 4 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 34 | 17 | Universal Input | 4 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 34 | 18 | Universal Input | 4 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 34 | 27 | Universal Input | 4 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 34 | 28 | Universal Input | 4 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 34 | 29 | Universal Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 34 | 30 | Universal Input | 4 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 34 | 31 | Universal Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 34 | 32 | Universal Input | 4 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 34 | 33 | Universal Input | 4 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 34 | 34 | Universal Input | 4 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 34 | 35 | Universal Input | 4 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 34 | 36 | Universal Input | 4 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 34 | 37 | Universal Input | 4 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 34 | 38 | Universal Input | 4 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 34 | 46 | Universal Input | 4 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 34 | 48 | Universal Input | 4 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 34 | 49 | Universal Input | 4 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 34 | 50 | Universal Input | 4 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 34 | 51 | Universal Input | 4 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 34 | 52 | Universal Input | 4 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 34 | 53 | Universal Input | 4 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 41 | 1 | Universal Input | 5 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 41 | 2 | Universal Input | 5 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 41 | 3 | Universal Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 41 | 4 | Universal Input | 5 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 41 | 5 | Universal Input | 5 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 41 | 6 | Universal Input | 5 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 41 | 7 | Universal Input | 5 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 41 | 8 | Universal Input | 5 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 41 | 9 | Universal Input | 5 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 41 | 10 | Universal Input | 5 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 41 | 11 | Universal Input | 5 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 41 | 12 | Universal Input | 5 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 41 | 13 | Universal Input | 5 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 41 | 14 | Universal Input | 5 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 41 | 15 | Universal Input | 5 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 41 | 16 | Universal Input | 5 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 41 | 17 | Universal Input | 5 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 41 | 18 | Universal Input | 5 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 41 | 27 | Universal Input | 5 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 41 | 28 | Universal Input | 5 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 41 | 29 | Universal Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 41 | 30 | Universal Input | 5 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 41 | 31 | Universal Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 41 | 32 | Universal Input | 5 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 41 | 33 | Universal Input | 5 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 41 | 34 | Universal Input | 5 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 41 | 35 | Universal Input | 5 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 41 | 36 | Universal Input | 5 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 41 | 37 | Universal Input | 5 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 41 | 38 | Universal Input | 5 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 41 | 46 | Universal Input | 5 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 41 | 48 | Universal Input | 5 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 41 | 49 | Universal Input | 5 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 41 | 50 | Universal Input | 5 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 41 | 51 | Universal Input | 5 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 41 | 52 | Universal Input | 5 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 41 | 53 | Universal Input | 5 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 42 | 1 | Universal Input | 5 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 42 | 2 | Universal Input | 5 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 42 | 3 | Universal Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 42 | 4 | Universal Input | 5 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 42 | 5 | Universal Input | 5 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 42 | 6 | Universal Input | 5 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 42 | 7 | Universal Input | 5 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 42 | 8 | Universal Input | 5 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 42 | 9 | Universal Input | 5 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 42 | 10 | Universal Input | 5 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 42 | 11 | Universal Input | 5 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 42 | 12 | Universal Input | 5 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 42 | 13 | Universal Input | 5 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 42 | 14 | Universal Input | 5 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 42 | 15 | Universal Input | 5 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 42 | 16 | Universal Input | 5 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 42 | 17 | Universal Input | 5 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 42 | 18 | Universal Input | 5 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 42 | 27 | Universal Input | 5 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 42 | 28 | Universal Input | 5 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 42 | 29 | Universal Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 42 | 30 | Universal Input | 5 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 42 | 31 | Universal Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 42 | 32 | Universal Input | 5 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 42 | 33 | Universal Input | 5 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 42 | 34 | Universal Input | 5 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 42 | 35 | Universal Input | 5 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 42 | 36 | Universal Input | 5 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 42 | 37 | Universal Input | 5 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 42 | 38 | Universal Input | 5 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 42 | 46 | Universal Input | 5 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 42 | 48 | Universal Input | 5 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 42 | 49 | Universal Input | 5 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 42 | 50 | Universal Input | 5 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 42 | 51 | Universal Input | 5 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 42 | 52 | Universal Input | 5 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 42 | 53 | Universal Input | 5 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 43 | 1 | Universal Input | 5 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 43 | 2 | Universal Input | 5 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 43 | 3 | Universal Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 43 | 4 | Universal Input | 5 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 43 | 5 | Universal Input | 5 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 43 | 6 | Universal Input | 5 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 43 | 7 | Universal Input | 5 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 43 | 8 | Universal Input | 5 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 43 | 9 | Universal Input | 5 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 43 | 10 | Universal Input | 5 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 43 | 11 | Universal Input | 5 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 43 | 12 | Universal Input | 5 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 43 | 13 | Universal Input | 5 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 43 | 14 | Universal Input | 5 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 43 | 15 | Universal Input | 5 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 43 | 16 | Universal Input | 5 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 43 | 17 | Universal Input | 5 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 43 | 18 | Universal Input | 5 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 43 | 27 | Universal Input | 5 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 43 | 28 | Universal Input | 5 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 43 | 29 | Universal Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 43 | 30 | Universal Input | 5 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 43 | 31 | Universal Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 43 | 32 | Universal Input | 5 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 43 | 33 | Universal Input | 5 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 43 | 34 | Universal Input | 5 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 43 | 35 | Universal Input | 5 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 43 | 36 | Universal Input | 5 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 43 | 37 | Universal Input | 5 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 43 | 38 | Universal Input | 5 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 43 | 46 | Universal Input | 5 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 43 | 48 | Universal Input | 5 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 43 | 49 | Universal Input | 5 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 43 | 50 | Universal Input | 5 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 43 | 51 | Universal Input | 5 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 43 | 52 | Universal Input | 5 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 43 | 53 | Universal Input | 5 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 44 | 1 | Universal Input | 5 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 44 | 2 | Universal Input | 5 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 44 | 3 | Universal Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 44 | 4 | Universal Input | 5 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 44 | 5 | Universal Input | 5 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 44 | 6 | Universal Input | 5 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 44 | 7 | Universal Input | 5 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 44 | 8 | Universal Input | 5 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 44 | 9 | Universal Input | 5 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 44 | 10 | Universal Input | 5 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 44 | 11 | Universal Input | 5 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 44 | 12 | Universal Input | 5 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 44 | 13 | Universal Input | 5 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 44 | 14 | Universal Input | 5 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 44 | 15 | Universal Input | 5 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 44 | 16 | Universal Input | 5 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 44 | 17 | Universal Input | 5 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 44 | 18 | Universal Input | 5 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 44 | 27 | Universal Input | 5 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 44 | 28 | Universal Input | 5 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 44 | 29 | Universal Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 44 | 30 | Universal Input | 5 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 44 | 31 | Universal Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 44 | 32 | Universal Input | 5 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 44 | 33 | Universal Input | 5 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 44 | 34 | Universal Input | 5 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 44 | 35 | Universal Input | 5 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 44 | 36 | Universal Input | 5 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 44 | 37 | Universal Input | 5 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 44 | 38 | Universal Input | 5 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 44 | 46 | Universal Input | 5 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 44 | 48 | Universal Input | 5 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 44 | 49 | Universal Input | 5 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 44 | 50 | Universal Input | 5 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 44 | 51 | Universal Input | 5 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 44 | 52 | Universal Input | 5 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 44 | 53 | Universal Input | 5 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 51 | 1 | Universal Input | 6 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 51 | 2 | Universal Input | 6 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 51 | 3 | Universal Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 51 | 4 | Universal Input | 6 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 51 | 5 | Universal Input | 6 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 51 | 6 | Universal Input | 6 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 51 | 7 | Universal Input | 6 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 51 | 8 | Universal Input | 6 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 51 | 9 | Universal Input | 6 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 51 | 10 | Universal Input | 6 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 51 | 11 | Universal Input | 6 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 51 | 12 | Universal Input | 6 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 51 | 13 | Universal Input | 6 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 51 | 14 | Universal Input | 6 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 51 | 15 | Universal Input | 6 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 51 | 16 | Universal Input | 6 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 51 | 17 | Universal Input | 6 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 51 | 18 | Universal Input | 6 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 51 | 27 | Universal Input | 6 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 51 | 28 | Universal Input | 6 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 51 | 29 | Universal Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 51 | 30 | Universal Input | 6 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 51 | 31 | Universal Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 51 | 32 | Universal Input | 6 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 51 | 33 | Universal Input | 6 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 51 | 34 | Universal Input | 6 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 51 | 35 | Universal Input | 6 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 51 | 36 | Universal Input | 6 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 51 | 37 | Universal Input | 6 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 51 | 38 | Universal Input | 6 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 51 | 46 | Universal Input | 6 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 51 | 48 | Universal Input | 6 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 51 | 49 | Universal Input | 6 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 51 | 50 | Universal Input | 6 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 51 | 51 | Universal Input | 6 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 51 | 52 | Universal Input | 6 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 51 | 53 | Universal Input | 6 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 52 | 1 | Universal Input | 6 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 52 | 2 | Universal Input | 6 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 52 | 3 | Universal Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 52 | 4 | Universal Input | 6 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 52 | 5 | Universal Input | 6 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 52 | 6 | Universal Input | 6 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 52 | 7 | Universal Input | 6 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 52 | 8 | Universal Input | 6 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 52 | 9 | Universal Input | 6 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 52 | 10 | Universal Input | 6 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 52 | 11 | Universal Input | 6 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 52 | 12 | Universal Input | 6 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 52 | 13 | Universal Input | 6 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 52 | 14 | Universal Input | 6 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 52 | 15 | Universal Input | 6 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 52 | 16 | Universal Input | 6 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 52 | 17 | Universal Input | 6 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 52 | 18 | Universal Input | 6 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 52 | 27 | Universal Input | 6 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 52 | 28 | Universal Input | 6 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 52 | 29 | Universal Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 52 | 30 | Universal Input | 6 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 52 | 31 | Universal Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 52 | 32 | Universal Input | 6 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 52 | 33 | Universal Input | 6 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 52 | 34 | Universal Input | 6 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 52 | 35 | Universal Input | 6 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 52 | 36 | Universal Input | 6 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 52 | 37 | Universal Input | 6 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 52 | 38 | Universal Input | 6 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 52 | 46 | Universal Input | 6 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 52 | 48 | Universal Input | 6 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 52 | 49 | Universal Input | 6 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 52 | 50 | Universal Input | 6 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 52 | 51 | Universal Input | 6 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 52 | 52 | Universal Input | 6 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 52 | 53 | Universal Input | 6 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 53 | 1 | Universal Input | 6 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 53 | 2 | Universal Input | 6 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 53 | 3 | Universal Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 53 | 4 | Universal Input | 6 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 53 | 5 | Universal Input | 6 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 53 | 6 | Universal Input | 6 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 53 | 7 | Universal Input | 6 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 53 | 8 | Universal Input | 6 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 53 | 9 | Universal Input | 6 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 53 | 10 | Universal Input | 6 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 53 | 11 | Universal Input | 6 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 53 | 12 | Universal Input | 6 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 53 | 13 | Universal Input | 6 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 53 | 14 | Universal Input | 6 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 53 | 15 | Universal Input | 6 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 53 | 16 | Universal Input | 6 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 53 | 17 | Universal Input | 6 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 53 | 18 | Universal Input | 6 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 53 | 27 | Universal Input | 6 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 53 | 28 | Universal Input | 6 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 53 | 29 | Universal Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 53 | 30 | Universal Input | 6 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 53 | 31 | Universal Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 53 | 32 | Universal Input | 6 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 53 | 33 | Universal Input | 6 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 53 | 34 | Universal Input | 6 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 53 | 35 | Universal Input | 6 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 53 | 36 | Universal Input | 6 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 53 | 37 | Universal Input | 6 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 53 | 38 | Universal Input | 6 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 53 | 46 | Universal Input | 6 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 53 | 48 | Universal Input | 6 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 53 | 49 | Universal Input | 6 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 53 | 50 | Universal Input | 6 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 53 | 51 | Universal Input | 6 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 53 | 52 | Universal Input | 6 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 53 | 53 | Universal Input | 6 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 54 | 1 | Universal Input | 6 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 54 | 2 | Universal Input | 6 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
155 | 54 | 3 | Universal Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
155 | 54 | 4 | Universal Input | 6 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
155 | 54 | 5 | Universal Input | 6 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | UINT | R/W | 54 | Yes
155 | 54 | 6 | Universal Input | 6 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 54 | Yes
155 | 54 | 7 | Universal Input | 6 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | UINT | R/W | 54 | Yes
155 | 54 | 8 | Universal Input | 6 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 54 | 9 | Universal Input | 6 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | REAL | R/W | 54 | Yes
155 | 54 | 10 | Universal Input | 6 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 54 | 11 | Universal Input | 6 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | REAL | R/W | 54 | Yes
155 | 54 | 12 | Universal Input | 6 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | UINT | R/W | 54 | Yes
155 | 54 | 13 | Universal Input | 6 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 54 | 14 | Universal Input | 6 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
155 | 54 | 15 | Universal Input | 6 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | UINT | R/W | 54 | Yes
155 | 54 | 16 | Universal Input | 6 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
155 | 54 | 17 | Universal Input | 6 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
155 | 54 | 18 | Universal Input | 6 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
155 | 54 | 27 | Universal Input | 6 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
155 | 54 | 28 | Universal Input | 6 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
155 | 54 | 29 | Universal Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 54 | 30 | Universal Input | 6 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
155 | 54 | 31 | Universal Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 54 | 32 | Universal Input | 6 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 54 | 33 | Universal Input | 6 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 54 | 34 | Universal Input | 6 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
155 | 54 | 35 | Universal Input | 6 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 54 | 36 | Universal Input | 6 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
155 | 54 | 37 | Universal Input | 6 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 54 | 38 | Universal Input | 6 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
155 | 54 | 46 | Universal Input | 6 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
155 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
155 | 54 | 48 | Universal Input | 6 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | UINT | R | 54 | No
155 | 54 | 49 | Universal Input | 6 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
155 | 54 | 50 | Universal Input | 6 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 54 | 51 | Universal Input | 6 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 54 | 52 | Universal Input | 6 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
155 | 54 | 53 | Universal Input | 6 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 1 | 1 | Thermistor Input | 1 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 1 | 2 | Thermistor Input | 1 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 1 | 3 | Thermistor Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 1 | 4 | Thermistor Input | 1 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 1 | 5 | Thermistor Input | 1 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 1 | 6 | Thermistor Input | 1 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 1 | 7 | Thermistor Input | 1 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 1 | 8 | Thermistor Input | 1 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 1 | 9 | Thermistor Input | 1 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 1 | 10 | Thermistor Input | 1 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 1 | 14 | Thermistor Input | 1 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 1 | 16 | Thermistor Input | 1 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 1 | 17 | Thermistor Input | 1 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 1 | 18 | Thermistor Input | 1 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 1 | 27 | Thermistor Input | 1 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 1 | 28 | Thermistor Input | 1 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 1 | 29 | Thermistor Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 1 | 30 | Thermistor Input | 1 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 1 | 31 | Thermistor Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 1 | 32 | Thermistor Input | 1 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 1 | 33 | Thermistor Input | 1 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 1 | 34 | Thermistor Input | 1 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 1 | 35 | Thermistor Input | 1 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 1 | 36 | Thermistor Input | 1 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 1 | 37 | Thermistor Input | 1 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 1 | 38 | Thermistor Input | 1 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 1 | 46 | Thermistor Input | 1 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 1 | 48 | Thermistor Input | 1 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 1 | 49 | Thermistor Input | 1 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 1 | 50 | Thermistor Input | 1 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 1 | 51 | Thermistor Input | 1 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 1 | 52 | Thermistor Input | 1 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 1 | 53 | Thermistor Input | 1 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 2 | 1 | Thermistor Input | 1 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 2 | 2 | Thermistor Input | 1 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 2 | 3 | Thermistor Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 2 | 4 | Thermistor Input | 1 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 2 | 5 | Thermistor Input | 1 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 2 | 6 | Thermistor Input | 1 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 2 | 7 | Thermistor Input | 1 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 2 | 8 | Thermistor Input | 1 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 2 | 9 | Thermistor Input | 1 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 2 | 10 | Thermistor Input | 1 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 2 | 14 | Thermistor Input | 1 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 2 | 16 | Thermistor Input | 1 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 2 | 17 | Thermistor Input | 1 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 2 | 18 | Thermistor Input | 1 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 2 | 27 | Thermistor Input | 1 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 2 | 28 | Thermistor Input | 1 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 2 | 29 | Thermistor Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 2 | 30 | Thermistor Input | 1 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 2 | 31 | Thermistor Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 2 | 32 | Thermistor Input | 1 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 2 | 33 | Thermistor Input | 1 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 2 | 34 | Thermistor Input | 1 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 2 | 35 | Thermistor Input | 1 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 2 | 36 | Thermistor Input | 1 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 2 | 37 | Thermistor Input | 1 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 2 | 38 | Thermistor Input | 1 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 2 | 46 | Thermistor Input | 1 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 2 | 48 | Thermistor Input | 1 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 2 | 49 | Thermistor Input | 1 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 2 | 50 | Thermistor Input | 1 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 2 | 51 | Thermistor Input | 1 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 2 | 52 | Thermistor Input | 1 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 2 | 53 | Thermistor Input | 1 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 3 | 1 | Thermistor Input | 1 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 3 | 2 | Thermistor Input | 1 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 3 | 3 | Thermistor Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 3 | 4 | Thermistor Input | 1 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 3 | 5 | Thermistor Input | 1 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 3 | 6 | Thermistor Input | 1 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 3 | 7 | Thermistor Input | 1 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 3 | 8 | Thermistor Input | 1 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 3 | 9 | Thermistor Input | 1 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 3 | 10 | Thermistor Input | 1 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 3 | 14 | Thermistor Input | 1 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 3 | 16 | Thermistor Input | 1 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 3 | 17 | Thermistor Input | 1 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 3 | 18 | Thermistor Input | 1 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 3 | 27 | Thermistor Input | 1 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 3 | 28 | Thermistor Input | 1 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 3 | 29 | Thermistor Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 3 | 30 | Thermistor Input | 1 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 3 | 31 | Thermistor Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 3 | 32 | Thermistor Input | 1 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 3 | 33 | Thermistor Input | 1 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 3 | 34 | Thermistor Input | 1 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 3 | 35 | Thermistor Input | 1 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 3 | 36 | Thermistor Input | 1 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 3 | 37 | Thermistor Input | 1 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 3 | 38 | Thermistor Input | 1 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 3 | 46 | Thermistor Input | 1 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 3 | 48 | Thermistor Input | 1 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 3 | 49 | Thermistor Input | 1 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 3 | 50 | Thermistor Input | 1 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 3 | 51 | Thermistor Input | 1 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 3 | 52 | Thermistor Input | 1 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 3 | 53 | Thermistor Input | 1 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 4 | 1 | Thermistor Input | 1 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 4 | 2 | Thermistor Input | 1 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 4 | 3 | Thermistor Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 4 | 4 | Thermistor Input | 1 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 4 | 5 | Thermistor Input | 1 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 4 | 6 | Thermistor Input | 1 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 4 | 7 | Thermistor Input | 1 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 4 | 8 | Thermistor Input | 1 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 4 | 9 | Thermistor Input | 1 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 4 | 10 | Thermistor Input | 1 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 4 | 14 | Thermistor Input | 1 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 4 | 16 | Thermistor Input | 1 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 4 | 17 | Thermistor Input | 1 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 4 | 18 | Thermistor Input | 1 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 4 | 27 | Thermistor Input | 1 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 4 | 28 | Thermistor Input | 1 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 4 | 29 | Thermistor Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 4 | 30 | Thermistor Input | 1 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 4 | 31 | Thermistor Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 4 | 32 | Thermistor Input | 1 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 4 | 33 | Thermistor Input | 1 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 4 | 34 | Thermistor Input | 1 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 4 | 35 | Thermistor Input | 1 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 4 | 36 | Thermistor Input | 1 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 4 | 37 | Thermistor Input | 1 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 4 | 38 | Thermistor Input | 1 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 4 | 46 | Thermistor Input | 1 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 4 | 48 | Thermistor Input | 1 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 4 | 49 | Thermistor Input | 1 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 4 | 50 | Thermistor Input | 1 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 4 | 51 | Thermistor Input | 1 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 4 | 52 | Thermistor Input | 1 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 4 | 53 | Thermistor Input | 1 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 11 | 1 | Thermistor Input | 2 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 11 | 2 | Thermistor Input | 2 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 11 | 3 | Thermistor Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 11 | 4 | Thermistor Input | 2 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 11 | 5 | Thermistor Input | 2 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 11 | 6 | Thermistor Input | 2 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 11 | 7 | Thermistor Input | 2 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 11 | 8 | Thermistor Input | 2 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 11 | 9 | Thermistor Input | 2 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 11 | 10 | Thermistor Input | 2 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 11 | 14 | Thermistor Input | 2 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 11 | 16 | Thermistor Input | 2 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 11 | 17 | Thermistor Input | 2 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 11 | 18 | Thermistor Input | 2 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 11 | 27 | Thermistor Input | 2 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 11 | 28 | Thermistor Input | 2 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 11 | 29 | Thermistor Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 11 | 30 | Thermistor Input | 2 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 11 | 31 | Thermistor Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 11 | 32 | Thermistor Input | 2 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 11 | 33 | Thermistor Input | 2 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 11 | 34 | Thermistor Input | 2 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 11 | 35 | Thermistor Input | 2 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 11 | 36 | Thermistor Input | 2 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 11 | 37 | Thermistor Input | 2 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 11 | 38 | Thermistor Input | 2 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 11 | 46 | Thermistor Input | 2 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 11 | 48 | Thermistor Input | 2 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 11 | 49 | Thermistor Input | 2 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 11 | 50 | Thermistor Input | 2 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 11 | 51 | Thermistor Input | 2 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 11 | 52 | Thermistor Input | 2 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 11 | 53 | Thermistor Input | 2 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 12 | 1 | Thermistor Input | 2 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 12 | 2 | Thermistor Input | 2 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 12 | 3 | Thermistor Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 12 | 4 | Thermistor Input | 2 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 12 | 5 | Thermistor Input | 2 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 12 | 6 | Thermistor Input | 2 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 12 | 7 | Thermistor Input | 2 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 12 | 8 | Thermistor Input | 2 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 12 | 9 | Thermistor Input | 2 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 12 | 10 | Thermistor Input | 2 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 12 | 14 | Thermistor Input | 2 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 12 | 16 | Thermistor Input | 2 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 12 | 17 | Thermistor Input | 2 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 12 | 18 | Thermistor Input | 2 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 12 | 27 | Thermistor Input | 2 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 12 | 28 | Thermistor Input | 2 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 12 | 29 | Thermistor Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 12 | 30 | Thermistor Input | 2 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 12 | 31 | Thermistor Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 12 | 32 | Thermistor Input | 2 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 12 | 33 | Thermistor Input | 2 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 12 | 34 | Thermistor Input | 2 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 12 | 35 | Thermistor Input | 2 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 12 | 36 | Thermistor Input | 2 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 12 | 37 | Thermistor Input | 2 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 12 | 38 | Thermistor Input | 2 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 12 | 46 | Thermistor Input | 2 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 12 | 48 | Thermistor Input | 2 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 12 | 49 | Thermistor Input | 2 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 12 | 50 | Thermistor Input | 2 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 12 | 51 | Thermistor Input | 2 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 12 | 52 | Thermistor Input | 2 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 12 | 53 | Thermistor Input | 2 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 13 | 1 | Thermistor Input | 2 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 13 | 2 | Thermistor Input | 2 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 13 | 3 | Thermistor Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 13 | 4 | Thermistor Input | 2 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 13 | 5 | Thermistor Input | 2 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 13 | 6 | Thermistor Input | 2 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 13 | 7 | Thermistor Input | 2 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 13 | 8 | Thermistor Input | 2 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 13 | 9 | Thermistor Input | 2 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 13 | 10 | Thermistor Input | 2 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 13 | 14 | Thermistor Input | 2 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 13 | 16 | Thermistor Input | 2 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 13 | 17 | Thermistor Input | 2 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 13 | 18 | Thermistor Input | 2 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 13 | 27 | Thermistor Input | 2 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 13 | 28 | Thermistor Input | 2 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 13 | 29 | Thermistor Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 13 | 30 | Thermistor Input | 2 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 13 | 31 | Thermistor Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 13 | 32 | Thermistor Input | 2 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 13 | 33 | Thermistor Input | 2 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 13 | 34 | Thermistor Input | 2 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 13 | 35 | Thermistor Input | 2 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 13 | 36 | Thermistor Input | 2 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 13 | 37 | Thermistor Input | 2 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 13 | 38 | Thermistor Input | 2 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 13 | 46 | Thermistor Input | 2 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 13 | 48 | Thermistor Input | 2 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 13 | 49 | Thermistor Input | 2 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 13 | 50 | Thermistor Input | 2 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 13 | 51 | Thermistor Input | 2 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 13 | 52 | Thermistor Input | 2 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 13 | 53 | Thermistor Input | 2 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 14 | 1 | Thermistor Input | 2 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 14 | 2 | Thermistor Input | 2 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 14 | 3 | Thermistor Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 14 | 4 | Thermistor Input | 2 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 14 | 5 | Thermistor Input | 2 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 14 | 6 | Thermistor Input | 2 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 14 | 7 | Thermistor Input | 2 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 14 | 8 | Thermistor Input | 2 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 14 | 9 | Thermistor Input | 2 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 14 | 10 | Thermistor Input | 2 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 14 | 14 | Thermistor Input | 2 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 14 | 16 | Thermistor Input | 2 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 14 | 17 | Thermistor Input | 2 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 14 | 18 | Thermistor Input | 2 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 14 | 27 | Thermistor Input | 2 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 14 | 28 | Thermistor Input | 2 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 14 | 29 | Thermistor Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 14 | 30 | Thermistor Input | 2 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 14 | 31 | Thermistor Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 14 | 32 | Thermistor Input | 2 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 14 | 33 | Thermistor Input | 2 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 14 | 34 | Thermistor Input | 2 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 14 | 35 | Thermistor Input | 2 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 14 | 36 | Thermistor Input | 2 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 14 | 37 | Thermistor Input | 2 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 14 | 38 | Thermistor Input | 2 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 14 | 46 | Thermistor Input | 2 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 14 | 48 | Thermistor Input | 2 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 14 | 49 | Thermistor Input | 2 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 14 | 50 | Thermistor Input | 2 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 14 | 51 | Thermistor Input | 2 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 14 | 52 | Thermistor Input | 2 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 14 | 53 | Thermistor Input | 2 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 21 | 1 | Thermistor Input | 3 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 21 | 2 | Thermistor Input | 3 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 21 | 3 | Thermistor Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 21 | 4 | Thermistor Input | 3 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 21 | 5 | Thermistor Input | 3 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 21 | 6 | Thermistor Input | 3 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 21 | 7 | Thermistor Input | 3 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 21 | 8 | Thermistor Input | 3 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 21 | 9 | Thermistor Input | 3 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 21 | 10 | Thermistor Input | 3 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 21 | 14 | Thermistor Input | 3 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 21 | 16 | Thermistor Input | 3 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 21 | 17 | Thermistor Input | 3 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 21 | 18 | Thermistor Input | 3 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 21 | 27 | Thermistor Input | 3 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 21 | 28 | Thermistor Input | 3 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 21 | 29 | Thermistor Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 21 | 30 | Thermistor Input | 3 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 21 | 31 | Thermistor Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 21 | 32 | Thermistor Input | 3 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 21 | 33 | Thermistor Input | 3 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 21 | 34 | Thermistor Input | 3 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 21 | 35 | Thermistor Input | 3 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 21 | 36 | Thermistor Input | 3 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 21 | 37 | Thermistor Input | 3 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 21 | 38 | Thermistor Input | 3 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 21 | 46 | Thermistor Input | 3 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 21 | 48 | Thermistor Input | 3 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 21 | 49 | Thermistor Input | 3 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 21 | 50 | Thermistor Input | 3 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 21 | 51 | Thermistor Input | 3 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 21 | 52 | Thermistor Input | 3 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 21 | 53 | Thermistor Input | 3 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 22 | 1 | Thermistor Input | 3 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 22 | 2 | Thermistor Input | 3 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 22 | 3 | Thermistor Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 22 | 4 | Thermistor Input | 3 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 22 | 5 | Thermistor Input | 3 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 22 | 6 | Thermistor Input | 3 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 22 | 7 | Thermistor Input | 3 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 22 | 8 | Thermistor Input | 3 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 22 | 9 | Thermistor Input | 3 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 22 | 10 | Thermistor Input | 3 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 22 | 14 | Thermistor Input | 3 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 22 | 16 | Thermistor Input | 3 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 22 | 17 | Thermistor Input | 3 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 22 | 18 | Thermistor Input | 3 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 22 | 27 | Thermistor Input | 3 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 22 | 28 | Thermistor Input | 3 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 22 | 29 | Thermistor Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 22 | 30 | Thermistor Input | 3 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 22 | 31 | Thermistor Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 22 | 32 | Thermistor Input | 3 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 22 | 33 | Thermistor Input | 3 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 22 | 34 | Thermistor Input | 3 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 22 | 35 | Thermistor Input | 3 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 22 | 36 | Thermistor Input | 3 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 22 | 37 | Thermistor Input | 3 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 22 | 38 | Thermistor Input | 3 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 22 | 46 | Thermistor Input | 3 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 22 | 48 | Thermistor Input | 3 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 22 | 49 | Thermistor Input | 3 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 22 | 50 | Thermistor Input | 3 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 22 | 51 | Thermistor Input | 3 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 22 | 52 | Thermistor Input | 3 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 22 | 53 | Thermistor Input | 3 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 23 | 1 | Thermistor Input | 3 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 23 | 2 | Thermistor Input | 3 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 23 | 3 | Thermistor Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 23 | 4 | Thermistor Input | 3 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 23 | 5 | Thermistor Input | 3 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 23 | 6 | Thermistor Input | 3 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 23 | 7 | Thermistor Input | 3 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 23 | 8 | Thermistor Input | 3 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 23 | 9 | Thermistor Input | 3 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 23 | 10 | Thermistor Input | 3 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 23 | 14 | Thermistor Input | 3 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 23 | 16 | Thermistor Input | 3 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 23 | 17 | Thermistor Input | 3 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 23 | 18 | Thermistor Input | 3 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 23 | 27 | Thermistor Input | 3 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 23 | 28 | Thermistor Input | 3 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 23 | 29 | Thermistor Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 23 | 30 | Thermistor Input | 3 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 23 | 31 | Thermistor Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 23 | 32 | Thermistor Input | 3 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 23 | 33 | Thermistor Input | 3 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 23 | 34 | Thermistor Input | 3 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 23 | 35 | Thermistor Input | 3 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 23 | 36 | Thermistor Input | 3 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 23 | 37 | Thermistor Input | 3 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 23 | 38 | Thermistor Input | 3 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 23 | 46 | Thermistor Input | 3 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 23 | 48 | Thermistor Input | 3 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 23 | 49 | Thermistor Input | 3 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 23 | 50 | Thermistor Input | 3 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 23 | 51 | Thermistor Input | 3 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 23 | 52 | Thermistor Input | 3 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 23 | 53 | Thermistor Input | 3 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 24 | 1 | Thermistor Input | 3 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 24 | 2 | Thermistor Input | 3 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 24 | 3 | Thermistor Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 24 | 4 | Thermistor Input | 3 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 24 | 5 | Thermistor Input | 3 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 24 | 6 | Thermistor Input | 3 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 24 | 7 | Thermistor Input | 3 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 24 | 8 | Thermistor Input | 3 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 24 | 9 | Thermistor Input | 3 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 24 | 10 | Thermistor Input | 3 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 24 | 14 | Thermistor Input | 3 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 24 | 16 | Thermistor Input | 3 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 24 | 17 | Thermistor Input | 3 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 24 | 18 | Thermistor Input | 3 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 24 | 27 | Thermistor Input | 3 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 24 | 28 | Thermistor Input | 3 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 24 | 29 | Thermistor Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 24 | 30 | Thermistor Input | 3 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 24 | 31 | Thermistor Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 24 | 32 | Thermistor Input | 3 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 24 | 33 | Thermistor Input | 3 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 24 | 34 | Thermistor Input | 3 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 24 | 35 | Thermistor Input | 3 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 24 | 36 | Thermistor Input | 3 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 24 | 37 | Thermistor Input | 3 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 24 | 38 | Thermistor Input | 3 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 24 | 46 | Thermistor Input | 3 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 24 | 48 | Thermistor Input | 3 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 24 | 49 | Thermistor Input | 3 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 24 | 50 | Thermistor Input | 3 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 24 | 51 | Thermistor Input | 3 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 24 | 52 | Thermistor Input | 3 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 24 | 53 | Thermistor Input | 3 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 31 | 1 | Thermistor Input | 4 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 31 | 2 | Thermistor Input | 4 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 31 | 3 | Thermistor Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 31 | 4 | Thermistor Input | 4 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 31 | 5 | Thermistor Input | 4 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 31 | 6 | Thermistor Input | 4 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 31 | 7 | Thermistor Input | 4 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 31 | 8 | Thermistor Input | 4 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 31 | 9 | Thermistor Input | 4 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 31 | 10 | Thermistor Input | 4 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 31 | 14 | Thermistor Input | 4 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 31 | 16 | Thermistor Input | 4 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 31 | 17 | Thermistor Input | 4 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 31 | 18 | Thermistor Input | 4 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 31 | 27 | Thermistor Input | 4 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 31 | 28 | Thermistor Input | 4 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 31 | 29 | Thermistor Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 31 | 30 | Thermistor Input | 4 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 31 | 31 | Thermistor Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 31 | 32 | Thermistor Input | 4 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 31 | 33 | Thermistor Input | 4 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 31 | 34 | Thermistor Input | 4 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 31 | 35 | Thermistor Input | 4 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 31 | 36 | Thermistor Input | 4 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 31 | 37 | Thermistor Input | 4 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 31 | 38 | Thermistor Input | 4 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 31 | 46 | Thermistor Input | 4 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 31 | 48 | Thermistor Input | 4 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 31 | 49 | Thermistor Input | 4 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 31 | 50 | Thermistor Input | 4 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 31 | 51 | Thermistor Input | 4 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 31 | 52 | Thermistor Input | 4 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 31 | 53 | Thermistor Input | 4 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 32 | 1 | Thermistor Input | 4 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 32 | 2 | Thermistor Input | 4 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 32 | 3 | Thermistor Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 32 | 4 | Thermistor Input | 4 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 32 | 5 | Thermistor Input | 4 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 32 | 6 | Thermistor Input | 4 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 32 | 7 | Thermistor Input | 4 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 32 | 8 | Thermistor Input | 4 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 32 | 9 | Thermistor Input | 4 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 32 | 10 | Thermistor Input | 4 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 32 | 14 | Thermistor Input | 4 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 32 | 16 | Thermistor Input | 4 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 32 | 17 | Thermistor Input | 4 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 32 | 18 | Thermistor Input | 4 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 32 | 27 | Thermistor Input | 4 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 32 | 28 | Thermistor Input | 4 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 32 | 29 | Thermistor Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 32 | 30 | Thermistor Input | 4 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 32 | 31 | Thermistor Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 32 | 32 | Thermistor Input | 4 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 32 | 33 | Thermistor Input | 4 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 32 | 34 | Thermistor Input | 4 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 32 | 35 | Thermistor Input | 4 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 32 | 36 | Thermistor Input | 4 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 32 | 37 | Thermistor Input | 4 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 32 | 38 | Thermistor Input | 4 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 32 | 46 | Thermistor Input | 4 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 32 | 48 | Thermistor Input | 4 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 32 | 49 | Thermistor Input | 4 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 32 | 50 | Thermistor Input | 4 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 32 | 51 | Thermistor Input | 4 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 32 | 52 | Thermistor Input | 4 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 32 | 53 | Thermistor Input | 4 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 33 | 1 | Thermistor Input | 4 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 33 | 2 | Thermistor Input | 4 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 33 | 3 | Thermistor Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 33 | 4 | Thermistor Input | 4 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 33 | 5 | Thermistor Input | 4 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 33 | 6 | Thermistor Input | 4 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 33 | 7 | Thermistor Input | 4 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 33 | 8 | Thermistor Input | 4 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 33 | 9 | Thermistor Input | 4 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 33 | 10 | Thermistor Input | 4 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 33 | 14 | Thermistor Input | 4 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 33 | 16 | Thermistor Input | 4 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 33 | 17 | Thermistor Input | 4 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 33 | 18 | Thermistor Input | 4 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 33 | 27 | Thermistor Input | 4 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 33 | 28 | Thermistor Input | 4 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 33 | 29 | Thermistor Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 33 | 30 | Thermistor Input | 4 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 33 | 31 | Thermistor Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 33 | 32 | Thermistor Input | 4 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 33 | 33 | Thermistor Input | 4 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 33 | 34 | Thermistor Input | 4 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 33 | 35 | Thermistor Input | 4 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 33 | 36 | Thermistor Input | 4 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 33 | 37 | Thermistor Input | 4 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 33 | 38 | Thermistor Input | 4 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 33 | 46 | Thermistor Input | 4 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 33 | 48 | Thermistor Input | 4 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 33 | 49 | Thermistor Input | 4 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 33 | 50 | Thermistor Input | 4 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 33 | 51 | Thermistor Input | 4 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 33 | 52 | Thermistor Input | 4 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 33 | 53 | Thermistor Input | 4 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 34 | 1 | Thermistor Input | 4 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 34 | 2 | Thermistor Input | 4 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 34 | 3 | Thermistor Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 34 | 4 | Thermistor Input | 4 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 34 | 5 | Thermistor Input | 4 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 34 | 6 | Thermistor Input | 4 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 34 | 7 | Thermistor Input | 4 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 34 | 8 | Thermistor Input | 4 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 34 | 9 | Thermistor Input | 4 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 34 | 10 | Thermistor Input | 4 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 34 | 14 | Thermistor Input | 4 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 34 | 16 | Thermistor Input | 4 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 34 | 17 | Thermistor Input | 4 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 34 | 18 | Thermistor Input | 4 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 34 | 27 | Thermistor Input | 4 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 34 | 28 | Thermistor Input | 4 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 34 | 29 | Thermistor Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 34 | 30 | Thermistor Input | 4 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 34 | 31 | Thermistor Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 34 | 32 | Thermistor Input | 4 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 34 | 33 | Thermistor Input | 4 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 34 | 34 | Thermistor Input | 4 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 34 | 35 | Thermistor Input | 4 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 34 | 36 | Thermistor Input | 4 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 34 | 37 | Thermistor Input | 4 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 34 | 38 | Thermistor Input | 4 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 34 | 46 | Thermistor Input | 4 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 34 | 48 | Thermistor Input | 4 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 34 | 49 | Thermistor Input | 4 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 34 | 50 | Thermistor Input | 4 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 34 | 51 | Thermistor Input | 4 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 34 | 52 | Thermistor Input | 4 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 34 | 53 | Thermistor Input | 4 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 41 | 1 | Thermistor Input | 5 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 41 | 2 | Thermistor Input | 5 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 41 | 3 | Thermistor Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 41 | 4 | Thermistor Input | 5 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 41 | 5 | Thermistor Input | 5 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 41 | 6 | Thermistor Input | 5 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 41 | 7 | Thermistor Input | 5 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 41 | 8 | Thermistor Input | 5 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 41 | 9 | Thermistor Input | 5 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 41 | 10 | Thermistor Input | 5 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 41 | 14 | Thermistor Input | 5 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 41 | 16 | Thermistor Input | 5 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 41 | 17 | Thermistor Input | 5 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 41 | 18 | Thermistor Input | 5 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 41 | 27 | Thermistor Input | 5 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 41 | 28 | Thermistor Input | 5 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 41 | 29 | Thermistor Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 41 | 30 | Thermistor Input | 5 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 41 | 31 | Thermistor Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 41 | 32 | Thermistor Input | 5 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 41 | 33 | Thermistor Input | 5 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 41 | 34 | Thermistor Input | 5 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 41 | 35 | Thermistor Input | 5 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 41 | 36 | Thermistor Input | 5 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 41 | 37 | Thermistor Input | 5 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 41 | 38 | Thermistor Input | 5 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 41 | 46 | Thermistor Input | 5 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 41 | 48 | Thermistor Input | 5 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 41 | 49 | Thermistor Input | 5 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 41 | 50 | Thermistor Input | 5 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 41 | 51 | Thermistor Input | 5 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 41 | 52 | Thermistor Input | 5 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 41 | 53 | Thermistor Input | 5 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 42 | 1 | Thermistor Input | 5 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 42 | 2 | Thermistor Input | 5 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 42 | 3 | Thermistor Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 42 | 4 | Thermistor Input | 5 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 42 | 5 | Thermistor Input | 5 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 42 | 6 | Thermistor Input | 5 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 42 | 7 | Thermistor Input | 5 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 42 | 8 | Thermistor Input | 5 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 42 | 9 | Thermistor Input | 5 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 42 | 10 | Thermistor Input | 5 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 42 | 14 | Thermistor Input | 5 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 42 | 16 | Thermistor Input | 5 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 42 | 17 | Thermistor Input | 5 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 42 | 18 | Thermistor Input | 5 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 42 | 27 | Thermistor Input | 5 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 42 | 28 | Thermistor Input | 5 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 42 | 29 | Thermistor Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 42 | 30 | Thermistor Input | 5 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 42 | 31 | Thermistor Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 42 | 32 | Thermistor Input | 5 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 42 | 33 | Thermistor Input | 5 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 42 | 34 | Thermistor Input | 5 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 42 | 35 | Thermistor Input | 5 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 42 | 36 | Thermistor Input | 5 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 42 | 37 | Thermistor Input | 5 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 42 | 38 | Thermistor Input | 5 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 42 | 46 | Thermistor Input | 5 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 42 | 48 | Thermistor Input | 5 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 42 | 49 | Thermistor Input | 5 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 42 | 50 | Thermistor Input | 5 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 42 | 51 | Thermistor Input | 5 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 42 | 52 | Thermistor Input | 5 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 42 | 53 | Thermistor Input | 5 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 43 | 1 | Thermistor Input | 5 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 43 | 2 | Thermistor Input | 5 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 43 | 3 | Thermistor Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 43 | 4 | Thermistor Input | 5 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 43 | 5 | Thermistor Input | 5 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 43 | 6 | Thermistor Input | 5 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 43 | 7 | Thermistor Input | 5 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 43 | 8 | Thermistor Input | 5 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 43 | 9 | Thermistor Input | 5 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 43 | 10 | Thermistor Input | 5 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 43 | 14 | Thermistor Input | 5 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 43 | 16 | Thermistor Input | 5 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 43 | 17 | Thermistor Input | 5 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 43 | 18 | Thermistor Input | 5 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 43 | 27 | Thermistor Input | 5 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 43 | 28 | Thermistor Input | 5 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 43 | 29 | Thermistor Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 43 | 30 | Thermistor Input | 5 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 43 | 31 | Thermistor Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 43 | 32 | Thermistor Input | 5 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 43 | 33 | Thermistor Input | 5 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 43 | 34 | Thermistor Input | 5 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 43 | 35 | Thermistor Input | 5 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 43 | 36 | Thermistor Input | 5 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 43 | 37 | Thermistor Input | 5 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 43 | 38 | Thermistor Input | 5 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 43 | 46 | Thermistor Input | 5 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 43 | 48 | Thermistor Input | 5 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 43 | 49 | Thermistor Input | 5 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 43 | 50 | Thermistor Input | 5 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 43 | 51 | Thermistor Input | 5 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 43 | 52 | Thermistor Input | 5 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 43 | 53 | Thermistor Input | 5 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 44 | 1 | Thermistor Input | 5 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 44 | 2 | Thermistor Input | 5 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 44 | 3 | Thermistor Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 44 | 4 | Thermistor Input | 5 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 44 | 5 | Thermistor Input | 5 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 44 | 6 | Thermistor Input | 5 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 44 | 7 | Thermistor Input | 5 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 44 | 8 | Thermistor Input | 5 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 44 | 9 | Thermistor Input | 5 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 44 | 10 | Thermistor Input | 5 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 44 | 14 | Thermistor Input | 5 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 44 | 16 | Thermistor Input | 5 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 44 | 17 | Thermistor Input | 5 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 44 | 18 | Thermistor Input | 5 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 44 | 27 | Thermistor Input | 5 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 44 | 28 | Thermistor Input | 5 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 44 | 29 | Thermistor Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 44 | 30 | Thermistor Input | 5 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 44 | 31 | Thermistor Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 44 | 32 | Thermistor Input | 5 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 44 | 33 | Thermistor Input | 5 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 44 | 34 | Thermistor Input | 5 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 44 | 35 | Thermistor Input | 5 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 44 | 36 | Thermistor Input | 5 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 44 | 37 | Thermistor Input | 5 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 44 | 38 | Thermistor Input | 5 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 44 | 46 | Thermistor Input | 5 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 44 | 48 | Thermistor Input | 5 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 44 | 49 | Thermistor Input | 5 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 44 | 50 | Thermistor Input | 5 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 44 | 51 | Thermistor Input | 5 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 44 | 52 | Thermistor Input | 5 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 44 | 53 | Thermistor Input | 5 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 51 | 1 | Thermistor Input | 6 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 51 | 2 | Thermistor Input | 6 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 51 | 3 | Thermistor Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 51 | 4 | Thermistor Input | 6 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 51 | 5 | Thermistor Input | 6 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 51 | 6 | Thermistor Input | 6 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 51 | 7 | Thermistor Input | 6 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 51 | 8 | Thermistor Input | 6 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 51 | 9 | Thermistor Input | 6 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 51 | 10 | Thermistor Input | 6 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 51 | 14 | Thermistor Input | 6 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 51 | 16 | Thermistor Input | 6 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 51 | 17 | Thermistor Input | 6 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 51 | 18 | Thermistor Input | 6 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 51 | 27 | Thermistor Input | 6 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 51 | 28 | Thermistor Input | 6 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 51 | 29 | Thermistor Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 51 | 30 | Thermistor Input | 6 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 51 | 31 | Thermistor Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 51 | 32 | Thermistor Input | 6 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 51 | 33 | Thermistor Input | 6 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 51 | 34 | Thermistor Input | 6 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 51 | 35 | Thermistor Input | 6 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 51 | 36 | Thermistor Input | 6 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 51 | 37 | Thermistor Input | 6 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 51 | 38 | Thermistor Input | 6 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 51 | 46 | Thermistor Input | 6 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 51 | 48 | Thermistor Input | 6 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 51 | 49 | Thermistor Input | 6 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 51 | 50 | Thermistor Input | 6 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 51 | 51 | Thermistor Input | 6 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 51 | 52 | Thermistor Input | 6 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 51 | 53 | Thermistor Input | 6 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 52 | 1 | Thermistor Input | 6 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 52 | 2 | Thermistor Input | 6 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 52 | 3 | Thermistor Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 52 | 4 | Thermistor Input | 6 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 52 | 5 | Thermistor Input | 6 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 52 | 6 | Thermistor Input | 6 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 52 | 7 | Thermistor Input | 6 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 52 | 8 | Thermistor Input | 6 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 52 | 9 | Thermistor Input | 6 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 52 | 10 | Thermistor Input | 6 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 52 | 14 | Thermistor Input | 6 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 52 | 16 | Thermistor Input | 6 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 52 | 17 | Thermistor Input | 6 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 52 | 18 | Thermistor Input | 6 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 52 | 27 | Thermistor Input | 6 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 52 | 28 | Thermistor Input | 6 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 52 | 29 | Thermistor Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 52 | 30 | Thermistor Input | 6 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 52 | 31 | Thermistor Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 52 | 32 | Thermistor Input | 6 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 52 | 33 | Thermistor Input | 6 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 52 | 34 | Thermistor Input | 6 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 52 | 35 | Thermistor Input | 6 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 52 | 36 | Thermistor Input | 6 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 52 | 37 | Thermistor Input | 6 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 52 | 38 | Thermistor Input | 6 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 52 | 46 | Thermistor Input | 6 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 52 | 48 | Thermistor Input | 6 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 52 | 49 | Thermistor Input | 6 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 52 | 50 | Thermistor Input | 6 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 52 | 51 | Thermistor Input | 6 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 52 | 52 | Thermistor Input | 6 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 52 | 53 | Thermistor Input | 6 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 53 | 1 | Thermistor Input | 6 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 53 | 2 | Thermistor Input | 6 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 53 | 3 | Thermistor Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 53 | 4 | Thermistor Input | 6 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 53 | 5 | Thermistor Input | 6 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 53 | 6 | Thermistor Input | 6 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 53 | 7 | Thermistor Input | 6 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 53 | 8 | Thermistor Input | 6 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 53 | 9 | Thermistor Input | 6 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 53 | 10 | Thermistor Input | 6 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 53 | 14 | Thermistor Input | 6 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 53 | 16 | Thermistor Input | 6 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 53 | 17 | Thermistor Input | 6 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 53 | 18 | Thermistor Input | 6 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 53 | 27 | Thermistor Input | 6 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 53 | 28 | Thermistor Input | 6 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 53 | 29 | Thermistor Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 53 | 30 | Thermistor Input | 6 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 53 | 31 | Thermistor Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 53 | 32 | Thermistor Input | 6 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 53 | 33 | Thermistor Input | 6 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 53 | 34 | Thermistor Input | 6 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 53 | 35 | Thermistor Input | 6 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 53 | 36 | Thermistor Input | 6 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 53 | 37 | Thermistor Input | 6 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 53 | 38 | Thermistor Input | 6 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 53 | 46 | Thermistor Input | 6 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 53 | 48 | Thermistor Input | 6 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 53 | 49 | Thermistor Input | 6 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 53 | 50 | Thermistor Input | 6 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 53 | 51 | Thermistor Input | 6 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 53 | 52 | Thermistor Input | 6 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 53 | 53 | Thermistor Input | 6 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 54 | 1 | Thermistor Input | 6 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 54 | 2 | Thermistor Input | 6 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 54 | No
156 | 54 | 3 | Thermistor Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 54 | Yes
156 | 54 | 4 | Thermistor Input | 6 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | Yes
156 | 54 | 5 | Thermistor Input | 6 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | UINT | R/W | 54 | Yes
156 | 54 | 6 | Thermistor Input | 6 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | UINT | R/W | 54 | Yes
156 | 54 | 7 | Thermistor Input | 6 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | UINT | R/W | 54 | No
156 | 54 | 8 | Thermistor Input | 6 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | REAL | R/W | 54 | No
156 | 54 | 9 | Thermistor Input | 6 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | REAL | R/W | 54 | No
156 | 54 | 10 | Thermistor Input | 6 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | REAL | R/W | 54 | No
156 | 54 | 14 | Thermistor Input | 6 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 54 | Yes
156 | 54 | 16 | Thermistor Input | 6 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | Yes
156 | 54 | 17 | Thermistor Input | 6 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 54 | Yes
156 | 54 | 18 | Thermistor Input | 6 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 54 | Yes
156 | 54 | 27 | Thermistor Input | 6 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 54 | No
156 | 54 | 28 | Thermistor Input | 6 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 54 | No
156 | 54 | 29 | Thermistor Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 54 | 30 | Thermistor Input | 6 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 54 | No
156 | 54 | 31 | Thermistor Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 54 | 32 | Thermistor Input | 6 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 54 | 33 | Thermistor Input | 6 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 54 | 34 | Thermistor Input | 6 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 54 | No
156 | 54 | 35 | Thermistor Input | 6 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 54 | 36 | Thermistor Input | 6 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 54 | No
156 | 54 | 37 | Thermistor Input | 6 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 54 | 38 | Thermistor Input | 6 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 54 | No
156 | 54 | 46 | Thermistor Input | 6 | Gain |  | 0.0 to 10.0 |  | REAL | R/W | 54 | No
156 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
156 | 54 | 48 | Thermistor Input | 6 | Terminate |  | 2 (1), 3 (2) |  | UINT | R | 54 | No
156 | 54 | 49 | Thermistor Input | 6 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 54 | No
156 | 54 | 50 | Thermistor Input | 6 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 54 | 51 | Thermistor Input | 6 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 54 | 52 | Thermistor Input | 6 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
156 | 54 | 53 | Thermistor Input | 6 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 54 | No
157 | 1 | 1 | Temperature Input | 1 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 1 | 2 | Temperature Input | 1 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 51 | No
157 | 1 | 3 | Temperature Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 51 | Yes
157 | 1 | 4 | Temperature Input | 1 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | Yes
157 | 1 | 5 | Temperature Input | 1 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | UINT | R/W | 51 | Yes
157 | 1 | 6 | Temperature Input | 1 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 51 | Yes
157 | 1 | 7 | Temperature Input | 1 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | UINT | R/W | 51 | No
157 | 1 | 14 | Temperature Input | 1 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 51 | Yes
157 | 1 | 16 | Temperature Input | 1 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
157 | 1 | 17 | Temperature Input | 1 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 51 | Yes
157 | 1 | 18 | Temperature Input | 1 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 51 | Yes
157 | 1 | 27 | Temperature Input | 1 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 51 | No
157 | 1 | 28 | Temperature Input | 1 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 51 | No
157 | 1 | 29 | Temperature Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 1 | 30 | Temperature Input | 1 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 51 | No
157 | 1 | 31 | Temperature Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 1 | 32 | Temperature Input | 1 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 1 | 33 | Temperature Input | 1 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 1 | 34 | Temperature Input | 1 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 1 | 35 | Temperature Input | 1 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | No
157 | 1 | 36 | Temperature Input | 1 | Electrical Input Offset |  | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | No
157 | 1 | 37 | Temperature Input | 1 | Electrical Input Slope |  | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 51 | No
157 | 1 | 38 | Temperature Input | 1 | Calibration Slope |  | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 51 | No
157 | 1 | 46 | Temperature Input | 1 | Gain |  | 0.0 to 10.0 | 0.89 | REAL | R/W | 51 | No
157 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
157 | 1 | 49 | Temperature Input | 1 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 51 | No
157 | 1 | 50 | Temperature Input | 1 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 1 | 51 | Temperature Input | 1 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 1 | 52 | Temperature Input | 1 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 1 | 53 | Temperature Input | 1 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 11 | 1 | Temperature Input | 2 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 11 | 2 | Temperature Input | 2 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 51 | No
157 | 11 | 3 | Temperature Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 51 | Yes
157 | 11 | 4 | Temperature Input | 2 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | Yes
157 | 11 | 5 | Temperature Input | 2 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | UINT | R/W | 51 | Yes
157 | 11 | 6 | Temperature Input | 2 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 51 | Yes
157 | 11 | 7 | Temperature Input | 2 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | UINT | R/W | 51 | No
157 | 11 | 14 | Temperature Input | 2 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 51 | Yes
157 | 11 | 16 | Temperature Input | 2 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
157 | 11 | 17 | Temperature Input | 2 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 51 | Yes
157 | 11 | 18 | Temperature Input | 2 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 51 | Yes
157 | 11 | 27 | Temperature Input | 2 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 51 | No
157 | 11 | 28 | Temperature Input | 2 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 51 | No
157 | 11 | 29 | Temperature Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 11 | 30 | Temperature Input | 2 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 51 | No
157 | 11 | 31 | Temperature Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 11 | 32 | Temperature Input | 2 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 11 | 33 | Temperature Input | 2 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 11 | 34 | Temperature Input | 2 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 11 | 35 | Temperature Input | 2 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | No
157 | 11 | 36 | Temperature Input | 2 | Electrical Input Offset |  | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | No
157 | 11 | 37 | Temperature Input | 2 | Electrical Input Slope |  | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 51 | No
157 | 11 | 38 | Temperature Input | 2 | Calibration Slope |  | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 51 | No
157 | 11 | 46 | Temperature Input | 2 | Gain |  | 0.0 to 10.0 | 0.89 | REAL | R/W | 51 | No
157 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
157 | 11 | 49 | Temperature Input | 2 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 51 | No
157 | 11 | 50 | Temperature Input | 2 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 11 | 51 | Temperature Input | 2 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 11 | 52 | Temperature Input | 2 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 11 | 53 | Temperature Input | 2 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 21 | 1 | Temperature Input | 3 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 21 | 2 | Temperature Input | 3 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 51 | No
157 | 21 | 3 | Temperature Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 51 | Yes
157 | 21 | 4 | Temperature Input | 3 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | Yes
157 | 21 | 5 | Temperature Input | 3 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | UINT | R/W | 51 | Yes
157 | 21 | 6 | Temperature Input | 3 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 51 | Yes
157 | 21 | 7 | Temperature Input | 3 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | UINT | R/W | 51 | No
157 | 21 | 14 | Temperature Input | 3 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 51 | Yes
157 | 21 | 16 | Temperature Input | 3 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
157 | 21 | 17 | Temperature Input | 3 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 51 | Yes
157 | 21 | 18 | Temperature Input | 3 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 51 | Yes
157 | 21 | 27 | Temperature Input | 3 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 51 | No
157 | 21 | 28 | Temperature Input | 3 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 51 | No
157 | 21 | 29 | Temperature Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 21 | 30 | Temperature Input | 3 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 51 | No
157 | 21 | 31 | Temperature Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 21 | 32 | Temperature Input | 3 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 21 | 33 | Temperature Input | 3 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 21 | 34 | Temperature Input | 3 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 21 | 35 | Temperature Input | 3 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | No
157 | 21 | 36 | Temperature Input | 3 | Electrical Input Offset |  | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | No
157 | 21 | 37 | Temperature Input | 3 | Electrical Input Slope |  | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 51 | No
157 | 21 | 38 | Temperature Input | 3 | Calibration Slope |  | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 51 | No
157 | 21 | 46 | Temperature Input | 3 | Gain |  | 0.0 to 10.0 | 0.89 | REAL | R/W | 51 | No
157 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
157 | 21 | 49 | Temperature Input | 3 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 51 | No
157 | 21 | 50 | Temperature Input | 3 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 21 | 51 | Temperature Input | 3 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 21 | 52 | Temperature Input | 3 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 21 | 53 | Temperature Input | 3 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 31 | 1 | Temperature Input | 4 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 31 | 2 | Temperature Input | 4 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 51 | No
157 | 31 | 3 | Temperature Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 51 | Yes
157 | 31 | 4 | Temperature Input | 4 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | Yes
157 | 31 | 5 | Temperature Input | 4 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | UINT | R/W | 51 | Yes
157 | 31 | 6 | Temperature Input | 4 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 51 | Yes
157 | 31 | 7 | Temperature Input | 4 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | UINT | R/W | 51 | No
157 | 31 | 14 | Temperature Input | 4 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 51 | Yes
157 | 31 | 16 | Temperature Input | 4 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
157 | 31 | 17 | Temperature Input | 4 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 51 | Yes
157 | 31 | 18 | Temperature Input | 4 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 51 | Yes
157 | 31 | 27 | Temperature Input | 4 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 51 | No
157 | 31 | 28 | Temperature Input | 4 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 51 | No
157 | 31 | 29 | Temperature Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 31 | 30 | Temperature Input | 4 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 51 | No
157 | 31 | 31 | Temperature Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 31 | 32 | Temperature Input | 4 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 31 | 33 | Temperature Input | 4 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 31 | 34 | Temperature Input | 4 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 31 | 35 | Temperature Input | 4 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | No
157 | 31 | 36 | Temperature Input | 4 | Electrical Input Offset |  | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | No
157 | 31 | 37 | Temperature Input | 4 | Electrical Input Slope |  | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 51 | No
157 | 31 | 38 | Temperature Input | 4 | Calibration Slope |  | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 51 | No
157 | 31 | 46 | Temperature Input | 4 | Gain |  | 0.0 to 10.0 | 0.89 | REAL | R/W | 51 | No
157 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
157 | 31 | 49 | Temperature Input | 4 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 51 | No
157 | 31 | 50 | Temperature Input | 4 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 31 | 51 | Temperature Input | 4 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 31 | 52 | Temperature Input | 4 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 31 | 53 | Temperature Input | 4 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 41 | 1 | Temperature Input | 5 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 41 | 2 | Temperature Input | 5 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 51 | No
157 | 41 | 3 | Temperature Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 51 | Yes
157 | 41 | 4 | Temperature Input | 5 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | Yes
157 | 41 | 5 | Temperature Input | 5 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | UINT | R/W | 51 | Yes
157 | 41 | 6 | Temperature Input | 5 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 51 | Yes
157 | 41 | 7 | Temperature Input | 5 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | UINT | R/W | 51 | No
157 | 41 | 14 | Temperature Input | 5 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 51 | Yes
157 | 41 | 16 | Temperature Input | 5 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
157 | 41 | 17 | Temperature Input | 5 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 51 | Yes
157 | 41 | 18 | Temperature Input | 5 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 51 | Yes
157 | 41 | 27 | Temperature Input | 5 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 51 | No
157 | 41 | 28 | Temperature Input | 5 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 51 | No
157 | 41 | 29 | Temperature Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 41 | 30 | Temperature Input | 5 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 51 | No
157 | 41 | 31 | Temperature Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 41 | 32 | Temperature Input | 5 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 41 | 33 | Temperature Input | 5 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 41 | 34 | Temperature Input | 5 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 41 | 35 | Temperature Input | 5 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | No
157 | 41 | 36 | Temperature Input | 5 | Electrical Input Offset |  | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | No
157 | 41 | 37 | Temperature Input | 5 | Electrical Input Slope |  | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 51 | No
157 | 41 | 38 | Temperature Input | 5 | Calibration Slope |  | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 51 | No
157 | 41 | 46 | Temperature Input | 5 | Gain |  | 0.0 to 10.0 | 0.89 | REAL | R/W | 51 | No
157 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
157 | 41 | 49 | Temperature Input | 5 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 51 | No
157 | 41 | 50 | Temperature Input | 5 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 41 | 51 | Temperature Input | 5 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 41 | 52 | Temperature Input | 5 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 41 | 53 | Temperature Input | 5 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 51 | 1 | Temperature Input | 6 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 51 | 2 | Temperature Input | 6 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | UINT | R | 51 | No
157 | 51 | 3 | Temperature Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | REAL | R/W | 51 | Yes
157 | 51 | 4 | Temperature Input | 6 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | Yes
157 | 51 | 5 | Temperature Input | 6 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | UINT | R/W | 51 | Yes
157 | 51 | 6 | Temperature Input | 6 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | UINT | R/W | 51 | Yes
157 | 51 | 7 | Temperature Input | 6 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | UINT | R/W | 51 | No
157 | 51 | 14 | Temperature Input | 6 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | UINT | R/W | 51 | Yes
157 | 51 | 16 | Temperature Input | 6 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
157 | 51 | 17 | Temperature Input | 6 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | UINT | R/W | 51 | Yes
157 | 51 | 18 | Temperature Input | 6 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 51 | Yes
157 | 51 | 27 | Temperature Input | 6 | Counts |  | -2,147,483,648 to 2,147,483,647 |  | DINT | R | 51 | No
157 | 51 | 28 | Temperature Input | 6 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | REAL | R | 51 | No
157 | 51 | 29 | Temperature Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 51 | 30 | Temperature Input | 6 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | UINT | R/W | 51 | No
157 | 51 | 31 | Temperature Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 51 | 32 | Temperature Input | 6 | Micro Ambient Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 51 | 33 | Temperature Input | 6 | CJ Temperature |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 51 | 34 | Temperature Input | 6 | Compensation Value |  | -99,999.0 to 99,999.0 |  | REAL | R | 51 | No
157 | 51 | 35 | Temperature Input | 6 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | No
157 | 51 | 36 | Temperature Input | 6 | Electrical Input Offset |  | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | No
157 | 51 | 37 | Temperature Input | 6 | Electrical Input Slope |  | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 51 | No
157 | 51 | 38 | Temperature Input | 6 | Calibration Slope |  | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 51 | No
157 | 51 | 46 | Temperature Input | 6 | Gain |  | 0.0 to 10.0 | 0.89 | REAL | R/W | 51 | No
157 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
157 | 51 | 49 | Temperature Input | 6 | Calibration Action |  | None (61), Reset Ambient Offset (2500.0), Reset Calibration Offset (2501.0), Reset Calibration Gain (2502.0), Reset All (2503.0), Calculate Ambient Offset (2504.0), Calculate Electrical Calibration (2505.0) |  | UINT | R/W | 51 | No
157 | 51 | 50 | Temperature Input | 6 | Entered Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 51 | 51 | Temperature Input | 6 | Measured Value Low |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 51 | 52 | Temperature Input | 6 | Entered Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
157 | 51 | 53 | Temperature Input | 6 | Measured Value High |  | -3.4e38 to 3.4e38 |  | REAL | R/W | 51 | No
160 | 2 | 1 | Digital Input | 1 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | UINT | R/W | 52 | Yes
160 | 2 | 11 | Digital Input | 1 | Input State | Monitor input state. | On (63), Off (62) |  | UINT | R | 52 | Yes
160 | 2 | 18 | Digital Input | 1 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 52 | No
160 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
160 | 12 | 1 | Digital Input | 2 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | UINT | R/W | 52 | Yes
160 | 12 | 11 | Digital Input | 2 | Input State | Monitor input state. | On (63), Off (62) |  | UINT | R | 52 | Yes
160 | 12 | 18 | Digital Input | 2 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 52 | No
160 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
160 | 22 | 1 | Digital Input | 3 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | UINT | R/W | 52 | Yes
160 | 22 | 11 | Digital Input | 3 | Input State | Monitor input state. | On (63), Off (62) |  | UINT | R | 52 | Yes
160 | 22 | 18 | Digital Input | 3 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 52 | No
160 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
160 | 32 | 1 | Digital Input | 4 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | UINT | R/W | 52 | Yes
160 | 32 | 11 | Digital Input | 4 | Input State | Monitor input state. | On (63), Off (62) |  | UINT | R | 52 | Yes
160 | 32 | 18 | Digital Input | 4 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 52 | No
160 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
160 | 42 | 1 | Digital Input | 5 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | UINT | R/W | 52 | Yes
160 | 42 | 11 | Digital Input | 5 | Input State | Monitor input state. | On (63), Off (62) |  | UINT | R | 52 | Yes
160 | 42 | 18 | Digital Input | 5 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 52 | No
160 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
160 | 52 | 1 | Digital Input | 6 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | UINT | R/W | 52 | Yes
160 | 52 | 11 | Digital Input | 6 | Input State | Monitor input state. | On (63), Off (62) |  | UINT | R | 52 | Yes
160 | 52 | 18 | Digital Input | 6 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 52 | No
160 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
161 | 1 | 1 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 1 | 2 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 1 | 3 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 1 | 4 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 1 | 5 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 1 | 6 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 1 | 7 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 1 | 8 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 1 | 9 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 1 | 10 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 1 | 11 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 1 | 12 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 1 | 13 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 1 | 14 | Digital I/O | 1 | Status |  |  | 0 | USINT | R | 56 | No
161 | 1 | 15 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 1 | 18 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 2 | 1 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 2 | 2 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 2 | 3 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 2 | 4 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 2 | 5 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 2 | 6 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 2 | 7 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 2 | 8 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 2 | 9 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 2 | 10 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 2 | 11 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 2 | 12 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 2 | 13 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 2 | 14 | Digital I/O | 1 | Status |  |  | 0 | USINT | R | 56 | No
161 | 2 | 15 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 2 | 18 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 3 | 1 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 3 | 2 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 3 | 3 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 3 | 4 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 3 | 5 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 3 | 6 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 3 | 7 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 3 | 8 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 3 | 9 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 3 | 10 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 3 | 11 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 3 | 12 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 3 | 13 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 3 | 14 | Digital I/O | 1 | Status |  |  | 0 | USINT | R | 56 | No
161 | 3 | 15 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 3 | 18 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 4 | 1 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 4 | 2 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 4 | 3 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 4 | 4 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 4 | 5 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 4 | 6 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 4 | 7 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 4 | 8 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 4 | 9 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 4 | 10 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 4 | 11 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 4 | 12 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 4 | 13 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 4 | 14 | Digital I/O | 1 | Status |  |  | 0 | USINT | R | 56 | No
161 | 4 | 15 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 4 | 18 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 5 | 1 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 5 | 2 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 5 | 3 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 5 | 4 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 5 | 5 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 5 | 6 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 5 | 7 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 5 | 8 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 5 | 9 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 5 | 10 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 5 | 11 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 5 | 12 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 5 | 13 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 5 | 14 | Digital I/O | 1 | Status |  |  | 0 | USINT | R | 56 | No
161 | 5 | 15 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 5 | 18 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 6 | 1 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 6 | 2 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 6 | 3 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 6 | 4 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 6 | 5 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 6 | 6 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 6 | 7 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 6 | 8 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 6 | 9 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 6 | 10 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 6 | 11 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 6 | 12 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 6 | 13 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 6 | 14 | Digital I/O | 1 | Status |  |  | 0 | USINT | R | 56 | No
161 | 6 | 15 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 6 | 18 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 11 | 1 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 11 | 2 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 11 | 3 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 11 | 4 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 11 | 5 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 11 | 6 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 11 | 7 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 11 | 8 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 11 | 9 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 11 | 10 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 11 | 11 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 11 | 12 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 11 | 13 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 11 | 14 | Digital I/O | 2 | Status |  |  | 0 | USINT | R | 56 | No
161 | 11 | 15 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 11 | 18 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 12 | 1 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 12 | 2 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 12 | 3 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 12 | 4 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 12 | 5 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 12 | 6 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 12 | 7 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 12 | 8 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 12 | 9 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 12 | 10 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 12 | 11 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 12 | 12 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 12 | 13 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 12 | 14 | Digital I/O | 2 | Status |  |  | 0 | USINT | R | 56 | No
161 | 12 | 15 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 12 | 18 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 13 | 1 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 13 | 2 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 13 | 3 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 13 | 4 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 13 | 5 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 13 | 6 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 13 | 7 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 13 | 8 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 13 | 9 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 13 | 10 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 13 | 11 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 13 | 12 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 13 | 13 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 13 | 14 | Digital I/O | 2 | Status |  |  | 0 | USINT | R | 56 | No
161 | 13 | 15 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 13 | 18 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 14 | 1 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 14 | 2 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 14 | 3 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 14 | 4 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 14 | 5 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 14 | 6 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 14 | 7 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 14 | 8 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 14 | 9 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 14 | 10 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 14 | 11 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 14 | 12 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 14 | 13 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 14 | 14 | Digital I/O | 2 | Status |  |  | 0 | USINT | R | 56 | No
161 | 14 | 15 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 14 | 18 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 15 | 1 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 15 | 2 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 15 | 3 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 15 | 4 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 15 | 5 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 15 | 6 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 15 | 7 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 15 | 8 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 15 | 9 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 15 | 10 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 15 | 11 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 15 | 12 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 15 | 13 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 15 | 14 | Digital I/O | 2 | Status |  |  | 0 | USINT | R | 56 | No
161 | 15 | 15 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 15 | 18 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 16 | 1 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 16 | 2 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 16 | 3 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 16 | 4 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 16 | 5 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 16 | 6 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 16 | 7 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 16 | 8 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 16 | 9 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 16 | 10 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 16 | 11 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 16 | 12 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 16 | 13 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 16 | 14 | Digital I/O | 2 | Status |  |  | 0 | USINT | R | 56 | No
161 | 16 | 15 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 16 | 18 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 21 | 1 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 21 | 2 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 21 | 3 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 21 | 4 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 21 | 5 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 21 | 6 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 21 | 7 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 21 | 8 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 21 | 9 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 21 | 10 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 21 | 11 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 21 | 12 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 21 | 13 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 21 | 14 | Digital I/O | 3 | Status |  |  | 0 | USINT | R | 56 | No
161 | 21 | 15 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 21 | 18 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 22 | 1 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 22 | 2 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 22 | 3 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 22 | 4 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 22 | 5 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 22 | 6 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 22 | 7 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 22 | 8 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 22 | 9 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 22 | 10 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 22 | 11 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 22 | 12 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 22 | 13 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 22 | 14 | Digital I/O | 3 | Status |  |  | 0 | USINT | R | 56 | No
161 | 22 | 15 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 22 | 18 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 23 | 1 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 23 | 2 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 23 | 3 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 23 | 4 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 23 | 5 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 23 | 6 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 23 | 7 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 23 | 8 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 23 | 9 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 23 | 10 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 23 | 11 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 23 | 12 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 23 | 13 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 23 | 14 | Digital I/O | 3 | Status |  |  | 0 | USINT | R | 56 | No
161 | 23 | 15 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 23 | 18 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 24 | 1 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 24 | 2 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 24 | 3 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 24 | 4 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 24 | 5 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 24 | 6 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 24 | 7 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 24 | 8 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 24 | 9 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 24 | 10 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 24 | 11 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 24 | 12 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 24 | 13 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 24 | 14 | Digital I/O | 3 | Status |  |  | 0 | USINT | R | 56 | No
161 | 24 | 15 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 24 | 18 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 25 | 1 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 25 | 2 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 25 | 3 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 25 | 4 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 25 | 5 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 25 | 6 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 25 | 7 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 25 | 8 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 25 | 9 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 25 | 10 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 25 | 11 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 25 | 12 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 25 | 13 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 25 | 14 | Digital I/O | 3 | Status |  |  | 0 | USINT | R | 56 | No
161 | 25 | 15 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 25 | 18 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 26 | 1 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 26 | 2 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 26 | 3 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 26 | 4 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 26 | 5 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 26 | 6 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 26 | 7 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 26 | 8 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 26 | 9 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 26 | 10 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 26 | 11 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 26 | 12 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 26 | 13 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 26 | 14 | Digital I/O | 3 | Status |  |  | 0 | USINT | R | 56 | No
161 | 26 | 15 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 26 | 18 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 31 | 1 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 31 | 2 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 31 | 3 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 31 | 4 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 31 | 5 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 31 | 6 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 31 | 7 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 31 | 8 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 31 | 9 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 31 | 10 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 31 | 11 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 31 | 12 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 31 | 13 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 31 | 14 | Digital I/O | 4 | Status |  |  | 0 | USINT | R | 56 | No
161 | 31 | 15 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 31 | 18 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 32 | 1 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 32 | 2 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 32 | 3 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 32 | 4 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 32 | 5 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 32 | 6 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 32 | 7 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 32 | 8 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 32 | 9 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 32 | 10 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 32 | 11 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 32 | 12 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 32 | 13 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 32 | 14 | Digital I/O | 4 | Status |  |  | 0 | USINT | R | 56 | No
161 | 32 | 15 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 32 | 18 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 33 | 1 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 33 | 2 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 33 | 3 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 33 | 4 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 33 | 5 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 33 | 6 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 33 | 7 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 33 | 8 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 33 | 9 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 33 | 10 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 33 | 11 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 33 | 12 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 33 | 13 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 33 | 14 | Digital I/O | 4 | Status |  |  | 0 | USINT | R | 56 | No
161 | 33 | 15 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 33 | 18 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 34 | 1 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 34 | 2 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 34 | 3 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 34 | 4 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 34 | 5 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 34 | 6 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 34 | 7 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 34 | 8 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 34 | 9 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 34 | 10 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 34 | 11 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 34 | 12 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 34 | 13 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 34 | 14 | Digital I/O | 4 | Status |  |  | 0 | USINT | R | 56 | No
161 | 34 | 15 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 34 | 18 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 35 | 1 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 35 | 2 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 35 | 3 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 35 | 4 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 35 | 5 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 35 | 6 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 35 | 7 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 35 | 8 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 35 | 9 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 35 | 10 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 35 | 11 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 35 | 12 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 35 | 13 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 35 | 14 | Digital I/O | 4 | Status |  |  | 0 | USINT | R | 56 | No
161 | 35 | 15 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 35 | 18 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 36 | 1 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 36 | 2 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 36 | 3 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 36 | 4 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 36 | 5 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 36 | 6 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 36 | 7 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 36 | 8 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 36 | 9 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 36 | 10 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 36 | 11 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 36 | 12 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 36 | 13 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 36 | 14 | Digital I/O | 4 | Status |  |  | 0 | USINT | R | 56 | No
161 | 36 | 15 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 36 | 18 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 41 | 1 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 41 | 2 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 41 | 3 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 41 | 4 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 41 | 5 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 41 | 6 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 41 | 7 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 41 | 8 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 41 | 9 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 41 | 10 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 41 | 11 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 41 | 12 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 41 | 13 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 41 | 14 | Digital I/O | 5 | Status |  |  | 0 | USINT | R | 56 | No
161 | 41 | 15 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 41 | 18 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 42 | 1 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 42 | 2 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 42 | 3 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 42 | 4 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 42 | 5 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 42 | 6 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 42 | 7 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 42 | 8 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 42 | 9 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 42 | 10 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 42 | 11 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 42 | 12 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 42 | 13 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 42 | 14 | Digital I/O | 5 | Status |  |  | 0 | USINT | R | 56 | No
161 | 42 | 15 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 42 | 18 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 43 | 1 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 43 | 2 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 43 | 3 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 43 | 4 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 43 | 5 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 43 | 6 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 43 | 7 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 43 | 8 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 43 | 9 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 43 | 10 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 43 | 11 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 43 | 12 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 43 | 13 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 43 | 14 | Digital I/O | 5 | Status |  |  | 0 | USINT | R | 56 | No
161 | 43 | 15 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 43 | 18 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 44 | 1 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 44 | 2 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 44 | 3 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 44 | 4 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 44 | 5 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 44 | 6 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 44 | 7 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 44 | 8 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 44 | 9 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 44 | 10 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 44 | 11 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 44 | 12 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 44 | 13 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 44 | 14 | Digital I/O | 5 | Status |  |  | 0 | USINT | R | 56 | No
161 | 44 | 15 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 44 | 18 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 45 | 1 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 45 | 2 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 45 | 3 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 45 | 4 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 45 | 5 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 45 | 6 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 45 | 7 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 45 | 8 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 45 | 9 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 45 | 10 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 45 | 11 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 45 | 12 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 45 | 13 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 45 | 14 | Digital I/O | 5 | Status |  |  | 0 | USINT | R | 56 | No
161 | 45 | 15 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 45 | 18 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 46 | 1 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 46 | 2 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 46 | 3 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 46 | 4 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 46 | 5 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 46 | 6 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 46 | 7 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 46 | 8 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 46 | 9 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 46 | 10 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 46 | 11 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 46 | 12 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 46 | 13 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 46 | 14 | Digital I/O | 5 | Status |  |  | 0 | USINT | R | 56 | No
161 | 46 | 15 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 46 | 18 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 51 | 1 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 51 | 2 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 51 | 3 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 51 | 4 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 51 | 5 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 51 | 6 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 51 | 7 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 51 | 8 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 51 | 9 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 51 | 10 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 51 | 11 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 51 | 12 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 51 | 13 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 51 | 14 | Digital I/O | 6 | Status |  |  | 0 | USINT | R | 56 | No
161 | 51 | 15 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 51 | 18 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 52 | 1 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 52 | 2 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 52 | 3 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 52 | 4 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 52 | 5 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 52 | 6 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 52 | 7 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 52 | 8 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 52 | 9 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 52 | 10 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 52 | 11 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 52 | 12 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 52 | 13 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 52 | 14 | Digital I/O | 6 | Status |  |  | 0 | USINT | R | 56 | No
161 | 52 | 15 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 52 | 18 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 53 | 1 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 53 | 2 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 53 | 3 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 53 | 4 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 53 | 5 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 53 | 6 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 53 | 7 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 53 | 8 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 53 | 9 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 53 | 10 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 53 | 11 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 53 | 12 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 53 | 13 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 53 | 14 | Digital I/O | 6 | Status |  |  | 0 | USINT | R | 56 | No
161 | 53 | 15 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 53 | 18 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 54 | 1 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 54 | 2 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 54 | 3 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 54 | 4 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 54 | 5 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 54 | 6 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 54 | 7 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 54 | 8 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 54 | 9 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 54 | 10 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 54 | 11 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 54 | 12 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 54 | 13 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 54 | 14 | Digital I/O | 6 | Status |  |  | 0 | USINT | R | 56 | No
161 | 54 | 15 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 54 | 18 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 55 | 1 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 55 | 2 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 55 | 3 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 55 | 4 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 55 | 5 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 55 | 6 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 55 | 7 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 55 | 8 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 55 | 9 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 55 | 10 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 55 | 11 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 55 | 12 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 55 | 13 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 55 | 14 | Digital I/O | 6 | Status |  |  | 0 | USINT | R | 56 | No
161 | 55 | 15 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 55 | 18 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
161 | 56 | 1 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | UINT | R/W | 56 | Yes
161 | 56 | 2 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 56 | Yes
161 | 56 | 3 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 56 | Yes
161 | 56 | 4 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 56 | No
161 | 56 | 5 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 56 | No
161 | 56 | 6 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 56 | No
161 | 56 | 7 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 56 | No
161 | 56 | 8 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 56 | No
161 | 56 | 9 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 56 | Yes
161 | 56 | 10 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 56 | Yes
161 | 56 | 11 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | UINT | R | 56 | Yes
161 | 56 | 12 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 56 | No
161 | 56 | 13 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 56 | No
161 | 56 | 14 | Digital I/O | 6 | Status |  |  | 0 | USINT | R | 56 | No
161 | 56 | 15 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 56 | No
161 | 56 | 18 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 56 | No
161 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 56 | No
162 | 1 | 2 | Digital Output Fast | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 1 | 3 | Digital Output Fast | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 1 | 4 | Digital Output Fast | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 1 | 5 | Digital Output Fast | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 1 | 6 | Digital Output Fast | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 1 | 7 | Digital Output Fast | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 1 | 8 | Digital Output Fast | 1 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 1 | 9 | Digital Output Fast | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 1 | 10 | Digital Output Fast | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 1 | 12 | Digital Output Fast | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 1 | 13 | Digital Output Fast | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 1 | 14 | Digital Output Fast | 1 | Status |  |  | 0 | USINT | R | 54 | No
162 | 1 | 15 | Digital Output Fast | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 1 | 20 | Digital Output Fast | 1 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 2 | 2 | Digital Output Fast | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 2 | 3 | Digital Output Fast | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 2 | 4 | Digital Output Fast | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 2 | 5 | Digital Output Fast | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 2 | 6 | Digital Output Fast | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 2 | 7 | Digital Output Fast | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 2 | 8 | Digital Output Fast | 1 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 2 | 9 | Digital Output Fast | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 2 | 10 | Digital Output Fast | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 2 | 12 | Digital Output Fast | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 2 | 13 | Digital Output Fast | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 2 | 14 | Digital Output Fast | 1 | Status |  |  | 0 | USINT | R | 54 | No
162 | 2 | 15 | Digital Output Fast | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 2 | 20 | Digital Output Fast | 1 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 3 | 2 | Digital Output Fast | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 3 | 3 | Digital Output Fast | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 3 | 4 | Digital Output Fast | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 3 | 5 | Digital Output Fast | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 3 | 6 | Digital Output Fast | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 3 | 7 | Digital Output Fast | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 3 | 8 | Digital Output Fast | 1 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 3 | 9 | Digital Output Fast | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 3 | 10 | Digital Output Fast | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 3 | 12 | Digital Output Fast | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 3 | 13 | Digital Output Fast | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 3 | 14 | Digital Output Fast | 1 | Status |  |  | 0 | USINT | R | 54 | No
162 | 3 | 15 | Digital Output Fast | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 3 | 20 | Digital Output Fast | 1 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 4 | 2 | Digital Output Fast | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 4 | 3 | Digital Output Fast | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 4 | 4 | Digital Output Fast | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 4 | 5 | Digital Output Fast | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 4 | 6 | Digital Output Fast | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 4 | 7 | Digital Output Fast | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 4 | 8 | Digital Output Fast | 1 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 4 | 9 | Digital Output Fast | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 4 | 10 | Digital Output Fast | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 4 | 12 | Digital Output Fast | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 4 | 13 | Digital Output Fast | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 4 | 14 | Digital Output Fast | 1 | Status |  |  | 0 | USINT | R | 54 | No
162 | 4 | 15 | Digital Output Fast | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 4 | 20 | Digital Output Fast | 1 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 11 | 2 | Digital Output Fast | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 11 | 3 | Digital Output Fast | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 11 | 4 | Digital Output Fast | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 11 | 5 | Digital Output Fast | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 11 | 6 | Digital Output Fast | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 11 | 7 | Digital Output Fast | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 11 | 8 | Digital Output Fast | 2 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 11 | 9 | Digital Output Fast | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 11 | 10 | Digital Output Fast | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 11 | 12 | Digital Output Fast | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 11 | 13 | Digital Output Fast | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 11 | 14 | Digital Output Fast | 2 | Status |  |  | 0 | USINT | R | 54 | No
162 | 11 | 15 | Digital Output Fast | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 11 | 20 | Digital Output Fast | 2 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 12 | 2 | Digital Output Fast | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 12 | 3 | Digital Output Fast | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 12 | 4 | Digital Output Fast | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 12 | 5 | Digital Output Fast | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 12 | 6 | Digital Output Fast | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 12 | 7 | Digital Output Fast | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 12 | 8 | Digital Output Fast | 2 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 12 | 9 | Digital Output Fast | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 12 | 10 | Digital Output Fast | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 12 | 12 | Digital Output Fast | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 12 | 13 | Digital Output Fast | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 12 | 14 | Digital Output Fast | 2 | Status |  |  | 0 | USINT | R | 54 | No
162 | 12 | 15 | Digital Output Fast | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 12 | 20 | Digital Output Fast | 2 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 13 | 2 | Digital Output Fast | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 13 | 3 | Digital Output Fast | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 13 | 4 | Digital Output Fast | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 13 | 5 | Digital Output Fast | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 13 | 6 | Digital Output Fast | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 13 | 7 | Digital Output Fast | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 13 | 8 | Digital Output Fast | 2 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 13 | 9 | Digital Output Fast | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 13 | 10 | Digital Output Fast | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 13 | 12 | Digital Output Fast | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 13 | 13 | Digital Output Fast | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 13 | 14 | Digital Output Fast | 2 | Status |  |  | 0 | USINT | R | 54 | No
162 | 13 | 15 | Digital Output Fast | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 13 | 20 | Digital Output Fast | 2 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 14 | 2 | Digital Output Fast | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 14 | 3 | Digital Output Fast | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 14 | 4 | Digital Output Fast | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 14 | 5 | Digital Output Fast | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 14 | 6 | Digital Output Fast | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 14 | 7 | Digital Output Fast | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 14 | 8 | Digital Output Fast | 2 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 14 | 9 | Digital Output Fast | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 14 | 10 | Digital Output Fast | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 14 | 12 | Digital Output Fast | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 14 | 13 | Digital Output Fast | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 14 | 14 | Digital Output Fast | 2 | Status |  |  | 0 | USINT | R | 54 | No
162 | 14 | 15 | Digital Output Fast | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 14 | 20 | Digital Output Fast | 2 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 21 | 2 | Digital Output Fast | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 21 | 3 | Digital Output Fast | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 21 | 4 | Digital Output Fast | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 21 | 5 | Digital Output Fast | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 21 | 6 | Digital Output Fast | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 21 | 7 | Digital Output Fast | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 21 | 8 | Digital Output Fast | 3 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 21 | 9 | Digital Output Fast | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 21 | 10 | Digital Output Fast | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 21 | 12 | Digital Output Fast | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 21 | 13 | Digital Output Fast | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 21 | 14 | Digital Output Fast | 3 | Status |  |  | 0 | USINT | R | 54 | No
162 | 21 | 15 | Digital Output Fast | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 21 | 20 | Digital Output Fast | 3 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 22 | 2 | Digital Output Fast | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 22 | 3 | Digital Output Fast | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 22 | 4 | Digital Output Fast | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 22 | 5 | Digital Output Fast | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 22 | 6 | Digital Output Fast | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 22 | 7 | Digital Output Fast | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 22 | 8 | Digital Output Fast | 3 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 22 | 9 | Digital Output Fast | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 22 | 10 | Digital Output Fast | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 22 | 12 | Digital Output Fast | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 22 | 13 | Digital Output Fast | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 22 | 14 | Digital Output Fast | 3 | Status |  |  | 0 | USINT | R | 54 | No
162 | 22 | 15 | Digital Output Fast | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 22 | 20 | Digital Output Fast | 3 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 23 | 2 | Digital Output Fast | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 23 | 3 | Digital Output Fast | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 23 | 4 | Digital Output Fast | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 23 | 5 | Digital Output Fast | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 23 | 6 | Digital Output Fast | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 23 | 7 | Digital Output Fast | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 23 | 8 | Digital Output Fast | 3 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 23 | 9 | Digital Output Fast | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 23 | 10 | Digital Output Fast | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 23 | 12 | Digital Output Fast | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 23 | 13 | Digital Output Fast | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 23 | 14 | Digital Output Fast | 3 | Status |  |  | 0 | USINT | R | 54 | No
162 | 23 | 15 | Digital Output Fast | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 23 | 20 | Digital Output Fast | 3 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 24 | 2 | Digital Output Fast | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 24 | 3 | Digital Output Fast | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 24 | 4 | Digital Output Fast | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 24 | 5 | Digital Output Fast | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 24 | 6 | Digital Output Fast | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 24 | 7 | Digital Output Fast | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 24 | 8 | Digital Output Fast | 3 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 24 | 9 | Digital Output Fast | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 24 | 10 | Digital Output Fast | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 24 | 12 | Digital Output Fast | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 24 | 13 | Digital Output Fast | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 24 | 14 | Digital Output Fast | 3 | Status |  |  | 0 | USINT | R | 54 | No
162 | 24 | 15 | Digital Output Fast | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 24 | 20 | Digital Output Fast | 3 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 31 | 2 | Digital Output Fast | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 31 | 3 | Digital Output Fast | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 31 | 4 | Digital Output Fast | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 31 | 5 | Digital Output Fast | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 31 | 6 | Digital Output Fast | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 31 | 7 | Digital Output Fast | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 31 | 8 | Digital Output Fast | 4 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 31 | 9 | Digital Output Fast | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 31 | 10 | Digital Output Fast | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 31 | 12 | Digital Output Fast | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 31 | 13 | Digital Output Fast | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 31 | 14 | Digital Output Fast | 4 | Status |  |  | 0 | USINT | R | 54 | No
162 | 31 | 15 | Digital Output Fast | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 31 | 20 | Digital Output Fast | 4 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 32 | 2 | Digital Output Fast | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 32 | 3 | Digital Output Fast | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 32 | 4 | Digital Output Fast | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 32 | 5 | Digital Output Fast | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 32 | 6 | Digital Output Fast | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 32 | 7 | Digital Output Fast | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 32 | 8 | Digital Output Fast | 4 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 32 | 9 | Digital Output Fast | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 32 | 10 | Digital Output Fast | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 32 | 12 | Digital Output Fast | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 32 | 13 | Digital Output Fast | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 32 | 14 | Digital Output Fast | 4 | Status |  |  | 0 | USINT | R | 54 | No
162 | 32 | 15 | Digital Output Fast | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 32 | 20 | Digital Output Fast | 4 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 33 | 2 | Digital Output Fast | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 33 | 3 | Digital Output Fast | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 33 | 4 | Digital Output Fast | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 33 | 5 | Digital Output Fast | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 33 | 6 | Digital Output Fast | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 33 | 7 | Digital Output Fast | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 33 | 8 | Digital Output Fast | 4 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 33 | 9 | Digital Output Fast | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 33 | 10 | Digital Output Fast | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 33 | 12 | Digital Output Fast | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 33 | 13 | Digital Output Fast | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 33 | 14 | Digital Output Fast | 4 | Status |  |  | 0 | USINT | R | 54 | No
162 | 33 | 15 | Digital Output Fast | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 33 | 20 | Digital Output Fast | 4 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 34 | 2 | Digital Output Fast | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 34 | 3 | Digital Output Fast | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 34 | 4 | Digital Output Fast | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 34 | 5 | Digital Output Fast | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 34 | 6 | Digital Output Fast | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 34 | 7 | Digital Output Fast | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 34 | 8 | Digital Output Fast | 4 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 34 | 9 | Digital Output Fast | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 34 | 10 | Digital Output Fast | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 34 | 12 | Digital Output Fast | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 34 | 13 | Digital Output Fast | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 34 | 14 | Digital Output Fast | 4 | Status |  |  | 0 | USINT | R | 54 | No
162 | 34 | 15 | Digital Output Fast | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 34 | 20 | Digital Output Fast | 4 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 41 | 2 | Digital Output Fast | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 41 | 3 | Digital Output Fast | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 41 | 4 | Digital Output Fast | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 41 | 5 | Digital Output Fast | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 41 | 6 | Digital Output Fast | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 41 | 7 | Digital Output Fast | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 41 | 8 | Digital Output Fast | 5 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 41 | 9 | Digital Output Fast | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 41 | 10 | Digital Output Fast | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 41 | 12 | Digital Output Fast | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 41 | 13 | Digital Output Fast | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 41 | 14 | Digital Output Fast | 5 | Status |  |  | 0 | USINT | R | 54 | No
162 | 41 | 15 | Digital Output Fast | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 41 | 20 | Digital Output Fast | 5 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 42 | 2 | Digital Output Fast | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 42 | 3 | Digital Output Fast | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 42 | 4 | Digital Output Fast | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 42 | 5 | Digital Output Fast | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 42 | 6 | Digital Output Fast | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 42 | 7 | Digital Output Fast | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 42 | 8 | Digital Output Fast | 5 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 42 | 9 | Digital Output Fast | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 42 | 10 | Digital Output Fast | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 42 | 12 | Digital Output Fast | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 42 | 13 | Digital Output Fast | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 42 | 14 | Digital Output Fast | 5 | Status |  |  | 0 | USINT | R | 54 | No
162 | 42 | 15 | Digital Output Fast | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 42 | 20 | Digital Output Fast | 5 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 43 | 2 | Digital Output Fast | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 43 | 3 | Digital Output Fast | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 43 | 4 | Digital Output Fast | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 43 | 5 | Digital Output Fast | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 43 | 6 | Digital Output Fast | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 43 | 7 | Digital Output Fast | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 43 | 8 | Digital Output Fast | 5 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 43 | 9 | Digital Output Fast | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 43 | 10 | Digital Output Fast | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 43 | 12 | Digital Output Fast | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 43 | 13 | Digital Output Fast | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 43 | 14 | Digital Output Fast | 5 | Status |  |  | 0 | USINT | R | 54 | No
162 | 43 | 15 | Digital Output Fast | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 43 | 20 | Digital Output Fast | 5 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 44 | 2 | Digital Output Fast | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 44 | 3 | Digital Output Fast | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 44 | 4 | Digital Output Fast | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 44 | 5 | Digital Output Fast | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 44 | 6 | Digital Output Fast | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 44 | 7 | Digital Output Fast | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 44 | 8 | Digital Output Fast | 5 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 44 | 9 | Digital Output Fast | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 44 | 10 | Digital Output Fast | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 44 | 12 | Digital Output Fast | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 44 | 13 | Digital Output Fast | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 44 | 14 | Digital Output Fast | 5 | Status |  |  | 0 | USINT | R | 54 | No
162 | 44 | 15 | Digital Output Fast | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 44 | 20 | Digital Output Fast | 5 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 51 | 2 | Digital Output Fast | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 51 | 3 | Digital Output Fast | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 51 | 4 | Digital Output Fast | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 51 | 5 | Digital Output Fast | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 51 | 6 | Digital Output Fast | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 51 | 7 | Digital Output Fast | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 51 | 8 | Digital Output Fast | 6 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 51 | 9 | Digital Output Fast | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 51 | 10 | Digital Output Fast | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 51 | 12 | Digital Output Fast | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 51 | 13 | Digital Output Fast | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 51 | 14 | Digital Output Fast | 6 | Status |  |  | 0 | USINT | R | 54 | No
162 | 51 | 15 | Digital Output Fast | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 51 | 20 | Digital Output Fast | 6 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 52 | 2 | Digital Output Fast | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 52 | 3 | Digital Output Fast | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 52 | 4 | Digital Output Fast | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 52 | 5 | Digital Output Fast | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 52 | 6 | Digital Output Fast | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 52 | 7 | Digital Output Fast | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 52 | 8 | Digital Output Fast | 6 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 52 | 9 | Digital Output Fast | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 52 | 10 | Digital Output Fast | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 52 | 12 | Digital Output Fast | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 52 | 13 | Digital Output Fast | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 52 | 14 | Digital Output Fast | 6 | Status |  |  | 0 | USINT | R | 54 | No
162 | 52 | 15 | Digital Output Fast | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 52 | 20 | Digital Output Fast | 6 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 53 | 2 | Digital Output Fast | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 53 | 3 | Digital Output Fast | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 53 | 4 | Digital Output Fast | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 53 | 5 | Digital Output Fast | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 53 | 6 | Digital Output Fast | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 53 | 7 | Digital Output Fast | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 53 | 8 | Digital Output Fast | 6 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 53 | 9 | Digital Output Fast | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 53 | 10 | Digital Output Fast | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 53 | 12 | Digital Output Fast | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 53 | 13 | Digital Output Fast | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 53 | 14 | Digital Output Fast | 6 | Status |  |  | 0 | USINT | R | 54 | No
162 | 53 | 15 | Digital Output Fast | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 53 | 20 | Digital Output Fast | 6 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
162 | 54 | 2 | Digital Output Fast | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | UINT | R/W | 54 | Yes
162 | 54 | 3 | Digital Output Fast | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | REAL | R/W | 54 | Yes
162 | 54 | 4 | Digital Output Fast | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | UINT | R/W | 54 | No
162 | 54 | 5 | Digital Output Fast | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
162 | 54 | 6 | Digital Output Fast | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | USINT | R/W | 54 | No
162 | 54 | 7 | Digital Output Fast | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
162 | 54 | 8 | Digital Output Fast | 6 | Output Power | Monitor the power applied to this output. |  |  | REAL | R | 54 | No
162 | 54 | 9 | Digital Output Fast | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | REAL | R/W | 54 | Yes
162 | 54 | 10 | Digital Output Fast | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | REAL | R/W | 54 | Yes
162 | 54 | 12 | Digital Output Fast | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
162 | 54 | 13 | Digital Output Fast | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
162 | 54 | 14 | Digital Output Fast | 6 | Status |  |  | 0 | USINT | R | 54 | No
162 | 54 | 15 | Digital Output Fast | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
162 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
162 | 54 | 20 | Digital Output Fast | 6 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | UINT | R | 54 | No
163 | 1 | 5 | Digital Output Limit | 1 | Function | Set the function. | Limit (126) | Limit (126) | UINT | R/W | 52 | No
163 | 1 | 6 | Digital Output Limit | 1 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | USINT | R/W | 52 | No
163 | 1 | 7 | Digital Output Limit | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 52 | No
163 | 1 | 12 | Digital Output Limit | 1 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | USINT | R/W | 52 | No
163 | 1 | 13 | Digital Output Limit | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 52 | No
163 | 1 | 15 | Digital Output Limit | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 52 | No
163 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
163 | 1 | 20 | Digital Output Limit | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | UINT | R | 52 | No
163 | 2 | 5 | Digital Output Limit | 1 | Function | Set the function. | Limit (126) | Limit (126) | UINT | R/W | 52 | No
163 | 2 | 6 | Digital Output Limit | 1 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | USINT | R/W | 52 | No
163 | 2 | 7 | Digital Output Limit | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 52 | No
163 | 2 | 12 | Digital Output Limit | 1 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | USINT | R/W | 52 | No
163 | 2 | 13 | Digital Output Limit | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 52 | No
163 | 2 | 15 | Digital Output Limit | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 52 | No
163 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
163 | 2 | 20 | Digital Output Limit | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | UINT | R | 52 | No
163 | 11 | 5 | Digital Output Limit | 2 | Function | Set the function. | Limit (126) | Limit (126) | UINT | R/W | 52 | No
163 | 11 | 6 | Digital Output Limit | 2 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | USINT | R/W | 52 | No
163 | 11 | 7 | Digital Output Limit | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 52 | No
163 | 11 | 12 | Digital Output Limit | 2 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | USINT | R/W | 52 | No
163 | 11 | 13 | Digital Output Limit | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 52 | No
163 | 11 | 15 | Digital Output Limit | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 52 | No
163 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
163 | 11 | 20 | Digital Output Limit | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | UINT | R | 52 | No
163 | 12 | 5 | Digital Output Limit | 2 | Function | Set the function. | Limit (126) | Limit (126) | UINT | R/W | 52 | No
163 | 12 | 6 | Digital Output Limit | 2 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | USINT | R/W | 52 | No
163 | 12 | 7 | Digital Output Limit | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 52 | No
163 | 12 | 12 | Digital Output Limit | 2 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | USINT | R/W | 52 | No
163 | 12 | 13 | Digital Output Limit | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 52 | No
163 | 12 | 15 | Digital Output Limit | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 52 | No
163 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
163 | 12 | 20 | Digital Output Limit | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | UINT | R | 52 | No
163 | 21 | 5 | Digital Output Limit | 3 | Function | Set the function. | Limit (126) | Limit (126) | UINT | R/W | 52 | No
163 | 21 | 6 | Digital Output Limit | 3 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | USINT | R/W | 52 | No
163 | 21 | 7 | Digital Output Limit | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 52 | No
163 | 21 | 12 | Digital Output Limit | 3 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | USINT | R/W | 52 | No
163 | 21 | 13 | Digital Output Limit | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 52 | No
163 | 21 | 15 | Digital Output Limit | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 52 | No
163 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
163 | 21 | 20 | Digital Output Limit | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | UINT | R | 52 | No
163 | 22 | 5 | Digital Output Limit | 3 | Function | Set the function. | Limit (126) | Limit (126) | UINT | R/W | 52 | No
163 | 22 | 6 | Digital Output Limit | 3 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | USINT | R/W | 52 | No
163 | 22 | 7 | Digital Output Limit | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 52 | No
163 | 22 | 12 | Digital Output Limit | 3 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | USINT | R/W | 52 | No
163 | 22 | 13 | Digital Output Limit | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 52 | No
163 | 22 | 15 | Digital Output Limit | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 52 | No
163 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
163 | 22 | 20 | Digital Output Limit | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | UINT | R | 52 | No
163 | 31 | 5 | Digital Output Limit | 4 | Function | Set the function. | Limit (126) | Limit (126) | UINT | R/W | 52 | No
163 | 31 | 6 | Digital Output Limit | 4 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | USINT | R/W | 52 | No
163 | 31 | 7 | Digital Output Limit | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 52 | No
163 | 31 | 12 | Digital Output Limit | 4 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | USINT | R/W | 52 | No
163 | 31 | 13 | Digital Output Limit | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 52 | No
163 | 31 | 15 | Digital Output Limit | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 52 | No
163 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
163 | 31 | 20 | Digital Output Limit | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | UINT | R | 52 | No
163 | 32 | 5 | Digital Output Limit | 4 | Function | Set the function. | Limit (126) | Limit (126) | UINT | R/W | 52 | No
163 | 32 | 6 | Digital Output Limit | 4 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | USINT | R/W | 52 | No
163 | 32 | 7 | Digital Output Limit | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 52 | No
163 | 32 | 12 | Digital Output Limit | 4 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | USINT | R/W | 52 | No
163 | 32 | 13 | Digital Output Limit | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 52 | No
163 | 32 | 15 | Digital Output Limit | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 52 | No
163 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
163 | 32 | 20 | Digital Output Limit | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | UINT | R | 52 | No
163 | 41 | 5 | Digital Output Limit | 5 | Function | Set the function. | Limit (126) | Limit (126) | UINT | R/W | 52 | No
163 | 41 | 6 | Digital Output Limit | 5 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | USINT | R/W | 52 | No
163 | 41 | 7 | Digital Output Limit | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 52 | No
163 | 41 | 12 | Digital Output Limit | 5 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | USINT | R/W | 52 | No
163 | 41 | 13 | Digital Output Limit | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 52 | No
163 | 41 | 15 | Digital Output Limit | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 52 | No
163 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
163 | 41 | 20 | Digital Output Limit | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | UINT | R | 52 | No
163 | 42 | 5 | Digital Output Limit | 5 | Function | Set the function. | Limit (126) | Limit (126) | UINT | R/W | 52 | No
163 | 42 | 6 | Digital Output Limit | 5 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | USINT | R/W | 52 | No
163 | 42 | 7 | Digital Output Limit | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 52 | No
163 | 42 | 12 | Digital Output Limit | 5 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | USINT | R/W | 52 | No
163 | 42 | 13 | Digital Output Limit | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 52 | No
163 | 42 | 15 | Digital Output Limit | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 52 | No
163 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
163 | 42 | 20 | Digital Output Limit | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | UINT | R | 52 | No
163 | 51 | 5 | Digital Output Limit | 6 | Function | Set the function. | Limit (126) | Limit (126) | UINT | R/W | 52 | No
163 | 51 | 6 | Digital Output Limit | 6 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | USINT | R/W | 52 | No
163 | 51 | 7 | Digital Output Limit | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 52 | No
163 | 51 | 12 | Digital Output Limit | 6 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | USINT | R/W | 52 | No
163 | 51 | 13 | Digital Output Limit | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 52 | No
163 | 51 | 15 | Digital Output Limit | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 52 | No
163 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
163 | 51 | 20 | Digital Output Limit | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | UINT | R | 52 | No
163 | 52 | 5 | Digital Output Limit | 6 | Function | Set the function. | Limit (126) | Limit (126) | UINT | R/W | 52 | No
163 | 52 | 6 | Digital Output Limit | 6 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | USINT | R/W | 52 | No
163 | 52 | 7 | Digital Output Limit | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 52 | No
163 | 52 | 12 | Digital Output Limit | 6 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | USINT | R/W | 52 | No
163 | 52 | 13 | Digital Output Limit | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 52 | No
163 | 52 | 15 | Digital Output Limit | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 52 | No
163 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 52 | No
163 | 52 | 20 | Digital Output Limit | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | UINT | R | 52 | No
164 | 1 | 5 | Digital Output Slow | 1 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 1 | 6 | Digital Output Slow | 1 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 1 | 7 | Digital Output Slow | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 1 | 12 | Digital Output Slow | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 1 | 13 | Digital Output Slow | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 1 | 15 | Digital Output Slow | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 1 | 20 | Digital Output Slow | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 2 | 5 | Digital Output Slow | 1 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 2 | 6 | Digital Output Slow | 1 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 2 | 7 | Digital Output Slow | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 2 | 12 | Digital Output Slow | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 2 | 13 | Digital Output Slow | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 2 | 15 | Digital Output Slow | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 2 | 20 | Digital Output Slow | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 3 | 5 | Digital Output Slow | 1 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 3 | 6 | Digital Output Slow | 1 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 3 | 7 | Digital Output Slow | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 3 | 12 | Digital Output Slow | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 3 | 13 | Digital Output Slow | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 3 | 15 | Digital Output Slow | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 3 | 20 | Digital Output Slow | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 4 | 5 | Digital Output Slow | 1 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 4 | 6 | Digital Output Slow | 1 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 4 | 7 | Digital Output Slow | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 4 | 12 | Digital Output Slow | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 4 | 13 | Digital Output Slow | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 4 | 15 | Digital Output Slow | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 4 | 20 | Digital Output Slow | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 11 | 5 | Digital Output Slow | 2 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 11 | 6 | Digital Output Slow | 2 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 11 | 7 | Digital Output Slow | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 11 | 12 | Digital Output Slow | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 11 | 13 | Digital Output Slow | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 11 | 15 | Digital Output Slow | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 11 | 20 | Digital Output Slow | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 12 | 5 | Digital Output Slow | 2 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 12 | 6 | Digital Output Slow | 2 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 12 | 7 | Digital Output Slow | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 12 | 12 | Digital Output Slow | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 12 | 13 | Digital Output Slow | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 12 | 15 | Digital Output Slow | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 12 | 20 | Digital Output Slow | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 13 | 5 | Digital Output Slow | 2 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 13 | 6 | Digital Output Slow | 2 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 13 | 7 | Digital Output Slow | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 13 | 12 | Digital Output Slow | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 13 | 13 | Digital Output Slow | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 13 | 15 | Digital Output Slow | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 13 | 20 | Digital Output Slow | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 14 | 5 | Digital Output Slow | 2 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 14 | 6 | Digital Output Slow | 2 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 14 | 7 | Digital Output Slow | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 14 | 12 | Digital Output Slow | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 14 | 13 | Digital Output Slow | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 14 | 15 | Digital Output Slow | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 14 | 20 | Digital Output Slow | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 21 | 5 | Digital Output Slow | 3 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 21 | 6 | Digital Output Slow | 3 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 21 | 7 | Digital Output Slow | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 21 | 12 | Digital Output Slow | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 21 | 13 | Digital Output Slow | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 21 | 15 | Digital Output Slow | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 21 | 20 | Digital Output Slow | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 22 | 5 | Digital Output Slow | 3 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 22 | 6 | Digital Output Slow | 3 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 22 | 7 | Digital Output Slow | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 22 | 12 | Digital Output Slow | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 22 | 13 | Digital Output Slow | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 22 | 15 | Digital Output Slow | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 22 | 20 | Digital Output Slow | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 23 | 5 | Digital Output Slow | 3 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 23 | 6 | Digital Output Slow | 3 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 23 | 7 | Digital Output Slow | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 23 | 12 | Digital Output Slow | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 23 | 13 | Digital Output Slow | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 23 | 15 | Digital Output Slow | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 23 | 20 | Digital Output Slow | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 24 | 5 | Digital Output Slow | 3 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 24 | 6 | Digital Output Slow | 3 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 24 | 7 | Digital Output Slow | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 24 | 12 | Digital Output Slow | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 24 | 13 | Digital Output Slow | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 24 | 15 | Digital Output Slow | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 24 | 20 | Digital Output Slow | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 31 | 5 | Digital Output Slow | 4 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 31 | 6 | Digital Output Slow | 4 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 31 | 7 | Digital Output Slow | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 31 | 12 | Digital Output Slow | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 31 | 13 | Digital Output Slow | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 31 | 15 | Digital Output Slow | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 31 | 20 | Digital Output Slow | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 32 | 5 | Digital Output Slow | 4 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 32 | 6 | Digital Output Slow | 4 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 32 | 7 | Digital Output Slow | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 32 | 12 | Digital Output Slow | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 32 | 13 | Digital Output Slow | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 32 | 15 | Digital Output Slow | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 32 | 20 | Digital Output Slow | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 33 | 5 | Digital Output Slow | 4 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 33 | 6 | Digital Output Slow | 4 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 33 | 7 | Digital Output Slow | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 33 | 12 | Digital Output Slow | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 33 | 13 | Digital Output Slow | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 33 | 15 | Digital Output Slow | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 33 | 20 | Digital Output Slow | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 34 | 5 | Digital Output Slow | 4 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 34 | 6 | Digital Output Slow | 4 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 34 | 7 | Digital Output Slow | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 34 | 12 | Digital Output Slow | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 34 | 13 | Digital Output Slow | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 34 | 15 | Digital Output Slow | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 34 | 20 | Digital Output Slow | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 41 | 5 | Digital Output Slow | 5 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 41 | 6 | Digital Output Slow | 5 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 41 | 7 | Digital Output Slow | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 41 | 12 | Digital Output Slow | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 41 | 13 | Digital Output Slow | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 41 | 15 | Digital Output Slow | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 41 | 20 | Digital Output Slow | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 42 | 5 | Digital Output Slow | 5 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 42 | 6 | Digital Output Slow | 5 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 42 | 7 | Digital Output Slow | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 42 | 12 | Digital Output Slow | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 42 | 13 | Digital Output Slow | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 42 | 15 | Digital Output Slow | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 42 | 20 | Digital Output Slow | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 43 | 5 | Digital Output Slow | 5 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 43 | 6 | Digital Output Slow | 5 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 43 | 7 | Digital Output Slow | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 43 | 12 | Digital Output Slow | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 43 | 13 | Digital Output Slow | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 43 | 15 | Digital Output Slow | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 43 | 20 | Digital Output Slow | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 44 | 5 | Digital Output Slow | 5 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 44 | 6 | Digital Output Slow | 5 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 44 | 7 | Digital Output Slow | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 44 | 12 | Digital Output Slow | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 44 | 13 | Digital Output Slow | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 44 | 15 | Digital Output Slow | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 44 | 20 | Digital Output Slow | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 51 | 5 | Digital Output Slow | 6 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 51 | 6 | Digital Output Slow | 6 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 51 | 7 | Digital Output Slow | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 51 | 12 | Digital Output Slow | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 51 | 13 | Digital Output Slow | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 51 | 15 | Digital Output Slow | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 51 | 20 | Digital Output Slow | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 52 | 5 | Digital Output Slow | 6 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 52 | 6 | Digital Output Slow | 6 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 52 | 7 | Digital Output Slow | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 52 | 12 | Digital Output Slow | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 52 | 13 | Digital Output Slow | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 52 | 15 | Digital Output Slow | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 52 | 20 | Digital Output Slow | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 53 | 5 | Digital Output Slow | 6 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 53 | 6 | Digital Output Slow | 6 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 53 | 7 | Digital Output Slow | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 53 | 12 | Digital Output Slow | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 53 | 13 | Digital Output Slow | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 53 | 15 | Digital Output Slow | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 53 | 20 | Digital Output Slow | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
164 | 54 | 5 | Digital Output Slow | 6 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | UINT | R/W | 54 | No
164 | 54 | 6 | Digital Output Slow | 6 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | USINT | R/W | 54 | No
164 | 54 | 7 | Digital Output Slow | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | UINT | R | 54 | No
164 | 54 | 12 | Digital Output Slow | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | USINT | R/W | 54 | No
164 | 54 | 13 | Digital Output Slow | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | REAL | R | 54 | No
164 | 54 | 15 | Digital Output Slow | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R | 54 | No
164 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 54 | No
164 | 54 | 20 | Digital Output Slow | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | UINT | R | 54 | No
174 | 1 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | UINT | R/W | 14 | Yes
174 | 1 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 14 | Yes
174 | 1 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | REAL | R/W | 14 | Yes
174 | 1 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | REAL | R/W | 14 | Yes
174 | 1 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | REAL | R/W | 14 | Yes
174 | 1 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | UINT | R/W | 14 | Yes
174 | 1 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | UINT | R/W | 14 | Yes
174 | 1 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 14 | Yes
174 | 1 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | UINT | R/W | 14 | Yes
174 | 1 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | UINT | R/W | 14 | Yes
174 | 1 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | UINT | R | 14 | Yes
174 | 1 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 1 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 1 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | UINT | R | 14 | No
174 | 1 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 1 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 1 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 1 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 1 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 1 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 1 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 1 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 1 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 1 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 1 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 1 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 1 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 1 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 1 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 1 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 1 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 1 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 1 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 1 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 1 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 1 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 1 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 1 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 1 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 1 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 1 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 14 | No
174 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 14 | No
174 | 1 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | UINT | R/W | 14 | Yes
174 | 2 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | UINT | R/W | 14 | Yes
174 | 2 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 14 | Yes
174 | 2 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | REAL | R/W | 14 | Yes
174 | 2 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | REAL | R/W | 14 | Yes
174 | 2 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | REAL | R/W | 14 | Yes
174 | 2 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | UINT | R/W | 14 | Yes
174 | 2 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | UINT | R/W | 14 | Yes
174 | 2 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 14 | Yes
174 | 2 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | UINT | R/W | 14 | Yes
174 | 2 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | UINT | R/W | 14 | Yes
174 | 2 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | UINT | R | 14 | Yes
174 | 2 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 2 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 2 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | UINT | R | 14 | No
174 | 2 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 2 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 2 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 2 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 2 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 2 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 2 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 2 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 2 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 2 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 2 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 2 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 2 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 2 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 2 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 2 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 2 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 2 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 2 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 2 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 2 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 2 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 2 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 2 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 2 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 2 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 2 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 14 | No
174 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 14 | No
174 | 2 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | UINT | R/W | 14 | Yes
174 | 3 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | UINT | R/W | 14 | Yes
174 | 3 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 14 | Yes
174 | 3 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | REAL | R/W | 14 | Yes
174 | 3 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | REAL | R/W | 14 | Yes
174 | 3 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | REAL | R/W | 14 | Yes
174 | 3 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | UINT | R/W | 14 | Yes
174 | 3 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | UINT | R/W | 14 | Yes
174 | 3 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 14 | Yes
174 | 3 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | UINT | R/W | 14 | Yes
174 | 3 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | UINT | R/W | 14 | Yes
174 | 3 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | UINT | R | 14 | Yes
174 | 3 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 3 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 3 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | UINT | R | 14 | No
174 | 3 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 3 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 3 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 3 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 3 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 3 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 3 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 3 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 3 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 3 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 3 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 3 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 3 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 3 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 3 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 3 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 3 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 3 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 3 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 3 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 3 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 3 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 3 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 3 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 3 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 3 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 3 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 14 | No
174 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 14 | No
174 | 3 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | UINT | R/W | 14 | Yes
174 | 4 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | UINT | R/W | 14 | Yes
174 | 4 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 14 | Yes
174 | 4 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | REAL | R/W | 14 | Yes
174 | 4 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | REAL | R/W | 14 | Yes
174 | 4 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | REAL | R/W | 14 | Yes
174 | 4 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | UINT | R/W | 14 | Yes
174 | 4 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | UINT | R/W | 14 | Yes
174 | 4 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 14 | Yes
174 | 4 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | UINT | R/W | 14 | Yes
174 | 4 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | UINT | R/W | 14 | Yes
174 | 4 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | UINT | R | 14 | Yes
174 | 4 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 4 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 4 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | UINT | R | 14 | No
174 | 4 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 4 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 4 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 4 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 4 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 4 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 4 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 4 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 4 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 4 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 4 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 4 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 4 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 4 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 4 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 4 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 4 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 4 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 4 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 4 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 4 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 4 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 4 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 4 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 4 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 4 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 4 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 14 | No
174 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 14 | No
174 | 4 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | UINT | R/W | 14 | Yes
174 | 5 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | UINT | R/W | 14 | Yes
174 | 5 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 14 | Yes
174 | 5 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | REAL | R/W | 14 | Yes
174 | 5 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | REAL | R/W | 14 | Yes
174 | 5 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | REAL | R/W | 14 | Yes
174 | 5 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | UINT | R/W | 14 | Yes
174 | 5 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | UINT | R/W | 14 | Yes
174 | 5 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 14 | Yes
174 | 5 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | UINT | R/W | 14 | Yes
174 | 5 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | UINT | R/W | 14 | Yes
174 | 5 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | UINT | R | 14 | Yes
174 | 5 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 5 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 5 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | UINT | R | 14 | No
174 | 5 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 5 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 5 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 5 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 5 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 5 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 5 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 5 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 5 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 5 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 5 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 5 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 5 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 5 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 5 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 5 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 5 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 5 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 5 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 5 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 5 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 5 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 5 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 5 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 5 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 5 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 5 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 14 | No
174 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 14 | No
174 | 5 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | UINT | R/W | 14 | Yes
174 | 6 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | UINT | R/W | 14 | Yes
174 | 6 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 14 | Yes
174 | 6 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | REAL | R/W | 14 | Yes
174 | 6 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | REAL | R/W | 14 | Yes
174 | 6 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | REAL | R/W | 14 | Yes
174 | 6 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | UINT | R/W | 14 | Yes
174 | 6 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | UINT | R/W | 14 | Yes
174 | 6 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 14 | Yes
174 | 6 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | UINT | R/W | 14 | Yes
174 | 6 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | UINT | R/W | 14 | Yes
174 | 6 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | UINT | R | 14 | Yes
174 | 6 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 6 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 6 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | UINT | R | 14 | No
174 | 6 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 6 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 6 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 6 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 6 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 6 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 6 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 6 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 6 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 6 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 6 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 6 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 6 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 6 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 6 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 6 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 6 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 6 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 6 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 6 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 6 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 6 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 6 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 6 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 6 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 6 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 6 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 14 | No
174 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 14 | No
174 | 6 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | UINT | R/W | 14 | Yes
174 | 7 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | UINT | R/W | 14 | Yes
174 | 7 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 14 | Yes
174 | 7 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | REAL | R/W | 14 | Yes
174 | 7 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | REAL | R/W | 14 | Yes
174 | 7 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | REAL | R/W | 14 | Yes
174 | 7 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | UINT | R/W | 14 | Yes
174 | 7 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | UINT | R/W | 14 | Yes
174 | 7 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 14 | Yes
174 | 7 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | UINT | R/W | 14 | Yes
174 | 7 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | UINT | R/W | 14 | Yes
174 | 7 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | UINT | R | 14 | Yes
174 | 7 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 7 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 7 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | UINT | R | 14 | No
174 | 7 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 7 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 7 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 7 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 7 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 7 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 7 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 7 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 7 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 7 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 7 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 7 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 7 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 7 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 7 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 7 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 7 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 7 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 7 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 7 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 7 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 7 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 7 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 7 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 7 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 7 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 7 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 14 | No
174 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 14 | No
174 | 7 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | UINT | R/W | 14 | Yes
174 | 8 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | UINT | R/W | 14 | Yes
174 | 8 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 14 | Yes
174 | 8 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | REAL | R/W | 14 | Yes
174 | 8 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | REAL | R/W | 14 | Yes
174 | 8 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | REAL | R/W | 14 | Yes
174 | 8 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | UINT | R/W | 14 | Yes
174 | 8 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | UINT | R/W | 14 | Yes
174 | 8 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 14 | Yes
174 | 8 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | UINT | R/W | 14 | Yes
174 | 8 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | UINT | R/W | 14 | Yes
174 | 8 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | UINT | R | 14 | Yes
174 | 8 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 8 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 8 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | UINT | R | 14 | No
174 | 8 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 8 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 8 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 8 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 8 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 8 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 8 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 8 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 8 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 8 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 8 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 8 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 8 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 8 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 8 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 8 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 8 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 8 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 8 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 8 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 8 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 8 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 8 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 8 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 8 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 8 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 8 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 14 | No
174 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 14 | No
174 | 8 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | UINT | R/W | 14 | Yes
174 | 9 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | UINT | R/W | 14 | Yes
174 | 9 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 14 | Yes
174 | 9 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | REAL | R/W | 14 | Yes
174 | 9 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | REAL | R/W | 14 | Yes
174 | 9 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | REAL | R/W | 14 | Yes
174 | 9 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | UINT | R/W | 14 | Yes
174 | 9 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | UINT | R/W | 14 | Yes
174 | 9 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 14 | Yes
174 | 9 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | UINT | R/W | 14 | Yes
174 | 9 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | UINT | R/W | 14 | Yes
174 | 9 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | UINT | R | 14 | Yes
174 | 9 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 9 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 9 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | UINT | R | 14 | No
174 | 9 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 9 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 9 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 9 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 9 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 9 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 9 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 9 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 9 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 9 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 9 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 9 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 9 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 9 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 9 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 9 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 9 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 9 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 9 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 9 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 9 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 9 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 9 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 9 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 9 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 9 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 9 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 14 | No
174 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 14 | No
174 | 9 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | UINT | R/W | 14 | Yes
174 | 10 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | UINT | R/W | 14 | Yes
174 | 10 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 14 | Yes
174 | 10 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | REAL | R/W | 14 | Yes
174 | 10 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | REAL | R/W | 14 | Yes
174 | 10 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | REAL | R/W | 14 | Yes
174 | 10 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | UINT | R/W | 14 | Yes
174 | 10 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | UINT | R/W | 14 | Yes
174 | 10 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 14 | Yes
174 | 10 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | UINT | R/W | 14 | Yes
174 | 10 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | UINT | R/W | 14 | Yes
174 | 10 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | UINT | R | 14 | Yes
174 | 10 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 10 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 10 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | UINT | R | 14 | No
174 | 10 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 10 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 10 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 10 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 10 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 10 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 10 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 10 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 10 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 10 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 10 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 10 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 10 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 10 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 10 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 10 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 10 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 10 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 10 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 10 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 10 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 10 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 10 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 10 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 10 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 10 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 10 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 14 | No
174 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 14 | No
174 | 10 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | UINT | R/W | 14 | Yes
174 | 11 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | UINT | R/W | 14 | Yes
174 | 11 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 14 | Yes
174 | 11 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | REAL | R/W | 14 | Yes
174 | 11 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | REAL | R/W | 14 | Yes
174 | 11 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | REAL | R/W | 14 | Yes
174 | 11 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | UINT | R/W | 14 | Yes
174 | 11 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | UINT | R/W | 14 | Yes
174 | 11 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 14 | Yes
174 | 11 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | UINT | R/W | 14 | Yes
174 | 11 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | UINT | R/W | 14 | Yes
174 | 11 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | UINT | R | 14 | Yes
174 | 11 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 11 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 11 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | UINT | R | 14 | No
174 | 11 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 11 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 11 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 11 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 11 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 11 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 11 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 11 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 11 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 11 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 11 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 11 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 11 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 11 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 11 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 11 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 11 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 11 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 11 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 11 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 11 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 11 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 11 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 11 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 11 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 11 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 11 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 14 | No
174 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 14 | No
174 | 11 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | UINT | R/W | 14 | Yes
174 | 12 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | UINT | R/W | 14 | Yes
174 | 12 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 14 | Yes
174 | 12 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | REAL | R/W | 14 | Yes
174 | 12 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | REAL | R/W | 14 | Yes
174 | 12 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | REAL | R/W | 14 | Yes
174 | 12 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | UINT | R/W | 14 | Yes
174 | 12 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | UINT | R/W | 14 | Yes
174 | 12 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 14 | Yes
174 | 12 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | UINT | R/W | 14 | Yes
174 | 12 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | UINT | R/W | 14 | Yes
174 | 12 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | UINT | R | 14 | Yes
174 | 12 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 12 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 12 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | UINT | R | 14 | No
174 | 12 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 12 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 12 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 12 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 12 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 12 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 12 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 12 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 12 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 12 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 12 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 12 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 12 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 12 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 12 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 12 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 12 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 12 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 12 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 12 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 12 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 12 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 12 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 12 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 12 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 12 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 12 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 14 | No
174 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 14 | No
174 | 12 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | UINT | R/W | 14 | Yes
174 | 13 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | UINT | R/W | 14 | Yes
174 | 13 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 14 | Yes
174 | 13 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | REAL | R/W | 14 | Yes
174 | 13 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | REAL | R/W | 14 | Yes
174 | 13 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | REAL | R/W | 14 | Yes
174 | 13 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | UINT | R/W | 14 | Yes
174 | 13 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | UINT | R/W | 14 | Yes
174 | 13 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 14 | Yes
174 | 13 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | UINT | R/W | 14 | Yes
174 | 13 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | UINT | R/W | 14 | Yes
174 | 13 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | UINT | R | 14 | Yes
174 | 13 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 13 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 13 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | UINT | R | 14 | No
174 | 13 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 13 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 13 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 13 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 13 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 13 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 13 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 13 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 13 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 13 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 13 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 13 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 13 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 13 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 13 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 13 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 13 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 13 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 13 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 13 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 13 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 13 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 13 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 13 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 13 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 13 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 13 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 14 | No
174 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 14 | No
174 | 13 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | UINT | R/W | 14 | Yes
174 | 14 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | UINT | R/W | 14 | Yes
174 | 14 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 14 | Yes
174 | 14 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | REAL | R/W | 14 | Yes
174 | 14 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | REAL | R/W | 14 | Yes
174 | 14 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | REAL | R/W | 14 | Yes
174 | 14 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | UINT | R/W | 14 | Yes
174 | 14 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | UINT | R/W | 14 | Yes
174 | 14 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 14 | Yes
174 | 14 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | UINT | R/W | 14 | Yes
174 | 14 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | UINT | R/W | 14 | Yes
174 | 14 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | UINT | R | 14 | Yes
174 | 14 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 14 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | UINT | R/W | 14 | Yes
174 | 14 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | UINT | R | 14 | No
174 | 14 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 14 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 14 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | UINT | R | 14 | No
174 | 14 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 14 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 14 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 14 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 14 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 14 | No
174 | 14 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 14 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 14 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | REAL | R | 14 | No
174 | 14 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 14 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 14 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 14 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 14 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 14 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 14 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 14 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 14 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 14 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 14 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 14 | No
174 | 14 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | USINT | R/W | 14 | No
174 | 14 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | USINT | R/W | 14 | No
174 | 14 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | UINT | R | 14 | No
174 | 14 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | UINT | R/W | 14 | No
174 | 14 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 14 | No
174 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 14 | No
174 | 14 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | UINT | R/W | 14 | Yes
175 | 1 | 1 | Control Loop | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | UINT | R/W | 4 | Yes
175 | 1 | 2 | Control Loop | Base | Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | UINT | R/W | 4 | Yes
175 | 1 | 3 | Control Loop | Base | Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | UINT | R/W | 4 | Yes
175 | 1 | 4 | Control Loop | Base | Integral 1 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 1 | 5 | Control Loop | Base | Derivative 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 1 | 6 | Control Loop | Base | Dead Band | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 1 | 7 | Control Loop | Base | Heat Proportional Band 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 1 | 8 | Control Loop | Base | On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | REAL | R/W | 4 | Yes
175 | 1 | 9 | Control Loop | Base | Cool Proportional Band 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 1 | 10 | Control Loop | Base | On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | REAL | R/W | 4 | Yes
175 | 1 | 11 | Control Loop | Base | TRU-TUNE+ Enable | Set to enable or disable the TRU-TUNE+® adaptive tuning feature. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | Yes
175 | 1 | 12 | Control Loop | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | UINT | R/W | 4 | Yes
175 | 1 | 13 | Control Loop | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | REAL | R/W | 4 | Yes
175 | 1 | 14 | Control Loop | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | Yes
175 | 1 | 15 | Control Loop | Base | TRU-TUNE+ Band | Set the range, centered on the set point, within which TRU-TUNE+® will be in effect. | 0 to 100 | 0 | UINT | R/W | 4 | Yes
175 | 1 | 16 | Control Loop | Base | TRU-TUNE+ Gain | Set the responsiveness of the TRU-TUNE+® adaptive tuning calculations. | 1 to 6 | 3 | USINT | R/W | 4 | Yes
175 | 1 | 18 | Control Loop | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | UINT | R/W | 4 | Yes
175 | 1 | 19 | Control Loop | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | Yes
175 | 1 | 20 | Control Loop | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | UINT | R/W | 4 | Yes
175 | 1 | 21 | Control Loop | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | REAL | R/W | 4 | Yes
175 | 1 | 22 | Control Loop | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | UINT | R | 4 | Yes
175 | 1 | 23 | Control Loop | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 4 | Yes
175 | 1 | 24 | Control Loop | Base | Peltier Delay | Set a value that will cause a delay when switching from heat PID mode to cool PID mode. | 0.0 to 5.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 1 | 25 | Control Loop | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | REAL | R/W | 4 | Yes
175 | 1 | 26 | Control Loop | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | REAL | R/W | 4 | Yes
175 | 1 | 27 | Control Loop | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | REAL | R/W | 4 | Yes
175 | 1 | 28 | Control Loop | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | REAL | R/W | 4 | Yes
175 | 1 | 29 | Control Loop | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | REAL | R/W | 4 | Yes
175 | 1 | 30 | Control Loop | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | REAL | R/W | 4 | Yes
175 | 1 | 31 | Control Loop | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | REAL | R/W | 4 | Yes
175 | 1 | 32 | Control Loop | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | UINT | R/W | 4 | Yes
175 | 1 | 33 | Control Loop | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | UINT | R/W | 4 | Yes
175 | 1 | 34 | Control Loop | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | REAL | R/W | 4 | Yes
175 | 1 | 35 | Control Loop | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 4 | Yes
175 | 1 | 36 | Control Loop | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | UINT | R/W | 4 | Yes
175 | 1 | 37 | Control Loop | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | REAL | R/W | 4 | Yes
175 | 1 | 39 | Control Loop | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | Yes
175 | 1 | 40 | Control Loop | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | UINT | R/W | 4 | Yes
175 | 1 | 41 | Control Loop | Base | Heat Power | Monitor the PID heat power. | 0.0 to 100.0 |  | REAL | R | 4 | Yes
175 | 1 | 42 | Control Loop | Base | Cool Power | Monitor the PID cool power. | -100.0 to 0.0 |  | REAL | R | 4 | Yes
175 | 1 | 43 | Control Loop | Base | Control Loop Output Power | Monitor the PID total power. | -100.0 to 100.0 |  | REAL | R | 4 | Yes
175 | 1 | 44 | Control Loop | Base | Closed-Loop Set Point | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | REAL | R | 4 | Yes
175 | 1 | 45 | Control Loop | Base | Open-Loop Working Power | Monitor the set point used by the control loop while in manual mode. | -100.0 to 100.0 |  | REAL | R | 4 | Yes
175 | 1 | 46 | Control Loop | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | UINT | R | 4 | Yes
175 | 1 | 47 | Control Loop | Base | Control Action | Set the control loop action. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | UINT | R/W | 4 | Yes
175 | 1 | 48 | Control Loop | Base | Heat Proportional Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 1 | 49 | Control Loop | Base | Heat Integral Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 1 | 50 | Control Loop | Base | Heat Derivative Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 1 | 51 | Control Loop | Base | Cool Proportional Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 1 | 52 | Control Loop | Base | Cool Integral Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 1 | 53 | Control Loop | Base | Cool Derivative Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 1 | 54 | Control Loop | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | UINT | R | 4 | Yes
175 | 1 | 55 | Control Loop | Base | Input Error |  | None (61), Error (28) |  | UINT | R | 4 | No
175 | 1 | 56 | Control Loop | Base | Working Manual Source |  | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) |  | UINT | R | 4 | No
175 | 1 | 57 | Control Loop | Base | Set Point Active Closed |  |  |  | REAL | R | 4 | No
175 | 1 | 58 | Control Loop | Base | Set Point Active Open |  |  |  | REAL | R | 4 | No
175 | 1 | 59 | Control Loop | Base | Set Point Bumpless |  |  |  | REAL | R | 4 | No
175 | 1 | 60 | Control Loop | Base | Ramp Set Point |  |  |  | REAL | R | 4 | No
175 | 1 | 61 | Control Loop | Base | Idle Set Point |  |  |  | REAL | R | 4 | No
175 | 1 | 62 | Control Loop | Base | Ramp Set Point |  |  |  | REAL | R | 4 | No
175 | 1 | 63 | Control Loop | Base | Source Function A |  | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 4 | No
175 | 1 | 64 | Control Loop | Base | Source Instance A |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 1 | 65 | Control Loop | Base | Source Zone A |  | 0 to 0 | 0 | USINT | R/W | 4 | No
175 | 1 | 66 | Control Loop | Base | Source Value A | Monitor the analog input value used by the control loop while in auto mode. |  |  | REAL | R | 4 | No
175 | 1 | 67 | Control Loop | Base | Source Function B |  | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 4 | No
175 | 1 | 68 | Control Loop | Base | Source Instance B |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 1 | 69 | Control Loop | Base | Source Zone B |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 1 | 70 | Control Loop | Base | Source Value B | Monitor the remote set point value. |  |  | REAL | R | 4 | No
175 | 1 | 71 | Control Loop | Base | Source Function C | Set the source of remote set point for the control loop. | None (61), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778) | None (61) | UINT | R/W | 4 | No
175 | 1 | 72 | Control Loop | Base | Source Instance C |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 1 | 73 | Control Loop | Base | Source Zone C |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 1 | 74 | Control Loop | Base | Source Value C | Monitor the set point used by the control loop while a profile is active. |  |  | REAL | R | 4 | No
175 | 1 | 75 | Control Loop | Base | Source Function D |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 1 | 76 | Control Loop | Base | Source Instance D |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 1 | 77 | Control Loop | Base | Source Zone D |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 1 | 78 | Control Loop | Base | Source Value D |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 1 | 79 | Control Loop | Base | Use Remote SP Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 1 | 80 | Control Loop | Base | Source Function E |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 1 | 81 | Control Loop | Base | Source Instance E |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 1 | 82 | Control Loop | Base | Source Zone E |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 1 | 83 | Control Loop | Base | Source Value E |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 1 | 84 | Control Loop | Base | Use Idle SP Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 1 | 85 | Control Loop | Base | Source Function F |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 1 | 86 | Control Loop | Base | Source Instance F |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 1 | 87 | Control Loop | Base | Source Zone F |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 1 | 88 | Control Loop | Base | Source Value F |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 1 | 89 | Control Loop | Base | Off Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 1 | 90 | Control Loop | Base | Source Function G |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 1 | 91 | Control Loop | Base | Source Instance G |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 1 | 92 | Control Loop | Base | Source Zone G |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 1 | 93 | Control Loop | Base | Source Value G |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 1 | 94 | Control Loop | Base | Manual Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 1 | 95 | Control Loop | Base | Source Function H |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 1 | 96 | Control Loop | Base | Source Instance H |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 1 | 97 | Control Loop | Base | Source Zone H |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 1 | 98 | Control Loop | Base | Source Value H |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 1 | 99 | Control Loop | Base | Initiate Autotune Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 1 | 100 | Control Loop | Base | Source Function A |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 1 | 101 | Control Loop | Base | Source Instance A |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 1 | 102 | Control Loop | Base | Source Zone A |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 1 | 103 | Control Loop | Base | Source Value A |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 1 | 104 | Control Loop | Base | Disable TRU-TUNE+ Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 1 | 107 | Control Loop | Base | Profile End Action | Set profile end action for control loop when end step is not specified in profile. | User (100), Off (62), Hold (47) | User (100) | UINT | R/W | 4 | Yes
175 | 1 | 108 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 1 | 109 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 1 | 110 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 1 | 111 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 1 | 112 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 4 | No
175 | 1 | 114 | Control Loop | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | UINT | R/W | 4 | Yes
175 | 1 | 115 | Control Loop | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. | -99,999.0 to 99,999.0 |  | REAL | R/W | 4 | Yes
175 | 1 | 116 | Control Loop | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. | -99,999.0 to 99,999.0 |  | REAL | R/W | 4 | Yes
175 | 1 | 117 | Control Loop | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. | -99,999.0 to 99,999.0 |  | REAL | R/W | 4 | Yes
175 | 1 | 118 | Control Loop | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. | -99,999.0 to 99,999.0 |  | REAL | R/W | 4 | Yes
175 | 1 | 119 | Control Loop | Base | PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | USINT | R | 4 | Yes
175 | 1 | 120 | Control Loop | Base | Heat Proportional Band 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 1 | 121 | Control Loop | Base | Cool Proportional Band 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 1 | 122 | Control Loop | Base | Integral 2 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 1 | 123 | Control Loop | Base | Derivative 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 1 | 124 | Control Loop | Base | Heat Proportional Band 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 1 | 125 | Control Loop | Base | Cool Proportional Band 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 1 | 126 | Control Loop | Base | Integral 3 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 1 | 127 | Control Loop | Base | Derivative 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 1 | 128 | Control Loop | Base | Heat Proportional Band 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 1 | 129 | Control Loop | Base | Cool Proportional Band 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 1 | 130 | Control Loop | Base | Integral 4 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 1 | 131 | Control Loop | Base | Derivative 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 1 | 132 | Control Loop | Base | Heat Proportional Band 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 1 | 133 | Control Loop | Base | Cool Proportional Band 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 1 | 134 | Control Loop | Base | Integral 5 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 1 | 135 | Control Loop | Base | Derivative 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 1 | 136 | Control Loop | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | USINT | R/W | 4 | Yes
175 | 1 | 137 | Control Loop | Base | Control Loop Control Mode Is Off | Monitor the Control Loop Control Mode is Off. | On (63), Off (62) |  | UINT | R | 4 | Yes
175 | 1 | 138 | Control Loop | Base | Set Point | Moniotr the closed loop set point. | -99,999.0 to 99,999.0 |  | REAL | R | 4 | No
175 | 2 | 1 | Control Loop | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | UINT | R/W | 4 | Yes
175 | 2 | 2 | Control Loop | Base | Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | UINT | R/W | 4 | Yes
175 | 2 | 3 | Control Loop | Base | Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | UINT | R/W | 4 | Yes
175 | 2 | 4 | Control Loop | Base | Integral 1 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 2 | 5 | Control Loop | Base | Derivative 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 2 | 6 | Control Loop | Base | Dead Band | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 2 | 7 | Control Loop | Base | Heat Proportional Band 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 2 | 8 | Control Loop | Base | On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | REAL | R/W | 4 | Yes
175 | 2 | 9 | Control Loop | Base | Cool Proportional Band 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 2 | 10 | Control Loop | Base | On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | REAL | R/W | 4 | Yes
175 | 2 | 11 | Control Loop | Base | TRU-TUNE+ Enable | Set to enable or disable the TRU-TUNE+® adaptive tuning feature. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | Yes
175 | 2 | 12 | Control Loop | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | UINT | R/W | 4 | Yes
175 | 2 | 13 | Control Loop | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | REAL | R/W | 4 | Yes
175 | 2 | 14 | Control Loop | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | Yes
175 | 2 | 15 | Control Loop | Base | TRU-TUNE+ Band | Set the range, centered on the set point, within which TRU-TUNE+® will be in effect. | 0 to 100 | 0 | UINT | R/W | 4 | Yes
175 | 2 | 16 | Control Loop | Base | TRU-TUNE+ Gain | Set the responsiveness of the TRU-TUNE+® adaptive tuning calculations. | 1 to 6 | 3 | USINT | R/W | 4 | Yes
175 | 2 | 18 | Control Loop | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | UINT | R/W | 4 | Yes
175 | 2 | 19 | Control Loop | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | Yes
175 | 2 | 20 | Control Loop | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | UINT | R/W | 4 | Yes
175 | 2 | 21 | Control Loop | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | REAL | R/W | 4 | Yes
175 | 2 | 22 | Control Loop | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | UINT | R | 4 | Yes
175 | 2 | 23 | Control Loop | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 4 | Yes
175 | 2 | 24 | Control Loop | Base | Peltier Delay | Set a value that will cause a delay when switching from heat PID mode to cool PID mode. | 0.0 to 5.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 2 | 25 | Control Loop | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | REAL | R/W | 4 | Yes
175 | 2 | 26 | Control Loop | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | REAL | R/W | 4 | Yes
175 | 2 | 27 | Control Loop | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | REAL | R/W | 4 | Yes
175 | 2 | 28 | Control Loop | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | REAL | R/W | 4 | Yes
175 | 2 | 29 | Control Loop | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | REAL | R/W | 4 | Yes
175 | 2 | 30 | Control Loop | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | REAL | R/W | 4 | Yes
175 | 2 | 31 | Control Loop | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | REAL | R/W | 4 | Yes
175 | 2 | 32 | Control Loop | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | UINT | R/W | 4 | Yes
175 | 2 | 33 | Control Loop | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | UINT | R/W | 4 | Yes
175 | 2 | 34 | Control Loop | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | REAL | R/W | 4 | Yes
175 | 2 | 35 | Control Loop | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 4 | Yes
175 | 2 | 36 | Control Loop | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | UINT | R/W | 4 | Yes
175 | 2 | 37 | Control Loop | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | REAL | R/W | 4 | Yes
175 | 2 | 39 | Control Loop | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | Yes
175 | 2 | 40 | Control Loop | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | UINT | R/W | 4 | Yes
175 | 2 | 41 | Control Loop | Base | Heat Power | Monitor the PID heat power. | 0.0 to 100.0 |  | REAL | R | 4 | Yes
175 | 2 | 42 | Control Loop | Base | Cool Power | Monitor the PID cool power. | -100.0 to 0.0 |  | REAL | R | 4 | Yes
175 | 2 | 43 | Control Loop | Base | Control Loop Output Power | Monitor the PID total power. | -100.0 to 100.0 |  | REAL | R | 4 | Yes
175 | 2 | 44 | Control Loop | Base | Closed-Loop Set Point | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | REAL | R | 4 | Yes
175 | 2 | 45 | Control Loop | Base | Open-Loop Working Power | Monitor the set point used by the control loop while in manual mode. | -100.0 to 100.0 |  | REAL | R | 4 | Yes
175 | 2 | 46 | Control Loop | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | UINT | R | 4 | Yes
175 | 2 | 47 | Control Loop | Base | Control Action | Set the control loop action. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | UINT | R/W | 4 | Yes
175 | 2 | 48 | Control Loop | Base | Heat Proportional Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 2 | 49 | Control Loop | Base | Heat Integral Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 2 | 50 | Control Loop | Base | Heat Derivative Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 2 | 51 | Control Loop | Base | Cool Proportional Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 2 | 52 | Control Loop | Base | Cool Integral Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 2 | 53 | Control Loop | Base | Cool Derivative Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 2 | 54 | Control Loop | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | UINT | R | 4 | Yes
175 | 2 | 55 | Control Loop | Base | Input Error |  | None (61), Error (28) |  | UINT | R | 4 | No
175 | 2 | 56 | Control Loop | Base | Working Manual Source |  | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) |  | UINT | R | 4 | No
175 | 2 | 57 | Control Loop | Base | Set Point Active Closed |  |  |  | REAL | R | 4 | No
175 | 2 | 58 | Control Loop | Base | Set Point Active Open |  |  |  | REAL | R | 4 | No
175 | 2 | 59 | Control Loop | Base | Set Point Bumpless |  |  |  | REAL | R | 4 | No
175 | 2 | 60 | Control Loop | Base | Ramp Set Point |  |  |  | REAL | R | 4 | No
175 | 2 | 61 | Control Loop | Base | Idle Set Point |  |  |  | REAL | R | 4 | No
175 | 2 | 62 | Control Loop | Base | Ramp Set Point |  |  |  | REAL | R | 4 | No
175 | 2 | 63 | Control Loop | Base | Source Function A |  | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 4 | No
175 | 2 | 64 | Control Loop | Base | Source Instance A |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 2 | 65 | Control Loop | Base | Source Zone A |  | 0 to 0 | 0 | USINT | R/W | 4 | No
175 | 2 | 66 | Control Loop | Base | Source Value A | Monitor the analog input value used by the control loop while in auto mode. |  |  | REAL | R | 4 | No
175 | 2 | 67 | Control Loop | Base | Source Function B |  | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 4 | No
175 | 2 | 68 | Control Loop | Base | Source Instance B |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 2 | 69 | Control Loop | Base | Source Zone B |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 2 | 70 | Control Loop | Base | Source Value B | Monitor the remote set point value. |  |  | REAL | R | 4 | No
175 | 2 | 71 | Control Loop | Base | Source Function C | Set the source of remote set point for the control loop. | None (61), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778) | None (61) | UINT | R/W | 4 | No
175 | 2 | 72 | Control Loop | Base | Source Instance C |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 2 | 73 | Control Loop | Base | Source Zone C |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 2 | 74 | Control Loop | Base | Source Value C | Monitor the set point used by the control loop while a profile is active. |  |  | REAL | R | 4 | No
175 | 2 | 75 | Control Loop | Base | Source Function D |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 2 | 76 | Control Loop | Base | Source Instance D |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 2 | 77 | Control Loop | Base | Source Zone D |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 2 | 78 | Control Loop | Base | Source Value D |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 2 | 79 | Control Loop | Base | Use Remote SP Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 2 | 80 | Control Loop | Base | Source Function E |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 2 | 81 | Control Loop | Base | Source Instance E |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 2 | 82 | Control Loop | Base | Source Zone E |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 2 | 83 | Control Loop | Base | Source Value E |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 2 | 84 | Control Loop | Base | Use Idle SP Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 2 | 85 | Control Loop | Base | Source Function F |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 2 | 86 | Control Loop | Base | Source Instance F |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 2 | 87 | Control Loop | Base | Source Zone F |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 2 | 88 | Control Loop | Base | Source Value F |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 2 | 89 | Control Loop | Base | Off Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 2 | 90 | Control Loop | Base | Source Function G |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 2 | 91 | Control Loop | Base | Source Instance G |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 2 | 92 | Control Loop | Base | Source Zone G |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 2 | 93 | Control Loop | Base | Source Value G |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 2 | 94 | Control Loop | Base | Manual Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 2 | 95 | Control Loop | Base | Source Function H |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 2 | 96 | Control Loop | Base | Source Instance H |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 2 | 97 | Control Loop | Base | Source Zone H |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 2 | 98 | Control Loop | Base | Source Value H |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 2 | 99 | Control Loop | Base | Initiate Autotune Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 2 | 100 | Control Loop | Base | Source Function A |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 2 | 101 | Control Loop | Base | Source Instance A |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 2 | 102 | Control Loop | Base | Source Zone A |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 2 | 103 | Control Loop | Base | Source Value A |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 2 | 104 | Control Loop | Base | Disable TRU-TUNE+ Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 2 | 107 | Control Loop | Base | Profile End Action | Set profile end action for control loop when end step is not specified in profile. | User (100), Off (62), Hold (47) | User (100) | UINT | R/W | 4 | Yes
175 | 2 | 108 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 2 | 109 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 2 | 110 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 2 | 111 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 2 | 112 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 4 | No
175 | 2 | 114 | Control Loop | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | UINT | R/W | 4 | Yes
175 | 2 | 115 | Control Loop | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. | -99,999.0 to 99,999.0 |  | REAL | R/W | 4 | Yes
175 | 2 | 116 | Control Loop | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. | -99,999.0 to 99,999.0 |  | REAL | R/W | 4 | Yes
175 | 2 | 117 | Control Loop | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. | -99,999.0 to 99,999.0 |  | REAL | R/W | 4 | Yes
175 | 2 | 118 | Control Loop | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. | -99,999.0 to 99,999.0 |  | REAL | R/W | 4 | Yes
175 | 2 | 119 | Control Loop | Base | PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | USINT | R | 4 | Yes
175 | 2 | 120 | Control Loop | Base | Heat Proportional Band 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 2 | 121 | Control Loop | Base | Cool Proportional Band 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 2 | 122 | Control Loop | Base | Integral 2 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 2 | 123 | Control Loop | Base | Derivative 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 2 | 124 | Control Loop | Base | Heat Proportional Band 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 2 | 125 | Control Loop | Base | Cool Proportional Band 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 2 | 126 | Control Loop | Base | Integral 3 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 2 | 127 | Control Loop | Base | Derivative 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 2 | 128 | Control Loop | Base | Heat Proportional Band 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 2 | 129 | Control Loop | Base | Cool Proportional Band 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 2 | 130 | Control Loop | Base | Integral 4 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 2 | 131 | Control Loop | Base | Derivative 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 2 | 132 | Control Loop | Base | Heat Proportional Band 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 2 | 133 | Control Loop | Base | Cool Proportional Band 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 2 | 134 | Control Loop | Base | Integral 5 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 2 | 135 | Control Loop | Base | Derivative 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 2 | 136 | Control Loop | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | USINT | R/W | 4 | Yes
175 | 2 | 137 | Control Loop | Base | Control Loop Control Mode Is Off | Monitor the Control Loop Control Mode is Off. | On (63), Off (62) |  | UINT | R | 4 | Yes
175 | 2 | 138 | Control Loop | Base | Set Point | Monitor the control mode is in Off state. | -99,999.0 to 99,999.0 |  | REAL | R | 4 | No
175 | 3 | 1 | Control Loop | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | UINT | R/W | 4 | Yes
175 | 3 | 2 | Control Loop | Base | Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | UINT | R/W | 4 | Yes
175 | 3 | 3 | Control Loop | Base | Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | UINT | R/W | 4 | Yes
175 | 3 | 4 | Control Loop | Base | Integral 1 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 3 | 5 | Control Loop | Base | Derivative 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 3 | 6 | Control Loop | Base | Dead Band | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 3 | 7 | Control Loop | Base | Heat Proportional Band 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 3 | 8 | Control Loop | Base | On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | REAL | R/W | 4 | Yes
175 | 3 | 9 | Control Loop | Base | Cool Proportional Band 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 3 | 10 | Control Loop | Base | On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | REAL | R/W | 4 | Yes
175 | 3 | 11 | Control Loop | Base | TRU-TUNE+ Enable | Set to enable or disable the TRU-TUNE+® adaptive tuning feature. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | Yes
175 | 3 | 12 | Control Loop | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | UINT | R/W | 4 | Yes
175 | 3 | 13 | Control Loop | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | REAL | R/W | 4 | Yes
175 | 3 | 14 | Control Loop | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | Yes
175 | 3 | 15 | Control Loop | Base | TRU-TUNE+ Band | Set the range, centered on the set point, within which TRU-TUNE+® will be in effect. | 0 to 100 | 0 | UINT | R/W | 4 | Yes
175 | 3 | 16 | Control Loop | Base | TRU-TUNE+ Gain | Set the responsiveness of the TRU-TUNE+® adaptive tuning calculations. | 1 to 6 | 3 | USINT | R/W | 4 | Yes
175 | 3 | 18 | Control Loop | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | UINT | R/W | 4 | Yes
175 | 3 | 19 | Control Loop | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | Yes
175 | 3 | 20 | Control Loop | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | UINT | R/W | 4 | Yes
175 | 3 | 21 | Control Loop | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | REAL | R/W | 4 | Yes
175 | 3 | 22 | Control Loop | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | UINT | R | 4 | Yes
175 | 3 | 23 | Control Loop | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 4 | Yes
175 | 3 | 24 | Control Loop | Base | Peltier Delay | Set a value that will cause a delay when switching from heat PID mode to cool PID mode. | 0.0 to 5.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 3 | 25 | Control Loop | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | REAL | R/W | 4 | Yes
175 | 3 | 26 | Control Loop | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | REAL | R/W | 4 | Yes
175 | 3 | 27 | Control Loop | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | REAL | R/W | 4 | Yes
175 | 3 | 28 | Control Loop | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | REAL | R/W | 4 | Yes
175 | 3 | 29 | Control Loop | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | REAL | R/W | 4 | Yes
175 | 3 | 30 | Control Loop | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | REAL | R/W | 4 | Yes
175 | 3 | 31 | Control Loop | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | REAL | R/W | 4 | Yes
175 | 3 | 32 | Control Loop | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | UINT | R/W | 4 | Yes
175 | 3 | 33 | Control Loop | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | UINT | R/W | 4 | Yes
175 | 3 | 34 | Control Loop | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | REAL | R/W | 4 | Yes
175 | 3 | 35 | Control Loop | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 4 | Yes
175 | 3 | 36 | Control Loop | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | UINT | R/W | 4 | Yes
175 | 3 | 37 | Control Loop | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | REAL | R/W | 4 | Yes
175 | 3 | 39 | Control Loop | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | Yes
175 | 3 | 40 | Control Loop | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | UINT | R/W | 4 | Yes
175 | 3 | 41 | Control Loop | Base | Heat Power | Monitor the PID heat power. | 0.0 to 100.0 |  | REAL | R | 4 | Yes
175 | 3 | 42 | Control Loop | Base | Cool Power | Monitor the PID cool power. | -100.0 to 0.0 |  | REAL | R | 4 | Yes
175 | 3 | 43 | Control Loop | Base | Control Loop Output Power | Monitor the PID total power. | -100.0 to 100.0 |  | REAL | R | 4 | Yes
175 | 3 | 44 | Control Loop | Base | Closed-Loop Set Point | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | REAL | R | 4 | Yes
175 | 3 | 45 | Control Loop | Base | Open-Loop Working Power | Monitor the set point used by the control loop while in manual mode. | -100.0 to 100.0 |  | REAL | R | 4 | Yes
175 | 3 | 46 | Control Loop | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | UINT | R | 4 | Yes
175 | 3 | 47 | Control Loop | Base | Control Action | Set the control loop action. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | UINT | R/W | 4 | Yes
175 | 3 | 48 | Control Loop | Base | Heat Proportional Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 3 | 49 | Control Loop | Base | Heat Integral Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 3 | 50 | Control Loop | Base | Heat Derivative Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 3 | 51 | Control Loop | Base | Cool Proportional Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 3 | 52 | Control Loop | Base | Cool Integral Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 3 | 53 | Control Loop | Base | Cool Derivative Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 3 | 54 | Control Loop | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | UINT | R | 4 | Yes
175 | 3 | 55 | Control Loop | Base | Input Error |  | None (61), Error (28) |  | UINT | R | 4 | No
175 | 3 | 56 | Control Loop | Base | Working Manual Source |  | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) |  | UINT | R | 4 | No
175 | 3 | 57 | Control Loop | Base | Set Point Active Closed |  |  |  | REAL | R | 4 | No
175 | 3 | 58 | Control Loop | Base | Set Point Active Open |  |  |  | REAL | R | 4 | No
175 | 3 | 59 | Control Loop | Base | Set Point Bumpless |  |  |  | REAL | R | 4 | No
175 | 3 | 60 | Control Loop | Base | Ramp Set Point |  |  |  | REAL | R | 4 | No
175 | 3 | 61 | Control Loop | Base | Idle Set Point |  |  |  | REAL | R | 4 | No
175 | 3 | 62 | Control Loop | Base | Ramp Set Point |  |  |  | REAL | R | 4 | No
175 | 3 | 63 | Control Loop | Base | Source Function A |  | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 4 | No
175 | 3 | 64 | Control Loop | Base | Source Instance A |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 3 | 65 | Control Loop | Base | Source Zone A |  | 0 to 0 | 0 | USINT | R/W | 4 | No
175 | 3 | 66 | Control Loop | Base | Source Value A | Monitor the analog input value used by the control loop while in auto mode. |  |  | REAL | R | 4 | No
175 | 3 | 67 | Control Loop | Base | Source Function B |  | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 4 | No
175 | 3 | 68 | Control Loop | Base | Source Instance B |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 3 | 69 | Control Loop | Base | Source Zone B |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 3 | 70 | Control Loop | Base | Source Value B | Monitor the remote set point value. |  |  | REAL | R | 4 | No
175 | 3 | 71 | Control Loop | Base | Source Function C | Set the source of remote set point for the control loop. | None (61), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778) | None (61) | UINT | R/W | 4 | No
175 | 3 | 72 | Control Loop | Base | Source Instance C |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 3 | 73 | Control Loop | Base | Source Zone C |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 3 | 74 | Control Loop | Base | Source Value C | Monitor the set point used by the control loop while a profile is active. |  |  | REAL | R | 4 | No
175 | 3 | 75 | Control Loop | Base | Source Function D |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 3 | 76 | Control Loop | Base | Source Instance D |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 3 | 77 | Control Loop | Base | Source Zone D |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 3 | 78 | Control Loop | Base | Source Value D |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 3 | 79 | Control Loop | Base | Use Remote SP Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 3 | 80 | Control Loop | Base | Source Function E |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 3 | 81 | Control Loop | Base | Source Instance E |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 3 | 82 | Control Loop | Base | Source Zone E |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 3 | 83 | Control Loop | Base | Source Value E |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 3 | 84 | Control Loop | Base | Use Idle SP Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 3 | 85 | Control Loop | Base | Source Function F |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 3 | 86 | Control Loop | Base | Source Instance F |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 3 | 87 | Control Loop | Base | Source Zone F |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 3 | 88 | Control Loop | Base | Source Value F |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 3 | 89 | Control Loop | Base | Off Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 3 | 90 | Control Loop | Base | Source Function G |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 3 | 91 | Control Loop | Base | Source Instance G |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 3 | 92 | Control Loop | Base | Source Zone G |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 3 | 93 | Control Loop | Base | Source Value G |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 3 | 94 | Control Loop | Base | Manual Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 3 | 95 | Control Loop | Base | Source Function H |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 3 | 96 | Control Loop | Base | Source Instance H |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 3 | 97 | Control Loop | Base | Source Zone H |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 3 | 98 | Control Loop | Base | Source Value H |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 3 | 99 | Control Loop | Base | Initiate Autotune Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 3 | 100 | Control Loop | Base | Source Function A |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 3 | 101 | Control Loop | Base | Source Instance A |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 3 | 102 | Control Loop | Base | Source Zone A |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 3 | 103 | Control Loop | Base | Source Value A |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 3 | 104 | Control Loop | Base | Disable TRU-TUNE+ Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 3 | 107 | Control Loop | Base | Profile End Action | Set profile end action for control loop when end step is not specified. | User (100), Off (62), Hold (47) | User (100) | UINT | R/W | 4 | Yes
175 | 3 | 108 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 3 | 109 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 3 | 110 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 3 | 111 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 3 | 112 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 4 | No
175 | 3 | 114 | Control Loop | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | UINT | R/W | 4 | Yes
175 | 3 | 115 | Control Loop | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. | -99,999.0 to 99,999.0 |  | REAL | R/W | 4 | Yes
175 | 3 | 116 | Control Loop | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. | -99,999.0 to 99,999.0 |  | REAL | R/W | 4 | Yes
175 | 3 | 117 | Control Loop | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. | -99,999.0 to 99,999.0 |  | REAL | R/W | 4 | Yes
175 | 3 | 118 | Control Loop | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. | -99,999.0 to 99,999.0 |  | REAL | R/W | 4 | Yes
175 | 3 | 119 | Control Loop | Base | PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | USINT | R | 4 | Yes
175 | 3 | 120 | Control Loop | Base | Heat Proportional Band 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 3 | 121 | Control Loop | Base | Cool Proportional Band 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 3 | 122 | Control Loop | Base | Integral 2 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 3 | 123 | Control Loop | Base | Derivative 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 3 | 124 | Control Loop | Base | Heat Proportional Band 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 3 | 125 | Control Loop | Base | Cool Proportional Band 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 3 | 126 | Control Loop | Base | Integral 3 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 3 | 127 | Control Loop | Base | Derivative 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 3 | 128 | Control Loop | Base | Heat Proportional Band 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 3 | 129 | Control Loop | Base | Cool Proportional Band 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 3 | 130 | Control Loop | Base | Integral 4 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 3 | 131 | Control Loop | Base | Derivative 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 3 | 132 | Control Loop | Base | Heat Proportional Band 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 3 | 133 | Control Loop | Base | Cool Proportional Band 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 3 | 134 | Control Loop | Base | Integral 5 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 3 | 135 | Control Loop | Base | Derivative 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 3 | 136 | Control Loop | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | USINT | R/W | 4 | Yes
175 | 3 | 137 | Control Loop | Base | Control Loop Control Mode Is Off | Monitor the Control Loop Control Mode is Off. | On (63), Off (62) |  | UINT | R | 4 | Yes
175 | 3 | 138 | Control Loop | Base | Set Point | Monitor the control mode is in Off state. | -99,999.0 to 99,999.0 |  | REAL | R | 4 | No
175 | 4 | 1 | Control Loop | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | UINT | R/W | 4 | Yes
175 | 4 | 2 | Control Loop | Base | Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | UINT | R/W | 4 | Yes
175 | 4 | 3 | Control Loop | Base | Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | UINT | R/W | 4 | Yes
175 | 4 | 4 | Control Loop | Base | Integral 1 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 4 | 5 | Control Loop | Base | Derivative 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 4 | 6 | Control Loop | Base | Dead Band | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 4 | 7 | Control Loop | Base | Heat Proportional Band 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 4 | 8 | Control Loop | Base | On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | REAL | R/W | 4 | Yes
175 | 4 | 9 | Control Loop | Base | Cool Proportional Band 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 4 | 10 | Control Loop | Base | On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | REAL | R/W | 4 | Yes
175 | 4 | 11 | Control Loop | Base | TRU-TUNE+ Enable | Set to enable or disable the TRU-TUNE+® adaptive tuning feature. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | Yes
175 | 4 | 12 | Control Loop | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | UINT | R/W | 4 | Yes
175 | 4 | 13 | Control Loop | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | REAL | R/W | 4 | Yes
175 | 4 | 14 | Control Loop | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | Yes
175 | 4 | 15 | Control Loop | Base | TRU-TUNE+ Band | Set the range, centered on the set point, within which TRU-TUNE+® will be in effect. | 0 to 100 | 0 | UINT | R/W | 4 | Yes
175 | 4 | 16 | Control Loop | Base | TRU-TUNE+ Gain | Set the responsiveness of the TRU-TUNE+® adaptive tuning calculations. | 1 to 6 | 3 | USINT | R/W | 4 | Yes
175 | 4 | 18 | Control Loop | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | UINT | R/W | 4 | Yes
175 | 4 | 19 | Control Loop | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | Yes
175 | 4 | 20 | Control Loop | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | UINT | R/W | 4 | Yes
175 | 4 | 21 | Control Loop | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | REAL | R/W | 4 | Yes
175 | 4 | 22 | Control Loop | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | UINT | R | 4 | Yes
175 | 4 | 23 | Control Loop | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 4 | Yes
175 | 4 | 24 | Control Loop | Base | Peltier Delay | Set a value that will cause a delay when switching from heat PID mode to cool PID mode. | 0.0 to 5.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 4 | 25 | Control Loop | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | REAL | R/W | 4 | Yes
175 | 4 | 26 | Control Loop | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | REAL | R/W | 4 | Yes
175 | 4 | 27 | Control Loop | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | REAL | R/W | 4 | Yes
175 | 4 | 28 | Control Loop | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | REAL | R/W | 4 | Yes
175 | 4 | 29 | Control Loop | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | REAL | R/W | 4 | Yes
175 | 4 | 30 | Control Loop | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | REAL | R/W | 4 | Yes
175 | 4 | 31 | Control Loop | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | REAL | R/W | 4 | Yes
175 | 4 | 32 | Control Loop | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | UINT | R/W | 4 | Yes
175 | 4 | 33 | Control Loop | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | UINT | R/W | 4 | Yes
175 | 4 | 34 | Control Loop | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | REAL | R/W | 4 | Yes
175 | 4 | 35 | Control Loop | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | UINT | R/W | 4 | Yes
175 | 4 | 36 | Control Loop | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | UINT | R/W | 4 | Yes
175 | 4 | 37 | Control Loop | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | REAL | R/W | 4 | Yes
175 | 4 | 39 | Control Loop | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | Yes
175 | 4 | 40 | Control Loop | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | UINT | R/W | 4 | Yes
175 | 4 | 41 | Control Loop | Base | Heat Power | Monitor the PID heat power. | 0.0 to 100.0 |  | REAL | R | 4 | Yes
175 | 4 | 42 | Control Loop | Base | Cool Power | Monitor the PID cool power. | -100.0 to 0.0 |  | REAL | R | 4 | Yes
175 | 4 | 43 | Control Loop | Base | Control Loop Output Power | Monitor the PID total power. | -100.0 to 100.0 |  | REAL | R | 4 | Yes
175 | 4 | 44 | Control Loop | Base | Closed-Loop Set Point | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | REAL | R | 4 | Yes
175 | 4 | 45 | Control Loop | Base | Open-Loop Working Power | Monitor the set point used by the control loop while in manual mode. | -100.0 to 100.0 |  | REAL | R | 4 | Yes
175 | 4 | 46 | Control Loop | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | UINT | R | 4 | Yes
175 | 4 | 47 | Control Loop | Base | Control Action | Set the control loop action. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | UINT | R/W | 4 | Yes
175 | 4 | 48 | Control Loop | Base | Heat Proportional Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 4 | 49 | Control Loop | Base | Heat Integral Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 4 | 50 | Control Loop | Base | Heat Derivative Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 4 | 51 | Control Loop | Base | Cool Proportional Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 4 | 52 | Control Loop | Base | Cool Integral Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 4 | 53 | Control Loop | Base | Cool Derivative Term |  | -100.0 to 100.0 |  | REAL | R | 4 | No
175 | 4 | 54 | Control Loop | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | UINT | R | 4 | Yes
175 | 4 | 55 | Control Loop | Base | Input Error |  | None (61), Error (28) |  | UINT | R | 4 | No
175 | 4 | 56 | Control Loop | Base | Working Manual Source |  | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) |  | UINT | R | 4 | No
175 | 4 | 57 | Control Loop | Base | Set Point Active Closed |  |  |  | REAL | R | 4 | No
175 | 4 | 58 | Control Loop | Base | Set Point Active Open |  |  |  | REAL | R | 4 | No
175 | 4 | 59 | Control Loop | Base | Set Point Bumpless |  |  |  | REAL | R | 4 | No
175 | 4 | 60 | Control Loop | Base | Ramp Set Point |  |  |  | REAL | R | 4 | No
175 | 4 | 61 | Control Loop | Base | Idle Set Point |  |  |  | REAL | R | 4 | No
175 | 4 | 62 | Control Loop | Base | Ramp Set Point |  |  |  | REAL | R | 4 | No
175 | 4 | 63 | Control Loop | Base | Source Function A |  | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 4 | No
175 | 4 | 64 | Control Loop | Base | Source Instance A |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 4 | 65 | Control Loop | Base | Source Zone A |  | 0 to 0 | 0 | USINT | R/W | 4 | No
175 | 4 | 66 | Control Loop | Base | Source Value A | Monitor the analog input value used by the control loop while in auto mode. |  |  | REAL | R | 4 | No
175 | 4 | 67 | Control Loop | Base | Source Function B |  | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 4 | No
175 | 4 | 68 | Control Loop | Base | Source Instance B |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 4 | 69 | Control Loop | Base | Source Zone B |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 4 | 70 | Control Loop | Base | Source Value B | Monitor the remote set point value. |  |  | REAL | R | 4 | No
175 | 4 | 71 | Control Loop | Base | Source Function C | Set the source of remote set point for the control loop. | None (61), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778) | None (61) | UINT | R/W | 4 | No
175 | 4 | 72 | Control Loop | Base | Source Instance C |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 4 | 73 | Control Loop | Base | Source Zone C |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 4 | 74 | Control Loop | Base | Source Value C | Monitor the set point used by the control loop while a profile is active. |  |  | REAL | R | 4 | No
175 | 4 | 75 | Control Loop | Base | Source Function D |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 4 | 76 | Control Loop | Base | Source Instance D |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 4 | 77 | Control Loop | Base | Source Zone D |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 4 | 78 | Control Loop | Base | Source Value D |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 4 | 79 | Control Loop | Base | Use Remote SP Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 4 | 80 | Control Loop | Base | Source Function E |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 4 | 81 | Control Loop | Base | Source Instance E |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 4 | 82 | Control Loop | Base | Source Zone E |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 4 | 83 | Control Loop | Base | Source Value E |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 4 | 84 | Control Loop | Base | Use Idle SP Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 4 | 85 | Control Loop | Base | Source Function F |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 4 | 86 | Control Loop | Base | Source Instance F |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 4 | 87 | Control Loop | Base | Source Zone F |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 4 | 88 | Control Loop | Base | Source Value F |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 4 | 89 | Control Loop | Base | Off Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 4 | 90 | Control Loop | Base | Source Function G |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 4 | 91 | Control Loop | Base | Source Instance G |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 4 | 92 | Control Loop | Base | Source Zone G |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 4 | 93 | Control Loop | Base | Source Value G |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 4 | 94 | Control Loop | Base | Manual Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 4 | 95 | Control Loop | Base | Source Function H |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 4 | 96 | Control Loop | Base | Source Instance H |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 4 | 97 | Control Loop | Base | Source Zone H |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 4 | 98 | Control Loop | Base | Source Value H |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 4 | 99 | Control Loop | Base | Initiate Autotune Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 4 | 100 | Control Loop | Base | Source Function A |  | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 4 | No
175 | 4 | 101 | Control Loop | Base | Source Instance A |  | 1 to 250 | 1 | USINT | R/W | 4 | No
175 | 4 | 102 | Control Loop | Base | Source Zone A |  | 0 to 24 | 0 | USINT | R/W | 4 | No
175 | 4 | 103 | Control Loop | Base | Source Value A |  | On (63), Off (62) |  | UINT | R | 4 | No
175 | 4 | 104 | Control Loop | Base | Disable TRU-TUNE+ Active Level |  | High (37), Low (53) | High (37) | UINT | R/W | 4 | Yes
175 | 4 | 107 | Control Loop | Base | Profile End Action | Set profile end action for control loop when end step is not specified. | User (100), Off (62), Hold (47) | User (100) | UINT | R/W | 4 | Yes
175 | 4 | 108 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 4 | 109 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 4 | 110 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 4 | 111 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 4 | 112 | Control Loop | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 4 | No
175 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 4 | No
175 | 4 | 114 | Control Loop | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | UINT | R/W | 4 | Yes
175 | 4 | 115 | Control Loop | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. | -99,999.0 to 99,999.0 |  | REAL | R/W | 4 | Yes
175 | 4 | 116 | Control Loop | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. | -99,999.0 to 99,999.0 |  | REAL | R/W | 4 | Yes
175 | 4 | 117 | Control Loop | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. | -99,999.0 to 99,999.0 |  | REAL | R/W | 4 | Yes
175 | 4 | 118 | Control Loop | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. | -99,999.0 to 99,999.0 |  | REAL | R/W | 4 | Yes
175 | 4 | 119 | Control Loop | Base | PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | USINT | R | 4 | Yes
175 | 4 | 120 | Control Loop | Base | Heat Proportional Band 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 4 | 121 | Control Loop | Base | Cool Proportional Band 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 4 | 122 | Control Loop | Base | Integral 2 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 4 | 123 | Control Loop | Base | Derivative 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 4 | 124 | Control Loop | Base | Heat Proportional Band 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 4 | 125 | Control Loop | Base | Cool Proportional Band 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 4 | 126 | Control Loop | Base | Integral 3 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 4 | 127 | Control Loop | Base | Derivative 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 4 | 128 | Control Loop | Base | Heat Proportional Band 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 4 | 129 | Control Loop | Base | Cool Proportional Band 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 4 | 130 | Control Loop | Base | Integral 4 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 4 | 131 | Control Loop | Base | Derivative 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 4 | 132 | Control Loop | Base | Heat Proportional Band 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 4 | 133 | Control Loop | Base | Cool Proportional Band 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | REAL | R/W | 4 | Yes
175 | 4 | 134 | Control Loop | Base | Integral 5 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | REAL | R/W | 4 | Yes
175 | 4 | 135 | Control Loop | Base | Derivative 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | REAL | R/W | 4 | Yes
175 | 4 | 136 | Control Loop | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | USINT | R/W | 4 | Yes
175 | 4 | 137 | Control Loop | Base | Control Loop Control Mode Is Off | Monitor the Control Loop Control Mode is Off. | On (63), Off (62) |  | UINT | R | 4 | Yes
175 | 4 | 138 | Control Loop | Base | Set Point | Monitor the control mode is in Off state. | -99,999.0 to 99,999.0 |  | REAL | R | 4 | No
179 | 1 | 1 | Profile | Base | Units | Monitor units applied to PV1 receiver of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | UINT | R | 1 | No
179 | 1 | 2 | Profile | Base | Units | Monitor units applied to PV2 receiver of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | UINT | R | 1 | No
179 | 1 | 3 | Profile | Base | Units | Monitor units applied to PV3 receiver of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | UINT | R | 1 | No
179 | 1 | 4 | Profile | Base | Units | Monitor units applied to PV4 receiver of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | UINT | R | 1 | No
179 | 1 | 5 | Profile | Base | Units | Monitor units applied to EVT1 receiver when analog of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | UINT | R | 1 | No
179 | 1 | 6 | Profile | Base | Units | Monitor units applied to EVT2 receiver when analog of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | UINT | R | 1 | No
179 | 1 | 7 | Profile | Base | Units | Monitor units applied to EVT3 receiver when analog of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | UINT | R | 1 | No
179 | 1 | 8 | Profile | Base | Units | Monitor units applied to EVT4 receiver when analog of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | UINT | R | 1 | No
179 | 1 | 12 | Profile | Base | Start Profile | Enter Profile number to queue for start or calendar start via Profile Action Request. | 1 to 40 | 1 | UINT | R/W | 1 | No
179 | 1 | 13 | Profile | Base | Start Step | Enter Profile Step number to queue for start via Profile Action Request. |  | 1 | UINT | R/W | 1 | No
179 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | UINT | R/W | 1 | No
179 | 1 | 15 | Profile | Base | Profile Action Request | Resume a profile previously paused. | None (61), Resume (147) | None (61) | UINT | R/W | 1 | No
179 | 1 | 16 | Profile | Base | Profile Action Request | Pause running profile or terminate running profile. | None (61), Pause (146), Terminate (148) | None (61) | UINT | R/W | 1 | No
179 | 1 | 17 | Profile | Base | Profile State | Monitor state of profile. | Off (62), Running (149), Pause (146), Not Started (251), Completed Normal (252), Terminated (253), Calendar Start (1783) |  | UINT | R | 1 | No
179 | 1 | 18 | Profile | Base | Minutes | Monitor time remaining in profile (minutes portion). | 0 to 59 |  | USINT | R | 1 | No
179 | 1 | 19 | Profile | Base | Hours | Monitor time remaining in profile (hours portion). | 0 to 9,999 |  | UINT | R | 1 | No
179 | 1 | 20 | Profile | Base | Power Out Minutes | Set power out time (minutes portion). | 0 to 59 |  | USINT | R/W | 1 | Yes
179 | 1 | 21 | Profile | Base | Power Out Hours | Set power out time (hours portion). | 0 to 99 |  | USINT | R/W | 1 | Yes
179 | 1 | 23 | Profile | Base | Calendar Start Minute | Set Calendar Start time (minutes portion) for this profile. | 0 to 59 | 0 | USINT | R/W | 1 | Yes
179 | 1 | 24 | Profile | Base | Calendar Start Hour | Set Calendar Start time (hours portion) for this profile. | 0 to 23 | 0 | USINT | R/W | 1 | Yes
179 | 1 | 25 | Profile | Base | Calendar Start Day | Set Calendar Start time (day of week portion) for this profile. | Sunday (1565), Monday (1559), Tuesday (1560), Wednesday (1561), Thursday (1562), Friday (1563), Saturday (1564) | Monday (1559) | UINT | R/W | 1 | Yes
179 | 1 | 27 | Profile | Base | Current Profile | Monitor current file loaded in memory. | 0 to 40 | 1 | UINT | R | 1 | Yes
179 | 1 | 28 | Profile | Base | Current Step | Monitor current step loaded in memory. |  | 1 | UINT | R | 1 | No
179 | 1 | 29 | Profile | Base | Step Type | Monitor current step type loaded in memory. | Soak (87), Wait For (1542), Instant Change (1927), Jump (116), Ramp Time (1928), Ramp Rate (81), End (27) |  | UINT | R | 1 | No
179 | 1 | 30 | Profile | Base | Event 1 | Monitor/change current step Event Output 1 transmitter (ENT1) loaded in memory. | Off (62), On (63) | Off (62) | UINT | R/W | 1 | Yes
179 | 1 | 31 | Profile | Base | Event 2 | Monitor/change current step Event Output 2 transmitter (ENT2) loaded in memory. | Off (62), On (63) | Off (62) | UINT | R/W | 1 | Yes
179 | 1 | 32 | Profile | Base | Event 3 | Monitor/change current step Event Output 3 transmitter (ENT3) loaded in memory. | Off (62), On (63) | Off (62) | UINT | R/W | 1 | Yes
179 | 1 | 33 | Profile | Base | Event 4 | Monitor/change current step Event Output 4 transmitter (ENT4) loaded in memory. | Off (62), On (63) | Off (62) | UINT | R/W | 1 | Yes
179 | 1 | 34 | Profile | Base | Target Set Point Loop 1 | Monitor/Set Target Set Point Loop 1 for current step. | -99,999.0 to 99,999.0 |  | REAL | R/W | 1 | No
179 | 1 | 35 | Profile | Base | Target Set Point Loop 2 | Monitor/Set Target Set Point Loop 2 for current step. | -99,999.0 to 99,999.0 |  | REAL | R/W | 1 | No
179 | 1 | 36 | Profile | Base | Target Set Point Loop 3 | Monitor/Set Target Set Point Loop 3 for current step. | -99,999.0 to 99,999.0 |  | REAL | R/W | 1 | No
179 | 1 | 37 | Profile | Base | Target Set Point Loop 4 | Monitor/Set Target Set Point Loop 4 for current step. | -99,999.0 to 99,999.0 |  | REAL | R/W | 1 | No
179 | 1 | 38 | Profile | Base | Produced Set Point 1 | Monitor Produced Set Point 1 for current step. (SP1) | -99,999.0 to 99,999.0 | 0.0 | REAL | R | 1 | Yes
179 | 1 | 39 | Profile | Base | Produced Set Point 2 | Monitor Produced Set Point 2 for current step. (SP2) | -99,999.0 to 99,999.0 | 0.0 | REAL | R | 1 | Yes
179 | 1 | 40 | Profile | Base | Produced Set Point 3 | Monitor Produced Set Point 3 for current step. (SP3) | -99,999.0 to 99,999.0 | 0.0 | REAL | R | 1 | Yes
179 | 1 | 41 | Profile | Base | Produced Set Point 4 | Monitor Produced Set Point 4 for current step. (SP4) | -99,999.0 to 99,999.0 | 0.0 | REAL | R | 1 | Yes
179 | 1 | 42 | Profile | Base | Status | Monitor the Wait-for Status, Returns bit values for Event 1, 2, 3 and 4. If condition is met, appropriate bit is 1. Possible returned values are 1 to 16 if all four events inputs are connected. | 0 to 65,535 | 0 | UINT | R | 1 | No
179 | 1 | 43 | Profile | Base | Step Time Remaining | Monitor the current total Step Time remaining in seconds. | 0.0 to 3,600,000.0 | 0.0 | REAL | R | 1 | No
179 | 1 | 44 | Profile | Base | Seconds | Monitor the current Step Time remaining (seconds portion). | 0 to 59 | 0 | USINT | R/W | 1 | No
179 | 1 | 45 | Profile | Base | Minutes | Monitor the current total Step Time remaining (minutes portion). | 0 to 59 | 0 | USINT | R/W | 1 | No
179 | 1 | 46 | Profile | Base | Hours | Monitor the current total Step Time remaining (hours portion). | 0 to 999 | 0 | UINT | R/W | 1 | No
179 | 1 | 47 | Profile | Base | Name |  | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 1 | No
179 | 1 | 48 | Profile | Base | Name |  | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 1 | No
179 | 1 | 49 | Profile | Base | Name |  | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 1 | No
179 | 1 | 50 | Profile | Base | Name |  | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 1 | No
179 | 1 | 53 | Profile | Base | Source Function A | Set source to PV1 receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 1 | No
179 | 1 | 54 | Profile | Base | Source Function B | Set source to PV2 receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 1 | No
179 | 1 | 55 | Profile | Base | Source Function C | Set source to PV3 receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 1 | No
179 | 1 | 56 | Profile | Base | Source Function D | Set source to PV4 receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 1 | No
179 | 1 | 57 | Profile | Base | Source Instance A | Set source instance to PV1 receiver on profile function block. | 1 to 250 | 1 | USINT | R/W | 1 | No
179 | 1 | 58 | Profile | Base | Source Instance B | Set source instance to PV2 receiver on profile function block. | 1 to 250 | 1 | USINT | R/W | 1 | No
179 | 1 | 59 | Profile | Base | Source Instance C | Set source instance to PV3 receiver on profile function block. | 1 to 250 | 1 | USINT | R/W | 1 | No
179 | 1 | 60 | Profile | Base | Source Instance D | Set source instance to PV4 receiver on profile function block. | 1 to 250 | 1 | USINT | R/W | 1 | No
179 | 1 | 61 | Profile | Base | Source Zone A | Set source ZONE to PV1 receiver on profile function block. | 0 to 24 | 0 | USINT | R/W | 1 | No
179 | 1 | 62 | Profile | Base | Source Zone B | Set source ZONE to PV2 receiver on profile function block. | 0 to 24 | 0 | USINT | R/W | 1 | No
179 | 1 | 63 | Profile | Base | Source Zone C | Set source ZONE to PV3 receiver on profile function block. | 0 to 24 | 0 | USINT | R/W | 1 | No
179 | 1 | 64 | Profile | Base | Source Zone D | Set source ZONE to PV4 receiver on profile function block. | 0 to 24 | 0 | USINT | R/W | 1 | No
179 | 1 | 65 | Profile | Base | Source Value A | Monitor analog source value of PV1 source. | -99,999.0 to 99,999.0 |  | REAL | R | 1 | No
179 | 1 | 66 | Profile | Base | Source Value B | Monitor analog source value of PV2 source. | -99,999.0 to 99,999.0 |  | REAL | R | 1 | No
179 | 1 | 67 | Profile | Base | Source Value C | Monitor analog source value of PV3 source. | -99,999.0 to 99,999.0 |  | REAL | R | 1 | No
179 | 1 | 68 | Profile | Base | Source Value D | Monitor analog source value of PV4 source. | -99,999.0 to 99,999.0 |  | REAL | R | 1 | No
179 | 1 | 69 | Profile | Base | Source Function A | Set source to EVT1 receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 1 | No
179 | 1 | 70 | Profile | Base | Source Function B | Set source to EVT2 receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 1 | No
179 | 1 | 71 | Profile | Base | Source Function C | Set source to EVT3 receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 1 | No
179 | 1 | 72 | Profile | Base | Source Function D | Set source to EVT4 receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 1 | No
179 | 1 | 73 | Profile | Base | Source Instance A | Set source instance to ENT1 receiver on profile function block. | 1 to 250 | 1 | USINT | R/W | 1 | No
179 | 1 | 74 | Profile | Base | Source Instance B | Set source instance to ENT2 receiver on profile function block. | 1 to 250 | 1 | USINT | R/W | 1 | No
179 | 1 | 75 | Profile | Base | Source Instance C | Set source instance to ENT3 receiver on profile function block. | 1 to 250 | 1 | USINT | R/W | 1 | No
179 | 1 | 76 | Profile | Base | Source Instance D | Set source instance to ENT4 receiver on profile function block. | 1 to 250 | 1 | USINT | R/W | 1 | No
179 | 1 | 77 | Profile | Base | Source Zone A | Set source zone to ENT1 receiver on profile function block. | 0 to 24 | 0 | USINT | R/W | 1 | No
179 | 1 | 78 | Profile | Base | Source Zone B | Set source zone to ENT2 receiver on profile function block. | 0 to 24 | 0 | USINT | R/W | 1 | No
179 | 1 | 79 | Profile | Base | Source Zone C | Set source zone to ENT3 receiver on profile function block. | 0 to 24 | 0 | USINT | R/W | 1 | No
179 | 1 | 80 | Profile | Base | Source Zone D | Set source zone to ENT4 receiver on profile function block. | 0 to 24 | 0 | USINT | R/W | 1 | No
179 | 1 | 81 | Profile | Base | Source Value A | Monitor Wait-for source value applied to EVT1 receiver when digital of profile function block. | On (63), Off (62) | [n/a] | UINT | R | 1 | No
179 | 1 | 82 | Profile | Base | Source Value B | Monitor Wait-for source value applied to EVT2 receiver when digital of profile function block. | On (63), Off (62) | [n/a] | UINT | R | 1 | No
179 | 1 | 83 | Profile | Base | Source Value C | Monitor Wait-for source value applied to EVT3 receiver when digital of profile function block. | On (63), Off (62) | [n/a] | UINT | R | 1 | No
179 | 1 | 84 | Profile | Base | Source Value D | Monitor Wait-for source value applied to EVT4 receiver when digital of profile function block. | On (63), Off (62) | [n/a] | UINT | R | 1 | No
179 | 1 | 85 | Profile | Base | Source Function E | Set source to S/T receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 1 | No
179 | 1 | 86 | Profile | Base | Source Function F | Set source to STRT receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 1 | No
179 | 1 | 87 | Profile | Base | Source Function G | Set source to P/R receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 1 | No
179 | 1 | 88 | Profile | Base | Source Function H | Set source to DIS receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 1 | No
179 | 1 | 89 | Profile | Base | Source Instance E | Set source instance to S/T receiver on profile function block. | 1 to 250 | 1 | USINT | R/W | 1 | No
179 | 1 | 90 | Profile | Base | Source Instance F | Set source instance to STRT receiver on profile function block. | 1 to 250 | 1 | USINT | R/W | 1 | No
179 | 1 | 91 | Profile | Base | Source Instance G | Set source instance to P/R receiver on profile function block. | 1 to 250 | 1 | USINT | R/W | 1 | No
179 | 1 | 92 | Profile | Base | Source Instance H | Set source instance to DIS receiver on profile function block. | 1 to 250 | 1 | USINT | R/W | 1 | No
179 | 1 | 93 | Profile | Base | Source Zone E | Set source zone to S/T receiver on profile function block. | 0 to 24 | 0 | USINT | R/W | 1 | No
179 | 1 | 94 | Profile | Base | Source Zone F | Set source zone to STRT receiver on profile function block. | 0 to 24 | 0 | USINT | R/W | 1 | No
179 | 1 | 95 | Profile | Base | Source Zone G | Set source zone to P/R receiver on profile function block. | 0 to 24 | 0 | USINT | R/W | 1 | No
179 | 1 | 96 | Profile | Base | Source Zone H | Set source zone to DIS receiver on profile function block. | 0 to 24 | 0 | USINT | R/W | 1 | No
179 | 1 | 97 | Profile | Base | Source Value E | Monitor source value to S/T receiver on profile function block. | On (63), Off (62) |  | UINT | R | 1 | No
179 | 1 | 98 | Profile | Base | Source Value F | Monitor source value to STRT receiver on profile function block. | On (63), Off (62) |  | UINT | R | 1 | No
179 | 1 | 99 | Profile | Base | Source Value G | Monitor source value to P/R receiver on profile function block. | On (63), Off (62) |  | UINT | R | 1 | No
179 | 1 | 100 | Profile | Base | Source Value H | Monitor source value to DIS receiver on profile function block. | On (63), Off (62) |  | UINT | R | 1 | No
179 | 1 | 101 | Profile | Base | Start / Stop Active Level | Set Active Level for S/T receiver on profile function block. | High (37), Low (53) | High (37) | UINT | R/W | 1 | Yes
179 | 1 | 102 | Profile | Base | Start Active Level | Set Active Level for STRT receiver on profile function block. | High (37), Low (53) | High (37) | UINT | R/W | 1 | Yes
179 | 1 | 103 | Profile | Base | Pause / Resume Active Level | Set Active Level for P/R receiver on profile function block. | High (37), Low (53) | High (37) | UINT | R/W | 1 | Yes
179 | 1 | 104 | Profile | Base | Disable Active Level | Set Active Level for DIS receiver on profile function block. | High (37), Low (53) | High (37) | UINT | R/W | 1 | Yes
179 | 1 | 105 | Profile | Base | Source Function A | Set source to PRF receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 1 | No
179 | 1 | 106 | Profile | Base | Source Function B | Set source to STP receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 1 | No
179 | 1 | 107 | Profile | Base | Source Instance A | Set source instance to PRF receiver on profile function block. | 1 to 250 | 1 | USINT | R/W | 1 | No
179 | 1 | 108 | Profile | Base | Source Instance B | Set source instance to STP receiver on profile function block. | 1 to 250 | 1 | USINT | R/W | 1 | No
179 | 1 | 109 | Profile | Base | Source Zone A | Set source zone to PRF receiver on profile function block. | 0 to 24 | 0 | USINT | R/W | 1 | No
179 | 1 | 110 | Profile | Base | Source Zone B | Set source zone to STP receiver on profile function block. | 0 to 24 | 0 | USINT | R/W | 1 | No
179 | 1 | 111 | Profile | Base | Source Value A | Monitor profile number source value to PRF receiver on profile function block. | -99,999.0 to 99,999.0 |  | REAL | R | 1 | No
179 | 1 | 112 | Profile | Base | Source Value B | Monitor step number source value to STP receiver on profile function block. | -99,999.0 to 99,999.0 |  | REAL | R | 1 | No
179 | 1 | 113 | Profile | Base | Rate | If step type is rate, monitor/change ramp rate for control loop 1. | 0 to 9,999.000 | 0.0 | REAL | R/W | 1 | No
179 | 1 | 114 | Profile | Base | Rate | If step type is rate, monitor/change ramp rate for control loop 2. | 0 to 9,999.000 | 0.0 | REAL | R/W | 1 | No
179 | 1 | 115 | Profile | Base | Rate | If step type is rate, monitor/change ramp rate for control loop 3. | 0 to 9,999.000 | 0.0 | REAL | R/W | 1 | No
179 | 1 | 116 | Profile | Base | Rate | If step type is rate, monitor/change ramp rate for control loop 4. | 0 to 9,999.000 | 0.0 | REAL | R/W | 1 | No
179 | 1 | 119 | Profile | Base | Profile Running | Monitor profile running status. | On (63), Off (62) |  | UINT | R | 1 | Yes
179 | 1 | 120 | Profile | Base | Profile Paused | Monitor profile paused status. | On (63), Off (62) |  | UINT | R | 1 | Yes
179 | 1 | 125 | Profile | Base | Error | Monitor error status for produced set point 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 1 | No
179 | 1 | 126 | Profile | Base | Error | Monitor error status for produced set point 2. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 1 | No
179 | 1 | 127 | Profile | Base | Error | Monitor error status for produced set point 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 1 | No
179 | 1 | 128 | Profile | Base | Error | Monitor error status for produced set point 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 1 | No
179 | 1 | 129 | Profile | Base | Error | Monitor error status for produced event output 1 transmitter (EVT1). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 1 | No
179 | 1 | 130 | Profile | Base | Error | Monitor error status for produced event output 2 transmitter (EVT2). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 1 | No
179 | 1 | 131 | Profile | Base | Error | Monitor error status for produced event output 3 transmitter (EVT3). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 1 | No
179 | 1 | 132 | Profile | Base | Error | Monitor error status for produced event output 4 transmitter (EVT4). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 1 | No
179 | 1 | 133 | Profile | Base | Error | Monitor error status for profile running. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 1 | No
179 | 1 | 134 | Profile | Base | Error | Monitor error status for profile paused. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 1 | No
179 | 1 | 135 | Profile | Base | Error | Monitor error status for current profile. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 1 | No
179 | 1 | 136 | Profile | Base | Error | Monitor error status for current profile step. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 1 | No
179 | 1 | 137 | Profile | Base | Unknown | Monitor control loop 1 precision. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) |  | UINT | R | 1 | No
179 | 1 | 138 | Profile | Base | Unknown | Monitor control loop 2 precision. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) |  | UINT | R | 1 | No
179 | 1 | 139 | Profile | Base | Unknown | Monitor control loop 3 precision. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) |  | UINT | R | 1 | No
179 | 1 | 140 | Profile | Base | Unknown | Monitor control loop 4 precision. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) |  | UINT | R | 1 | No
179 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 20 bytes (UTF-8) |  | SHORT_STRING | R | 1 | No
179 | 1 | 142 | Profile | Base | Profile State | Monitor the profile status. | Off (62), Running (149), Pause (146), Not Started (251), Completed Normal (252), Terminated (253), Calendar Start (1783) | Off (62) | UINT | R | 1 | No
179 | 1 | 143 | Profile | Base |  | Monitor the number of steps for profile loaded in memory. | 0 to 50 | 0 | UINT | R | 1 | No
179 | 1 | 144 | Profile | Base | Event 5 | Monitor/change current step Event Output 5 transmitter (EVT5) loaded in memory. | Off (62), On (63) | Off (62) | UINT | R/W | 1 | Yes
179 | 1 | 145 | Profile | Base | Event 6 | Monitor/change current step Event Output 6 transmitter (EVT6) loaded in memory. | Off (62), On (63) | Off (62) | UINT | R/W | 1 | Yes
179 | 1 | 146 | Profile | Base | Event 7 | Monitor/change current step Event Output 7 transmitter (EVT7) loaded in memory. | Off (62), On (63) | Off (62) | UINT | R/W | 1 | Yes
179 | 1 | 147 | Profile | Base | Event 8 | Monitor/change current step Event Output 8 transmitter (EVT8) loaded in memory. | Off (62), On (63) | Off (62) | UINT | R/W | 1 | Yes
179 | 1 | 148 | Profile | Base | Name |  | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 1 | No
179 | 1 | 149 | Profile | Base | Name |  | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 1 | No
179 | 1 | 150 | Profile | Base | Name |  | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 1 | No
179 | 1 | 151 | Profile | Base | Name |  | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 1 | No
179 | 1 | 152 | Profile | Base | Error | Monitor error status for produced Event Output 5 transmitter (EVT5). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 1 | No
179 | 1 | 153 | Profile | Base | Error | Monitor error status for produced Event Output 6 transmitter (EVT6). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 1 | No
179 | 1 | 154 | Profile | Base | Error | Monitor error status for produced Event Output 7 transmitter (EVT7). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 1 | No
179 | 1 | 155 | Profile | Base | Error | Monitor error status for produced Event Output 8 transmitter (EVT8). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 1 | No
191 | 1 | 1 | Message | Base | Message Enable | Set to enable message. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | No
191 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 4 | No
191 | 1 | 3 | Message | Base | Change |  | 0 to 4,294,967,295 | 0 | UDINT | R | 4 | No
191 | 2 | 1 | Message | Base | Message Enable | Set to enable message. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | No
191 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 4 | No
191 | 2 | 3 | Message | Base | Change |  | 0 to 4,294,967,295 | 0 | UDINT | R | 4 | No
191 | 3 | 1 | Message | Base | Message Enable | Set to enable message. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | No
191 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 4 | No
191 | 3 | 3 | Message | Base | Change |  | 0 to 4,294,967,295 | 0 | UDINT | R | 4 | No
191 | 4 | 1 | Message | Base | Message Enable | Set to enable message. | No (59), Yes (106) | No (59) | UINT | R/W | 4 | No
191 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 4 | No
191 | 4 | 3 | Message | Base | Change |  | 0 to 4,294,967,295 | 0 | UDINT | R | 4 | No

## LabVIEW
Parameter ID | Instance | Class Name | Module | Parameter Name | Description | Range/Enumerations | Default Value | Data Type | Access | Max Instances
1001 | 1 | Device | Base | Hardware ID | Monitor the hardware ID. | 0 to 65,535 | 124 | Signed 32-bit | R | 7
1002 | 1 | Device | Base | Software ID | Monitor the software ID. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1003 | 1 | Device | Base | Software Release Version | Monitor the software release version. For example, if the About screen is showing 04:06:0008, 4 will be returned. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1004 | 1 | Device | Base | Software Prototype Version | Monitor the prototype version if prototype. For example, if the About screen is showing 04:06:0008, 6 will be returned. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1005 | 1 | Device | Base | Software Build Number | Monitor the software build number. For example, if the About screen is showing 04:06:0008, 8 will be returned. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1006 | 1 | Device | Base | Firmware Branch Number | Monitor the firmware branch number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1007 | 1 | Device | Base | Serial Number | Monitor the serial number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1008 | 1 | Device | Base | Date of Manufacture | Monitor the date the hardware was manufactured. Serial number in format YYDDD | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1009 | 1 | Device | Base | Part Number | Monitor the model number of the base. | 15 bytes (UTF-8) | F4T1A1A1A1A5000 | String | R | 7
1011 | 1 | Device | Base | Device Name | Set the name to assign the base. | 32 bytes (UTF-8) | F4T | String | R/W | 7
1013 | 1 | Device | Base | Restore Settings From | Set to restore factory settings. | None (61), Factory (31) | None (61) | Enumeration | R/W | 7
1016 | 1 | Device | Base | Device Status | Monitor the base for failure. | OK (138), Fail (32) |  | Enumeration | R | 7
1034 | 1 | Device | Base | AC Line Frequency | Set the frequency used for variable time base control. | 50 Hz (3), 60 Hz (4) | 60 Hz (4) | Enumeration | R/W | 7
1001 | 2 | Device | 1 | Hardware ID | Monitor the hardware card ID populated in slot 1. | 0 to 65,535 |  | Signed 32-bit | R | 7
1002 | 2 | Device | 1 | Software ID | Monitor the hardware ID. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1003 | 2 | Device | 1 | Software Release Version | Monitor the software release version. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1004 | 2 | Device | 1 | Software Prototype Version | Monitor the prototype version if prototype. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1005 | 2 | Device | 1 | Software Build Number | Monitor the software build number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1006 | 2 | Device | 1 | Firmware Branch Number | Monitor the firmware branch number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1007 | 2 | Device | 1 | Serial Number | Monitor the serial number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1008 | 2 | Device | 1 | Date of Manufacture | Monitor the date the hardware was manufactured. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1009 | 2 | Device | 1 | Part Number | Monitor the model number of the card. | 15 bytes (UTF-8) | F4T1A1A1A1A5000 | String | R | 7
1011 | 2 | Device | 1 | Device Name | Set the name to assign the card. | 32 bytes (UTF-8) | F4T | String | R/W | 7
1013 | 2 | Device | 1 | Restore Settings From | Set to restore factory settings. | None (61), Factory (31) | None (61) | Enumeration | R/W | 7
1016 | 2 | Device | 1 | Device Status | Monitor the base for failure. | OK (138), Fail (32) |  | Enumeration | R | 7
1034 | 2 | Device | 1 | AC Line Frequency | Set the frequency used for variable time base control. | 50 Hz (3), 60 Hz (4) | 60 Hz (4) | Enumeration | R/W | 7
1001 | 3 | Device | 2 | Hardware ID | Monitor the hardware card ID populated in slot 2. | 0 to 65,535 |  | Signed 32-bit | R | 7
1002 | 3 | Device | 2 | Software ID | Monitor the hardware ID. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1003 | 3 | Device | 2 | Software Release Version | Monitor the software release version. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1004 | 3 | Device | 2 | Software Prototype Version | Monitor the prototype version if prototype. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1005 | 3 | Device | 2 | Software Build Number | Monitor the software build number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1006 | 3 | Device | 2 | Firmware Branch Number | Monitor the firmware branch number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1007 | 3 | Device | 2 | Serial Number | Monitor the serial number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1008 | 3 | Device | 2 | Date of Manufacture | Monitor the date the hardware was manufactured. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1009 | 3 | Device | 2 | Part Number | Monitor the model number of the card. | 15 bytes (UTF-8) | F4T1A1A1A1A5000 | String | R | 7
1011 | 3 | Device | 2 | Device Name | Set the name to assign the card. | 32 bytes (UTF-8) | F4T | String | R/W | 7
1013 | 3 | Device | 2 | Restore Settings From | Set to restore factory settings. | None (61), Factory (31) | None (61) | Enumeration | R/W | 7
1016 | 3 | Device | 2 | Device Status | Monitor the base for failure. | OK (138), Fail (32) |  | Enumeration | R | 7
1034 | 3 | Device | 2 | AC Line Frequency | Set the frequency used for variable time base control. | 50 Hz (3), 60 Hz (4) | 60 Hz (4) | Enumeration | R/W | 7
1001 | 4 | Device | 3 | Hardware ID | Monitor the hardware card ID populated in slot 3. | 0 to 65,535 |  | Signed 32-bit | R | 7
1002 | 4 | Device | 3 | Software ID | Monitor the hardware ID. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1003 | 4 | Device | 3 | Software Release Version | Monitor the software release version. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1004 | 4 | Device | 3 | Software Prototype Version | Monitor the prototype version if prototype. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1005 | 4 | Device | 3 | Software Build Number | Monitor the software build number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1006 | 4 | Device | 3 | Firmware Branch Number | Monitor the firmware branch number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1007 | 4 | Device | 3 | Serial Number | Monitor the serial number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1008 | 4 | Device | 3 | Date of Manufacture | Monitor the date the hardware was manufactured. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1009 | 4 | Device | 3 | Part Number | Monitor the model number of the card. | 15 bytes (UTF-8) | F4T1A1A1A1A5000 | String | R | 7
1011 | 4 | Device | 3 | Device Name | Set the name to assign the card. | 32 bytes (UTF-8) | F4T | String | R/W | 7
1013 | 4 | Device | 3 | Restore Settings From | Set to restore factory settings. | None (61), Factory (31) | None (61) | Enumeration | R/W | 7
1016 | 4 | Device | 3 | Device Status | Monitor the base for failure. | OK (138), Fail (32) |  | Enumeration | R | 7
1034 | 4 | Device | 3 | AC Line Frequency | Set the frequency used for variable time base control. | 50 Hz (3), 60 Hz (4) | 60 Hz (4) | Enumeration | R/W | 7
1001 | 5 | Device | 4 | Hardware ID | Monitor the hardware card ID populated in slot 4. | 0 to 65,535 |  | Signed 32-bit | R | 7
1002 | 5 | Device | 4 | Software ID | Monitor the hardware ID. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1003 | 5 | Device | 4 | Software Release Version | Monitor the software release version. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1004 | 5 | Device | 4 | Software Prototype Version | Monitor the prototype version if prototype. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1005 | 5 | Device | 4 | Software Build Number | Monitor the software build number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1006 | 5 | Device | 4 | Firmware Branch Number | Monitor the firmware branch number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1007 | 5 | Device | 4 | Serial Number | Monitor the serial number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1008 | 5 | Device | 4 | Date of Manufacture | Monitor the date the hardware was manufactured. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1009 | 5 | Device | 4 | Part Number | Monitor the model number of the card. | 15 bytes (UTF-8) | F4T1A1A1A1A5000 | String | R | 7
1011 | 5 | Device | 4 | Device Name | Set the name to assign the card. | 32 bytes (UTF-8) | F4T | String | R/W | 7
1013 | 5 | Device | 4 | Restore Settings From | Set to restore factory settings. | None (61), Factory (31) | None (61) | Enumeration | R/W | 7
1016 | 5 | Device | 4 | Device Status | Monitor the base for failure. | OK (138), Fail (32) |  | Enumeration | R | 7
1034 | 5 | Device | 4 | AC Line Frequency | Set the frequency used for variable time base control. | 50 Hz (3), 60 Hz (4) | 60 Hz (4) | Enumeration | R/W | 7
1001 | 6 | Device | 5 | Hardware ID | Monitor the hardware card ID populated in slot 5. | 0 to 65,535 |  | Signed 32-bit | R | 7
1002 | 6 | Device | 5 | Software ID | Monitor the hardware ID. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1003 | 6 | Device | 5 | Software Release Version | Monitor the software release version. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1004 | 6 | Device | 5 | Software Prototype Version | Monitor the prototype version if prototype. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1005 | 6 | Device | 5 | Software Build Number | Monitor the software build number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1006 | 6 | Device | 5 | Firmware Branch Number | Monitor the firmware branch number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1007 | 6 | Device | 5 | Serial Number | Monitor the serial number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1008 | 6 | Device | 5 | Date of Manufacture | Monitor the date the hardware was manufactured. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1009 | 6 | Device | 5 | Part Number | Monitor the model number of the card. | 15 bytes (UTF-8) | F4T1A1A1A1A5000 | String | R | 7
1011 | 6 | Device | 5 | Device Name | Set the name to assign the card. | 32 bytes (UTF-8) | F4T | String | R/W | 7
1013 | 6 | Device | 5 | Restore Settings From | Set to restore factory settings. | None (61), Factory (31) | None (61) | Enumeration | R/W | 7
1016 | 6 | Device | 5 | Device Status | Monitor the base for failure. | OK (138), Fail (32) |  | Enumeration | R | 7
1034 | 6 | Device | 5 | AC Line Frequency | Set the frequency used for variable time base control. | 50 Hz (3), 60 Hz (4) | 60 Hz (4) | Enumeration | R/W | 7
1001 | 7 | Device | 6 | Hardware ID | Monitor the hardware card ID populated in slot 6. | 0 to 65,535 |  | Signed 32-bit | R | 7
1002 | 7 | Device | 6 | Software ID | Monitor the hardware ID. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1003 | 7 | Device | 6 | Software Release Version | Monitor the software release version. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1004 | 7 | Device | 6 | Software Prototype Version | Monitor the prototype version if prototype. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1005 | 7 | Device | 6 | Software Build Number | Monitor the software build number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1006 | 7 | Device | 6 | Firmware Branch Number | Monitor the firmware branch number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1007 | 7 | Device | 6 | Serial Number | Monitor the serial number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1008 | 7 | Device | 6 | Date of Manufacture | Monitor the date the hardware was manufactured. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 7
1009 | 7 | Device | 6 | Part Number | Monitor the model number of the card. | 15 bytes (UTF-8) | F4T1A1A1A1A5000 | String | R | 7
1011 | 7 | Device | 6 | Device Name | Set the name to assign the card. | 32 bytes (UTF-8) | F4T | String | R/W | 7
1013 | 7 | Device | 6 | Restore Settings From | Set to restore factory settings. | None (61), Factory (31) | None (61) | Enumeration | R/W | 7
1016 | 7 | Device | 6 | Device Status | Monitor the base for failure. | OK (138), Fail (32) |  | Enumeration | R | 7
1034 | 7 | Device | 6 | AC Line Frequency | Set the frequency used for variable time base control. | 50 Hz (3), 60 Hz (4) | 60 Hz (4) | Enumeration | R/W | 7
2001 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 1 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 1 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 1 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 1 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 1 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 2 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 2 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 2 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 2 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 2 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 3 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 3 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 3 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 3 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 3 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 4 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 4 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 4 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 4 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 4 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 5 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 5 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 5 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 5 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 5 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 5 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 6 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 6 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 6 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 6 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 6 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 6 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 7 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 7 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 7 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 7 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 7 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 8 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 8 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 8 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 8 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 8 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 8 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 9 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 9 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 9 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 9 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 9 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 9 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 10 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 10 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 10 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 10 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 10 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 11 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 11 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 11 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 11 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 11 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 11 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 12 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 12 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 12 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 12 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 12 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 12 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 13 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 13 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 13 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 13 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 13 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 13 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 14 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 14 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 14 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 14 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 14 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 14 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 15 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 15 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 15 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 15 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 15 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 15 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 16 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 16 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 16 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 16 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 16 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 16 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 17 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 17 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 17 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 17 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 17 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 17 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 18 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 18 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 18 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 18 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 18 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 18 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 19 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 19 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 19 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 19 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 19 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 19 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 20 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 20 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 20 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 20 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 20 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 20 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 21 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 21 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 21 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 21 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 21 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 21 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 22 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 22 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 22 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 22 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 22 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 22 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 23 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 23 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 23 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 23 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 23 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 23 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
2001 | 24 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 24
2002 | 24 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 24
2003 | 24 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
2004 | 24 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 24
2007 | 24 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 24
2010 | 24 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 24
3005 | 1 | Display | Base | Display Units | Set display units for touchscreen. | F (30), C (15) | F (30) | Enumeration | R/W | 1
12002 | 1 | Limit | 1 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | IEEE Float | R/W | 60
12003 | 1 | Limit | 1 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 60
12004 | 1 | Limit | 1 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 60
12005 | 1 | Limit | 1 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 60
12006 | 1 | Limit | 1 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | Enumeration | R | 60
12007 | 1 | Limit | 1 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | Enumeration | R | 60
12009 | 1 | Limit | 1 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 60
12010 | 1 | Limit | 1 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 60
12013 | 1 | Limit | 1 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | Enumeration | R | 60
12014 | 1 | Limit | 1 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
12015 | 1 | Limit | 1 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | Enumeration | R/W | 60
12016 | 1 | Limit | 1 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
12017 | 1 | Limit | 1 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
12018 | 1 | Limit | 1 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | Enumeration | R | 60
12019 | 1 | Limit | 1 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | Enumeration | R/W | 60
12020 | 1 | Limit | 1 | Source Instance B | Set the source Instance for the Limit sensor. | 1 to 1 | 1 | Unsigned 8-bit | R/W | 60
12021 | 1 | Limit | 1 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
12022 | 1 | Limit | 1 | Source Value B | Monitor the IN receiver source value. |  |  | IEEE Float | R | 60
12025 | 1 | Limit | 1 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
12026 | 1 | Limit | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
12002 | 11 | Limit | 2 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | IEEE Float | R/W | 60
12003 | 11 | Limit | 2 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 60
12004 | 11 | Limit | 2 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 60
12005 | 11 | Limit | 2 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 60
12006 | 11 | Limit | 2 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | Enumeration | R | 60
12007 | 11 | Limit | 2 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | Enumeration | R | 60
12009 | 11 | Limit | 2 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 60
12010 | 11 | Limit | 2 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 60
12013 | 11 | Limit | 2 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | Enumeration | R | 60
12014 | 11 | Limit | 2 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
12015 | 11 | Limit | 2 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | Enumeration | R/W | 60
12016 | 11 | Limit | 2 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
12017 | 11 | Limit | 2 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
12018 | 11 | Limit | 2 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | Enumeration | R | 60
12019 | 11 | Limit | 2 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | Enumeration | R/W | 60
12020 | 11 | Limit | 2 | Source Instance B | Set the source Instance for the Limit sensor. | 11 to 11 | 11 | Unsigned 8-bit | R/W | 60
12021 | 11 | Limit | 2 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
12022 | 11 | Limit | 2 | Source Value B | Monitor the IN receiver source value. |  |  | IEEE Float | R | 60
12025 | 11 | Limit | 2 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
12026 | 11 | Limit | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
12002 | 21 | Limit | 3 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | IEEE Float | R/W | 60
12003 | 21 | Limit | 3 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 60
12004 | 21 | Limit | 3 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 60
12005 | 21 | Limit | 3 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 60
12006 | 21 | Limit | 3 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | Enumeration | R | 60
12007 | 21 | Limit | 3 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | Enumeration | R | 60
12009 | 21 | Limit | 3 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 60
12010 | 21 | Limit | 3 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 60
12013 | 21 | Limit | 3 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | Enumeration | R | 60
12014 | 21 | Limit | 3 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
12015 | 21 | Limit | 3 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | Enumeration | R/W | 60
12016 | 21 | Limit | 3 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
12017 | 21 | Limit | 3 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
12018 | 21 | Limit | 3 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | Enumeration | R | 60
12019 | 21 | Limit | 3 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | Enumeration | R/W | 60
12020 | 21 | Limit | 3 | Source Instance B | Set the source Instance for the Limit sensor. | 21 to 21 | 21 | Unsigned 8-bit | R/W | 60
12021 | 21 | Limit | 3 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
12022 | 21 | Limit | 3 | Source Value B | Monitor the IN receiver source value. |  |  | IEEE Float | R | 60
12025 | 21 | Limit | 3 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
12026 | 21 | Limit | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
12002 | 31 | Limit | 4 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | IEEE Float | R/W | 60
12003 | 31 | Limit | 4 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 60
12004 | 31 | Limit | 4 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 60
12005 | 31 | Limit | 4 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 60
12006 | 31 | Limit | 4 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | Enumeration | R | 60
12007 | 31 | Limit | 4 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | Enumeration | R | 60
12009 | 31 | Limit | 4 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 60
12010 | 31 | Limit | 4 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 60
12013 | 31 | Limit | 4 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | Enumeration | R | 60
12014 | 31 | Limit | 4 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
12015 | 31 | Limit | 4 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | Enumeration | R/W | 60
12016 | 31 | Limit | 4 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
12017 | 31 | Limit | 4 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
12018 | 31 | Limit | 4 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | Enumeration | R | 60
12019 | 31 | Limit | 4 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | Enumeration | R/W | 60
12020 | 31 | Limit | 4 | Source Instance B | Set the source Instance for the Limit sensor. | 31 to 31 | 31 | Unsigned 8-bit | R/W | 60
12021 | 31 | Limit | 4 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
12022 | 31 | Limit | 4 | Source Value B | Monitor the IN receiver source value. |  |  | IEEE Float | R | 60
12025 | 31 | Limit | 4 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
12026 | 31 | Limit | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
12002 | 41 | Limit | 5 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | IEEE Float | R/W | 60
12003 | 41 | Limit | 5 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 60
12004 | 41 | Limit | 5 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 60
12005 | 41 | Limit | 5 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 60
12006 | 41 | Limit | 5 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | Enumeration | R | 60
12007 | 41 | Limit | 5 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | Enumeration | R | 60
12009 | 41 | Limit | 5 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 60
12010 | 41 | Limit | 5 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 60
12013 | 41 | Limit | 5 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | Enumeration | R | 60
12014 | 41 | Limit | 5 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
12015 | 41 | Limit | 5 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | Enumeration | R/W | 60
12016 | 41 | Limit | 5 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
12017 | 41 | Limit | 5 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
12018 | 41 | Limit | 5 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | Enumeration | R | 60
12019 | 41 | Limit | 5 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | Enumeration | R/W | 60
12020 | 41 | Limit | 5 | Source Instance B | Set the source Instance for the Limit sensor. | 41 to 41 | 41 | Unsigned 8-bit | R/W | 60
12021 | 41 | Limit | 5 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
12022 | 41 | Limit | 5 | Source Value B | Monitor the IN receiver source value. |  |  | IEEE Float | R | 60
12025 | 41 | Limit | 5 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
12026 | 41 | Limit | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
12002 | 51 | Limit | 6 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | IEEE Float | R/W | 60
12003 | 51 | Limit | 6 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 60
12004 | 51 | Limit | 6 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 60
12005 | 51 | Limit | 6 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 60
12006 | 51 | Limit | 6 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | Enumeration | R | 60
12007 | 51 | Limit | 6 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | Enumeration | R | 60
12009 | 51 | Limit | 6 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 60
12010 | 51 | Limit | 6 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 60
12013 | 51 | Limit | 6 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | Enumeration | R | 60
12014 | 51 | Limit | 6 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
12015 | 51 | Limit | 6 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | Enumeration | R/W | 60
12016 | 51 | Limit | 6 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
12017 | 51 | Limit | 6 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
12018 | 51 | Limit | 6 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | Enumeration | R | 60
12019 | 51 | Limit | 6 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | Enumeration | R/W | 60
12020 | 51 | Limit | 6 | Source Instance B | Set the source Instance for the Limit sensor. | 51 to 51 | 51 | Unsigned 8-bit | R/W | 60
12021 | 51 | Limit | 6 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
12022 | 51 | Limit | 6 | Source Value B | Monitor the IN receiver source value. |  |  | IEEE Float | R | 60
12025 | 51 | Limit | 6 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
12026 | 51 | Limit | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
15001 | 1 | Current | 1 | Current Read | Monitor current of S&H transmitter. |  |  | IEEE Float | R | 60
15002 | 1 | Current | 1 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | Enumeration | R | 60
15003 | 1 | Current | 1 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | Enumeration | R | 60
15004 | 1 | Current | 1 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | Enumeration | R/W | 60
15005 | 1 | Current | 1 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | Enumeration | R/W | 60
15007 | 1 | Current | 1 | Load Current RMS | Monitor current of CUR transmitter. |  |  | IEEE Float | R | 60
15008 | 1 | Current | 1 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | IEEE Float | R/W | 60
15009 | 1 | Current | 1 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
15010 | 1 | Current | 1 | Current Gain | Monitor the Gain setting. |  | 0.17 | IEEE Float | R | 60
15011 | 1 | Current | 1 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
15012 | 1 | Current | 1 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | Unsigned 16-bit | R/W | 60
15019 | 1 | Current | 1 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
15020 | 1 | Current | 1 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | IEEE Float | R | 60
15021 | 1 | Current | 1 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | Enumeration | R | 60
15022 | 1 | Current | 1 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | IEEE Float | R/W | 60
15037 | 1 | Current | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
15001 | 11 | Current | 2 | Current Read | Monitor current of S&H transmitter. |  |  | IEEE Float | R | 60
15002 | 11 | Current | 2 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | Enumeration | R | 60
15003 | 11 | Current | 2 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | Enumeration | R | 60
15004 | 11 | Current | 2 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | Enumeration | R/W | 60
15005 | 11 | Current | 2 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | Enumeration | R/W | 60
15007 | 11 | Current | 2 | Load Current RMS | Monitor current of CUR transmitter. |  |  | IEEE Float | R | 60
15008 | 11 | Current | 2 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | IEEE Float | R/W | 60
15009 | 11 | Current | 2 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
15010 | 11 | Current | 2 | Current Gain | Monitor the Gain setting. |  | 0.17 | IEEE Float | R | 60
15011 | 11 | Current | 2 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
15012 | 11 | Current | 2 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | Unsigned 16-bit | R/W | 60
15019 | 11 | Current | 2 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
15020 | 11 | Current | 2 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | IEEE Float | R | 60
15021 | 11 | Current | 2 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | Enumeration | R | 60
15022 | 11 | Current | 2 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | IEEE Float | R/W | 60
15037 | 11 | Current | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
15001 | 21 | Current | 3 | Current Read | Monitor current of S&H transmitter. |  |  | IEEE Float | R | 60
15002 | 21 | Current | 3 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | Enumeration | R | 60
15003 | 21 | Current | 3 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | Enumeration | R | 60
15004 | 21 | Current | 3 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | Enumeration | R/W | 60
15005 | 21 | Current | 3 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | Enumeration | R/W | 60
15007 | 21 | Current | 3 | Load Current RMS | Monitor current of CUR transmitter. |  |  | IEEE Float | R | 60
15008 | 21 | Current | 3 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | IEEE Float | R/W | 60
15009 | 21 | Current | 3 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
15010 | 21 | Current | 3 | Current Gain | Monitor the Gain setting. |  | 0.17 | IEEE Float | R | 60
15011 | 21 | Current | 3 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
15012 | 21 | Current | 3 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | Unsigned 16-bit | R/W | 60
15019 | 21 | Current | 3 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
15020 | 21 | Current | 3 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | IEEE Float | R | 60
15021 | 21 | Current | 3 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | Enumeration | R | 60
15022 | 21 | Current | 3 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | IEEE Float | R/W | 60
15037 | 21 | Current | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
15001 | 31 | Current | 4 | Current Read | Monitor current of S&H transmitter. |  |  | IEEE Float | R | 60
15002 | 31 | Current | 4 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | Enumeration | R | 60
15003 | 31 | Current | 4 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | Enumeration | R | 60
15004 | 31 | Current | 4 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | Enumeration | R/W | 60
15005 | 31 | Current | 4 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | Enumeration | R/W | 60
15007 | 31 | Current | 4 | Load Current RMS | Monitor current of CUR transmitter. |  |  | IEEE Float | R | 60
15008 | 31 | Current | 4 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | IEEE Float | R/W | 60
15009 | 31 | Current | 4 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
15010 | 31 | Current | 4 | Current Gain | Monitor the Gain setting. |  | 0.17 | IEEE Float | R | 60
15011 | 31 | Current | 4 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
15012 | 31 | Current | 4 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | Unsigned 16-bit | R/W | 60
15019 | 31 | Current | 4 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
15020 | 31 | Current | 4 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | IEEE Float | R | 60
15021 | 31 | Current | 4 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | Enumeration | R | 60
15022 | 31 | Current | 4 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | IEEE Float | R/W | 60
15037 | 31 | Current | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
15001 | 41 | Current | 5 | Current Read | Monitor current of S&H transmitter. |  |  | IEEE Float | R | 60
15002 | 41 | Current | 5 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | Enumeration | R | 60
15003 | 41 | Current | 5 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | Enumeration | R | 60
15004 | 41 | Current | 5 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | Enumeration | R/W | 60
15005 | 41 | Current | 5 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | Enumeration | R/W | 60
15007 | 41 | Current | 5 | Load Current RMS | Monitor current of CUR transmitter. |  |  | IEEE Float | R | 60
15008 | 41 | Current | 5 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | IEEE Float | R/W | 60
15009 | 41 | Current | 5 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
15010 | 41 | Current | 5 | Current Gain | Monitor the Gain setting. |  | 0.17 | IEEE Float | R | 60
15011 | 41 | Current | 5 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
15012 | 41 | Current | 5 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | Unsigned 16-bit | R/W | 60
15019 | 41 | Current | 5 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
15020 | 41 | Current | 5 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | IEEE Float | R | 60
15021 | 41 | Current | 5 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | Enumeration | R | 60
15022 | 41 | Current | 5 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | IEEE Float | R/W | 60
15037 | 41 | Current | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
15001 | 51 | Current | 6 | Current Read | Monitor current of S&H transmitter. |  |  | IEEE Float | R | 60
15002 | 51 | Current | 6 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | Enumeration | R | 60
15003 | 51 | Current | 6 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | Enumeration | R | 60
15004 | 51 | Current | 6 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | Enumeration | R/W | 60
15005 | 51 | Current | 6 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | Enumeration | R/W | 60
15007 | 51 | Current | 6 | Load Current RMS | Monitor current of CUR transmitter. |  |  | IEEE Float | R | 60
15008 | 51 | Current | 6 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | IEEE Float | R/W | 60
15009 | 51 | Current | 6 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
15010 | 51 | Current | 6 | Current Gain | Monitor the Gain setting. |  | 0.17 | IEEE Float | R | 60
15011 | 51 | Current | 6 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
15012 | 51 | Current | 6 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | Unsigned 16-bit | R/W | 60
15019 | 51 | Current | 6 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
15020 | 51 | Current | 6 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | IEEE Float | R | 60
15021 | 51 | Current | 6 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | Enumeration | R | 60
15022 | 51 | Current | 6 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | IEEE Float | R/W | 60
15037 | 51 | Current | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18001 | 1 | Analog Output | 1 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 1 | Analog Output | 1 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 1 | Analog Output | 1 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 1 | Analog Output | 1 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 1 | Analog Output | 1 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 1 | Analog Output | 1 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 1 | Analog Output | 1 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 1 | Analog Output | 1 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 1 | Analog Output | 1 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 1 | Analog Output | 1 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 1 | Analog Output | 1 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 1 | Analog Output | 1 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 1 | Analog Output | 1 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 1 | Analog Output | 1 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 1 | Analog Output | 1 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 1 | Analog Output | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 1 | Analog Output | 1 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 2 | Analog Output | 1 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 2 | Analog Output | 1 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 2 | Analog Output | 1 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 2 | Analog Output | 1 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 2 | Analog Output | 1 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 2 | Analog Output | 1 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 2 | Analog Output | 1 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 2 | Analog Output | 1 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 2 | Analog Output | 1 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 2 | Analog Output | 1 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 2 | Analog Output | 1 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 2 | Analog Output | 1 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 2 | Analog Output | 1 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 2 | Analog Output | 1 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 2 | Analog Output | 1 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 2 | Analog Output | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 2 | Analog Output | 1 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 3 | Analog Output | 1 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 3 | Analog Output | 1 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 3 | Analog Output | 1 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 3 | Analog Output | 1 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 3 | Analog Output | 1 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 3 | Analog Output | 1 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 3 | Analog Output | 1 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 3 | Analog Output | 1 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 3 | Analog Output | 1 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 3 | Analog Output | 1 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 3 | Analog Output | 1 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 3 | Analog Output | 1 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 3 | Analog Output | 1 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 3 | Analog Output | 1 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 3 | Analog Output | 1 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 3 | Analog Output | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 3 | Analog Output | 1 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 11 | Analog Output | 2 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 11 | Analog Output | 2 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 11 | Analog Output | 2 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 11 | Analog Output | 2 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 11 | Analog Output | 2 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 11 | Analog Output | 2 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 11 | Analog Output | 2 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 11 | Analog Output | 2 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 11 | Analog Output | 2 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 11 | Analog Output | 2 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 11 | Analog Output | 2 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 11 | Analog Output | 2 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 11 | Analog Output | 2 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 11 | Analog Output | 2 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 11 | Analog Output | 2 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 11 | Analog Output | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 11 | Analog Output | 2 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 12 | Analog Output | 2 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 12 | Analog Output | 2 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 12 | Analog Output | 2 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 12 | Analog Output | 2 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 12 | Analog Output | 2 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 12 | Analog Output | 2 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 12 | Analog Output | 2 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 12 | Analog Output | 2 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 12 | Analog Output | 2 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 12 | Analog Output | 2 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 12 | Analog Output | 2 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 12 | Analog Output | 2 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 12 | Analog Output | 2 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 12 | Analog Output | 2 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 12 | Analog Output | 2 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 12 | Analog Output | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 12 | Analog Output | 2 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 13 | Analog Output | 2 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 13 | Analog Output | 2 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 13 | Analog Output | 2 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 13 | Analog Output | 2 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 13 | Analog Output | 2 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 13 | Analog Output | 2 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 13 | Analog Output | 2 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 13 | Analog Output | 2 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 13 | Analog Output | 2 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 13 | Analog Output | 2 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 13 | Analog Output | 2 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 13 | Analog Output | 2 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 13 | Analog Output | 2 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 13 | Analog Output | 2 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 13 | Analog Output | 2 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 13 | Analog Output | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 13 | Analog Output | 2 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 21 | Analog Output | 3 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 21 | Analog Output | 3 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 21 | Analog Output | 3 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 21 | Analog Output | 3 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 21 | Analog Output | 3 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 21 | Analog Output | 3 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 21 | Analog Output | 3 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 21 | Analog Output | 3 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 21 | Analog Output | 3 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 21 | Analog Output | 3 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 21 | Analog Output | 3 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 21 | Analog Output | 3 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 21 | Analog Output | 3 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 21 | Analog Output | 3 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 21 | Analog Output | 3 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 21 | Analog Output | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 21 | Analog Output | 3 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 22 | Analog Output | 3 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 22 | Analog Output | 3 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 22 | Analog Output | 3 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 22 | Analog Output | 3 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 22 | Analog Output | 3 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 22 | Analog Output | 3 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 22 | Analog Output | 3 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 22 | Analog Output | 3 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 22 | Analog Output | 3 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 22 | Analog Output | 3 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 22 | Analog Output | 3 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 22 | Analog Output | 3 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 22 | Analog Output | 3 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 22 | Analog Output | 3 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 22 | Analog Output | 3 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 22 | Analog Output | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 22 | Analog Output | 3 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 23 | Analog Output | 3 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 23 | Analog Output | 3 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 23 | Analog Output | 3 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 23 | Analog Output | 3 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 23 | Analog Output | 3 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 23 | Analog Output | 3 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 23 | Analog Output | 3 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 23 | Analog Output | 3 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 23 | Analog Output | 3 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 23 | Analog Output | 3 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 23 | Analog Output | 3 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 23 | Analog Output | 3 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 23 | Analog Output | 3 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 23 | Analog Output | 3 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 23 | Analog Output | 3 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 23 | Analog Output | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 23 | Analog Output | 3 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 31 | Analog Output | 4 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 31 | Analog Output | 4 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 31 | Analog Output | 4 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 31 | Analog Output | 4 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 31 | Analog Output | 4 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 31 | Analog Output | 4 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 31 | Analog Output | 4 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 31 | Analog Output | 4 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 31 | Analog Output | 4 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 31 | Analog Output | 4 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 31 | Analog Output | 4 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 31 | Analog Output | 4 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 31 | Analog Output | 4 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 31 | Analog Output | 4 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 31 | Analog Output | 4 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 31 | Analog Output | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 31 | Analog Output | 4 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 32 | Analog Output | 4 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 32 | Analog Output | 4 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 32 | Analog Output | 4 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 32 | Analog Output | 4 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 32 | Analog Output | 4 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 32 | Analog Output | 4 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 32 | Analog Output | 4 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 32 | Analog Output | 4 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 32 | Analog Output | 4 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 32 | Analog Output | 4 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 32 | Analog Output | 4 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 32 | Analog Output | 4 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 32 | Analog Output | 4 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 32 | Analog Output | 4 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 32 | Analog Output | 4 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 32 | Analog Output | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 32 | Analog Output | 4 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 33 | Analog Output | 4 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 33 | Analog Output | 4 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 33 | Analog Output | 4 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 33 | Analog Output | 4 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 33 | Analog Output | 4 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 33 | Analog Output | 4 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 33 | Analog Output | 4 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 33 | Analog Output | 4 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 33 | Analog Output | 4 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 33 | Analog Output | 4 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 33 | Analog Output | 4 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 33 | Analog Output | 4 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 33 | Analog Output | 4 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 33 | Analog Output | 4 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 33 | Analog Output | 4 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 33 | Analog Output | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 33 | Analog Output | 4 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 41 | Analog Output | 5 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 41 | Analog Output | 5 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 41 | Analog Output | 5 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 41 | Analog Output | 5 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 41 | Analog Output | 5 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 41 | Analog Output | 5 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 41 | Analog Output | 5 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 41 | Analog Output | 5 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 41 | Analog Output | 5 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 41 | Analog Output | 5 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 41 | Analog Output | 5 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 41 | Analog Output | 5 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 41 | Analog Output | 5 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 41 | Analog Output | 5 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 41 | Analog Output | 5 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 41 | Analog Output | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 41 | Analog Output | 5 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 42 | Analog Output | 5 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 42 | Analog Output | 5 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 42 | Analog Output | 5 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 42 | Analog Output | 5 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 42 | Analog Output | 5 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 42 | Analog Output | 5 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 42 | Analog Output | 5 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 42 | Analog Output | 5 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 42 | Analog Output | 5 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 42 | Analog Output | 5 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 42 | Analog Output | 5 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 42 | Analog Output | 5 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 42 | Analog Output | 5 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 42 | Analog Output | 5 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 42 | Analog Output | 5 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 42 | Analog Output | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 42 | Analog Output | 5 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 43 | Analog Output | 5 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 43 | Analog Output | 5 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 43 | Analog Output | 5 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 43 | Analog Output | 5 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 43 | Analog Output | 5 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 43 | Analog Output | 5 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 43 | Analog Output | 5 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 43 | Analog Output | 5 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 43 | Analog Output | 5 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 43 | Analog Output | 5 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 43 | Analog Output | 5 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 43 | Analog Output | 5 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 43 | Analog Output | 5 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 43 | Analog Output | 5 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 43 | Analog Output | 5 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 43 | Analog Output | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 43 | Analog Output | 5 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 51 | Analog Output | 6 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 51 | Analog Output | 6 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 51 | Analog Output | 6 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 51 | Analog Output | 6 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 51 | Analog Output | 6 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 51 | Analog Output | 6 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 51 | Analog Output | 6 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 51 | Analog Output | 6 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 51 | Analog Output | 6 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 51 | Analog Output | 6 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 51 | Analog Output | 6 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 51 | Analog Output | 6 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 51 | Analog Output | 6 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 51 | Analog Output | 6 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 51 | Analog Output | 6 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 51 | Analog Output | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 51 | Analog Output | 6 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 52 | Analog Output | 6 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 52 | Analog Output | 6 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 52 | Analog Output | 6 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 52 | Analog Output | 6 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 52 | Analog Output | 6 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 52 | Analog Output | 6 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 52 | Analog Output | 6 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 52 | Analog Output | 6 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 52 | Analog Output | 6 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 52 | Analog Output | 6 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 52 | Analog Output | 6 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 52 | Analog Output | 6 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 52 | Analog Output | 6 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 52 | Analog Output | 6 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 52 | Analog Output | 6 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 52 | Analog Output | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 52 | Analog Output | 6 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
18001 | 53 | Analog Output | 6 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 60
18002 | 53 | Analog Output | 6 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 60
18004 | 53 | Analog Output | 6 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
18005 | 53 | Analog Output | 6 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18006 | 53 | Analog Output | 6 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18007 | 53 | Analog Output | 6 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18008 | 53 | Analog Output | 6 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
18009 | 53 | Analog Output | 6 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
18010 | 53 | Analog Output | 6 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 60
18011 | 53 | Analog Output | 6 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
18012 | 53 | Analog Output | 6 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 60
18016 | 53 | Analog Output | 6 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 60
18017 | 53 | Analog Output | 6 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 60
18018 | 53 | Analog Output | 6 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 60
18019 | 53 | Analog Output | 6 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
18024 | 53 | Analog Output | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
18025 | 53 | Analog Output | 6 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 60
19001 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19002 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19003 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19004 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19005 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19006 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19007 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19008 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19009 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19010 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19011 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19012 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19013 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19014 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19015 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19016 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19017 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19018 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19019 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19020 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19021 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19022 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19023 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19024 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19025 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19026 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19027 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19028 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19029 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19030 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19031 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19032 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19033 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19034 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19035 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19036 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19037 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19038 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19039 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19040 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19041 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19042 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19043 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19044 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19045 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19046 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19047 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19048 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19049 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19050 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19051 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19052 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19053 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19054 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19055 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19056 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19057 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19058 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19059 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19060 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19001 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19002 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19003 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19004 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19005 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19006 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19007 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19008 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19009 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19010 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19011 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19012 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19013 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19014 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19015 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19016 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19017 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19018 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19019 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19020 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19021 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19022 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19023 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19024 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19025 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19026 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19027 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19028 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19029 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19030 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19031 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19032 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19033 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19034 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19035 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19036 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19037 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19038 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19039 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19040 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19041 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19042 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19043 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19044 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19045 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19046 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19047 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19048 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19049 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19050 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19051 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19052 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19053 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19054 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19055 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19056 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19057 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19058 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19059 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
19060 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 124
20001 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20002 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20003 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20004 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20005 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20006 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20007 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20008 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20009 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20010 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20011 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20012 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20013 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20014 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20015 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20016 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20017 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20018 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20019 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20020 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20021 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20022 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20023 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20024 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20025 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20026 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20027 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20028 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20029 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20030 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20031 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20032 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20033 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20034 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20035 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20036 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20037 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20038 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20039 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20040 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20041 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20042 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20043 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20044 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20045 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20046 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20047 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20048 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20049 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20050 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20051 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20052 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20053 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20054 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20055 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20056 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20057 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20058 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20059 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20060 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20001 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20002 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20003 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20004 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20005 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20006 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20007 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20008 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20009 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20010 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20011 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20012 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20013 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20014 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20015 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20016 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20017 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20018 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20019 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20020 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20021 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20022 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20023 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20024 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20025 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20026 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20027 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20028 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20029 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20030 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20031 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20032 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20033 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20034 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20035 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20036 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20037 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20038 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20039 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20040 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20041 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20042 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20043 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20044 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20045 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20046 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20047 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20048 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20049 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20050 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20051 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20052 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20053 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20054 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20055 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20056 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20057 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20058 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20059 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
20060 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 124
25001 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 1 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 1 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 1 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 1 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 1 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 1 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 1 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 1 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 1 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 1 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 1 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 1 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 1 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 1 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 1 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 1 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 1 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 1 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 1 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 1 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 1 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 1 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 1 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 1 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 1 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 1 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 1 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 1 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 1 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 1 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 1 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 2 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 2 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 2 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 2 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 2 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 2 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 2 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 2 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 2 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 2 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 2 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 2 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 2 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 2 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 2 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 2 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 2 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 2 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 2 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 2 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 2 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 2 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 2 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 2 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 2 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 2 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 2 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 2 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 2 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 2 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 2 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 3 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 3 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 3 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 3 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 3 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 3 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 3 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 3 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 3 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 3 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 3 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 3 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 3 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 3 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 3 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 3 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 3 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 3 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 3 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 3 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 3 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 3 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 3 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 3 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 3 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 3 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 3 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 3 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 3 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 3 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 3 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 4 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 4 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 4 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 4 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 4 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 4 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 4 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 4 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 4 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 4 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 4 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 4 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 4 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 4 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 4 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 4 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 4 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 4 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 4 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 4 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 4 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 4 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 4 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 4 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 4 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 4 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 4 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 4 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 4 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 4 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 4 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 5 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 5 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 5 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 5 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 5 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 5 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 5 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 5 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 5 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 5 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 5 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 5 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 5 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 5 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 5 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 5 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 5 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 5 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 5 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 5 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 5 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 5 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 5 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 5 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 5 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 5 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 5 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 5 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 5 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 5 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 5 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 6 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 6 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 6 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 6 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 6 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 6 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 6 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 6 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 6 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 6 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 6 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 6 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 6 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 6 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 6 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 6 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 6 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 6 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 6 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 6 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 6 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 6 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 6 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 6 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 6 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 6 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 6 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 6 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 6 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 6 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 6 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 7 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 7 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 7 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 7 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 7 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 7 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 7 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 7 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 7 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 7 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 7 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 7 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 7 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 7 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 7 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 7 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 7 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 7 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 7 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 7 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 7 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 7 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 7 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 7 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 7 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 7 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 7 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 7 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 7 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 7 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 7 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 8 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 8 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 8 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 8 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 8 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 8 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 8 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 8 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 8 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 8 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 8 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 8 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 8 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 8 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 8 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 8 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 8 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 8 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 8 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 8 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 8 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 8 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 8 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 8 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 8 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 8 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 8 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 8 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 8 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 8 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 8 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 9 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 9 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 9 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 9 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 9 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 9 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 9 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 9 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 9 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 9 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 9 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 9 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 9 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 9 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 9 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 9 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 9 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 9 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 9 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 9 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 9 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 9 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 9 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 9 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 9 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 9 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 9 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 9 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 9 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 9 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 9 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 10 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 10 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 10 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 10 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 10 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 10 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 10 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 10 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 10 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 10 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 10 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 10 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 10 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 10 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 10 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 10 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 10 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 10 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 10 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 10 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 10 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 10 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 10 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 10 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 10 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 10 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 10 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 10 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 10 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 10 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 10 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 11 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 11 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 11 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 11 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 11 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 11 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 11 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 11 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 11 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 11 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 11 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 11 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 11 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 11 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 11 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 11 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 11 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 11 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 11 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 11 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 11 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 11 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 11 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 11 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 11 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 11 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 11 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 11 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 11 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 11 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 11 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 12 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 12 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 12 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 12 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 12 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 12 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 12 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 12 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 12 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 12 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 12 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 12 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 12 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 12 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 12 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 12 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 12 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 12 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 12 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 12 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 12 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 12 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 12 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 12 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 12 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 12 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 12 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 12 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 12 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 12 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 12 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 13 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 13 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 13 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 13 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 13 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 13 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 13 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 13 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 13 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 13 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 13 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 13 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 13 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 13 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 13 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 13 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 13 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 13 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 13 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 13 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 13 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 13 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 13 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 13 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 13 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 13 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 13 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 13 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 13 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 13 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 13 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 14 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 14 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 14 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 14 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 14 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 14 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 14 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 14 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 14 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 14 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 14 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 14 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 14 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 14 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 14 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 14 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 14 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 14 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 14 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 14 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 14 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 14 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 14 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 14 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 14 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 14 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 14 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 14 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 14 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 14 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 14 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 15 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 15 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 15 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 15 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 15 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 15 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 15 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 15 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 15 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 15 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 15 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 15 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 15 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 15 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 15 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 15 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 15 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 15 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 15 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 15 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 15 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 15 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 15 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 15 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 15 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 15 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 15 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 15 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 15 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 15 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 15 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 16 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 16 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 16 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 16 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 16 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 16 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 16 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 16 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 16 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 16 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 16 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 16 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 16 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 16 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 16 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 16 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 16 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 16 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 16 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 16 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 16 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 16 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 16 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 16 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 16 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 16 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 16 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 16 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 16 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 16 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 16 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 17 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 17 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 17 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 17 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 17 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 17 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 17 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 17 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 17 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 17 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 17 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 17 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 17 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 17 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 17 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 17 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 17 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 17 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 17 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 17 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 17 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 17 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 17 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 17 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 17 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 17 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 17 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 17 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 17 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 17 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 17 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 18 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 18 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 18 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 18 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 18 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 18 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 18 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 18 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 18 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 18 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 18 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 18 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 18 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 18 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 18 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 18 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 18 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 18 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 18 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 18 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 18 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 18 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 18 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 18 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 18 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 18 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 18 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 18 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 18 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 18 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 18 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 19 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 19 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 19 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 19 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 19 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 19 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 19 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 19 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 19 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 19 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 19 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 19 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 19 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 19 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 19 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 19 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 19 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 19 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 19 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 19 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 19 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 19 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 19 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 19 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 19 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 19 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 19 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 19 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 19 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 19 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 19 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 20 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 20 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 20 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 20 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 20 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 20 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 20 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 20 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 20 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 20 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 20 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 20 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 20 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 20 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 20 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 20 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 20 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 20 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 20 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 20 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 20 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 20 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 20 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 20 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 20 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 20 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 20 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 20 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 20 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 20 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 20 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 21 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 21 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 21 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 21 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 21 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 21 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 21 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 21 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 21 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 21 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 21 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 21 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 21 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 21 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 21 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 21 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 21 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 21 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 21 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 21 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 21 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 21 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 21 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 21 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 21 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 21 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 21 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 21 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 21 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 21 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 21 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 22 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 22 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 22 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 22 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 22 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 22 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 22 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 22 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 22 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 22 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 22 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 22 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 22 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 22 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 22 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 22 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 22 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 22 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 22 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 22 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 22 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 22 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 22 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 22 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 22 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 22 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 22 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 22 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 22 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 22 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 22 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 23 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 23 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 23 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 23 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 23 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 23 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 23 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 23 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 23 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 23 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 23 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 23 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 23 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 23 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 23 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 23 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 23 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 23 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 23 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 23 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 23 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 23 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 23 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 23 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 23 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 23 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 23 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 23 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 23 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 23 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 23 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
25001 | 24 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25002 | 24 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25003 | 24 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25004 | 24 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 24
25005 | 24 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
25006 | 24 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25007 | 24 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25008 | 24 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25009 | 24 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25010 | 24 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
25011 | 24 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25012 | 24 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25013 | 24 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25014 | 24 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25015 | 24 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
25016 | 24 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 24
25017 | 24 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 24
25018 | 24 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 24
25019 | 24 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 24
25020 | 24 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 24
25021 | 24 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 24
25022 | 24 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 24
25023 | 24 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25024 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25025 | 24 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25026 | 24 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24
25027 | 24 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 24
25028 | 24 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 24
25029 | 24 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
25030 | 24 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 24
25031 | 24 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 24
25032 | 24 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 24
26001 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26002 | 1 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26003 | 1 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26004 | 1 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26005 | 1 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8
26006 | 1 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26007 | 1 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26008 | 1 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26009 | 1 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26010 | 1 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26011 | 1 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26012 | 1 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26013 | 1 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26014 | 1 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26015 | 1 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26016 | 1 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 8
26017 | 1 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 8
26018 | 1 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 8
26019 | 1 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 8
26020 | 1 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8
26021 | 1 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | Enumeration | R/W | 8
26022 | 1 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | IEEE Float | R | 8
26023 | 1 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
26024 | 1 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 8
26025 | 1 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 8
26026 | 1 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 8
26027 | 1 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8
26028 | 1 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 8
26029 | 1 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 8
26030 | 1 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | IEEE Float | R/W | 8
26033 | 1 | Process Value | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 8
26001 | 2 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26002 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26003 | 2 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26004 | 2 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26005 | 2 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8
26006 | 2 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26007 | 2 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26008 | 2 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26009 | 2 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26010 | 2 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26011 | 2 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26012 | 2 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26013 | 2 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26014 | 2 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26015 | 2 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26016 | 2 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 8
26017 | 2 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 8
26018 | 2 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 8
26019 | 2 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 8
26020 | 2 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8
26021 | 2 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | Enumeration | R/W | 8
26022 | 2 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | IEEE Float | R | 8
26023 | 2 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
26024 | 2 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 8
26025 | 2 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 8
26026 | 2 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 8
26027 | 2 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8
26028 | 2 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 8
26029 | 2 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 8
26030 | 2 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | IEEE Float | R/W | 8
26033 | 2 | Process Value | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 8
26001 | 3 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26002 | 3 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26003 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26004 | 3 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26005 | 3 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8
26006 | 3 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26007 | 3 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26008 | 3 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26009 | 3 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26010 | 3 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26011 | 3 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26012 | 3 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26013 | 3 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26014 | 3 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26015 | 3 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26016 | 3 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 8
26017 | 3 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 8
26018 | 3 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 8
26019 | 3 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 8
26020 | 3 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8
26021 | 3 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | Enumeration | R/W | 8
26022 | 3 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | IEEE Float | R | 8
26023 | 3 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
26024 | 3 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 8
26025 | 3 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 8
26026 | 3 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 8
26027 | 3 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8
26028 | 3 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 8
26029 | 3 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 8
26030 | 3 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | IEEE Float | R/W | 8
26033 | 3 | Process Value | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 8
26001 | 4 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26002 | 4 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26003 | 4 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26004 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26005 | 4 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8
26006 | 4 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26007 | 4 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26008 | 4 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26009 | 4 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26010 | 4 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26011 | 4 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26012 | 4 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26013 | 4 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26014 | 4 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26015 | 4 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26016 | 4 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 8
26017 | 4 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 8
26018 | 4 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 8
26019 | 4 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 8
26020 | 4 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8
26021 | 4 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | Enumeration | R/W | 8
26022 | 4 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | IEEE Float | R | 8
26023 | 4 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
26024 | 4 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 8
26025 | 4 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 8
26026 | 4 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 8
26027 | 4 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8
26028 | 4 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 8
26029 | 4 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 8
26030 | 4 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | IEEE Float | R/W | 8
26033 | 4 | Process Value | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 8
26001 | 5 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26002 | 5 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26003 | 5 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26004 | 5 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26005 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8
26006 | 5 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26007 | 5 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26008 | 5 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26009 | 5 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26010 | 5 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26011 | 5 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26012 | 5 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26013 | 5 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26014 | 5 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26015 | 5 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26016 | 5 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 8
26017 | 5 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 8
26018 | 5 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 8
26019 | 5 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 8
26020 | 5 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8
26021 | 5 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | Enumeration | R/W | 8
26022 | 5 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | IEEE Float | R | 8
26023 | 5 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
26024 | 5 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 8
26025 | 5 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 8
26026 | 5 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 8
26027 | 5 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8
26028 | 5 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 8
26029 | 5 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 8
26030 | 5 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | IEEE Float | R/W | 8
26033 | 5 | Process Value | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 8
26001 | 6 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26002 | 6 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26003 | 6 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26004 | 6 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26005 | 6 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8
26006 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26007 | 6 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26008 | 6 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26009 | 6 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26010 | 6 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26011 | 6 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26012 | 6 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26013 | 6 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26014 | 6 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26015 | 6 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26016 | 6 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 8
26017 | 6 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 8
26018 | 6 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 8
26019 | 6 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 8
26020 | 6 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8
26021 | 6 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | Enumeration | R/W | 8
26022 | 6 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | IEEE Float | R | 8
26023 | 6 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
26024 | 6 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 8
26025 | 6 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 8
26026 | 6 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 8
26027 | 6 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8
26028 | 6 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 8
26029 | 6 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 8
26030 | 6 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | IEEE Float | R/W | 8
26033 | 6 | Process Value | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 8
26001 | 7 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26002 | 7 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26003 | 7 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26004 | 7 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26005 | 7 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8
26006 | 7 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26007 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26008 | 7 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26009 | 7 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26010 | 7 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26011 | 7 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26012 | 7 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26013 | 7 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26014 | 7 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26015 | 7 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26016 | 7 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 8
26017 | 7 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 8
26018 | 7 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 8
26019 | 7 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 8
26020 | 7 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8
26021 | 7 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | Enumeration | R/W | 8
26022 | 7 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | IEEE Float | R | 8
26023 | 7 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
26024 | 7 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 8
26025 | 7 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 8
26026 | 7 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 8
26027 | 7 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8
26028 | 7 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 8
26029 | 7 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 8
26030 | 7 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | IEEE Float | R/W | 8
26033 | 7 | Process Value | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 8
26001 | 8 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26002 | 8 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26003 | 8 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26004 | 8 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 8
26005 | 8 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8
26006 | 8 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26007 | 8 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26008 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26009 | 8 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26010 | 8 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
26011 | 8 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26012 | 8 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26013 | 8 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26014 | 8 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26015 | 8 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
26016 | 8 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 8
26017 | 8 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 8
26018 | 8 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 8
26019 | 8 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 8
26020 | 8 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8
26021 | 8 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | Enumeration | R/W | 8
26022 | 8 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | IEEE Float | R | 8
26023 | 8 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
26024 | 8 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 8
26025 | 8 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 8
26026 | 8 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 8
26027 | 8 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8
26028 | 8 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 8
26029 | 8 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 8
26030 | 8 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | IEEE Float | R/W | 8
26033 | 8 | Process Value | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 8
27001 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 1 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 1 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 1 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 1 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 1 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 1 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 1 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 1 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 1 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 1 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 1 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 1 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 1 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 1 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 1 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 1 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 1 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 1 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 1 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 1 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 1 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 1 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 1 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 1 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 1 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 1 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 1 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 1 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 1 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 1 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 1 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 1 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 1 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 1 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 1 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 2 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 2 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 2 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 2 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 2 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 2 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 2 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 2 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 2 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 2 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 2 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 2 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 2 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 2 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 2 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 2 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 2 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 2 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 2 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 2 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 2 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 2 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 2 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 2 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 2 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 2 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 2 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 2 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 2 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 2 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 2 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 2 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 2 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 2 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 2 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 3 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 3 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 3 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 3 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 3 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 3 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 3 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 3 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 3 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 3 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 3 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 3 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 3 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 3 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 3 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 3 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 3 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 3 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 3 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 3 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 3 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 3 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 3 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 3 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 3 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 3 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 3 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 3 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 3 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 3 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 3 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 3 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 3 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 3 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 3 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 4 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 4 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 4 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 4 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 4 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 4 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 4 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 4 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 4 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 4 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 4 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 4 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 4 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 4 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 4 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 4 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 4 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 4 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 4 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 4 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 4 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 4 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 4 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 4 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 4 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 4 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 4 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 4 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 4 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 4 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 4 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 4 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 4 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 4 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 4 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 5 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 5 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 5 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 5 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 5 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 5 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 5 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 5 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 5 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 5 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 5 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 5 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 5 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 5 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 5 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 5 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 5 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 5 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 5 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 5 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 5 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 5 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 5 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 5 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 5 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 5 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 5 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 5 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 5 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 5 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 5 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 5 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 5 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 5 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 5 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 6 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 6 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 6 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 6 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 6 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 6 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 6 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 6 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 6 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 6 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 6 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 6 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 6 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 6 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 6 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 6 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 6 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 6 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 6 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 6 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 6 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 6 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 6 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 6 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 6 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 6 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 6 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 6 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 6 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 6 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 6 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 6 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 6 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 6 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 6 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 7 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 7 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 7 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 7 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 7 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 7 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 7 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 7 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 7 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 7 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 7 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 7 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 7 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 7 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 7 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 7 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 7 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 7 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 7 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 7 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 7 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 7 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 7 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 7 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 7 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 7 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 7 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 7 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 7 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 7 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 7 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 7 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 7 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 7 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 7 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 8 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 8 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 8 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 8 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 8 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 8 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 8 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 8 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 8 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 8 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 8 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 8 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 8 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 8 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 8 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 8 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 8 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 8 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 8 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 8 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 8 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 8 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 8 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 8 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 8 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 8 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 8 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 8 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 8 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 8 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 8 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 8 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 8 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 8 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 8 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 9 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 9 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 9 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 9 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 9 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 9 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 9 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 9 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 9 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 9 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 9 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 9 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 9 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 9 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 9 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 9 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 9 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 9 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 9 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 9 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 9 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 9 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 9 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 9 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 9 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 9 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 9 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 9 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 9 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 9 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 9 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 9 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 9 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 9 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 9 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 10 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 10 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 10 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 10 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 10 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 10 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 10 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 10 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 10 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 10 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 10 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 10 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 10 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 10 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 10 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 10 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 10 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 10 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 10 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 10 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 10 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 10 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 10 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 10 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 10 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 10 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 10 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 10 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 10 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 10 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 10 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 10 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 10 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 10 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 10 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 11 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 11 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 11 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 11 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 11 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 11 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 11 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 11 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 11 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 11 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 11 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 11 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 11 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 11 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 11 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 11 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 11 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 11 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 11 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 11 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 11 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 11 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 11 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 11 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 11 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 11 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 11 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 11 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 11 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 11 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 11 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 11 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 11 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 11 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 11 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 12 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 12 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 12 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 12 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 12 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 12 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 12 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 12 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 12 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 12 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 12 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 12 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 12 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 12 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 12 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 12 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 12 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 12 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 12 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 12 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 12 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 12 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 12 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 12 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 12 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 12 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 12 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 12 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 12 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 12 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 12 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 12 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 12 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 12 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 12 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 13 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 13 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 13 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 13 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 13 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 13 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 13 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 13 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 13 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 13 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 13 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 13 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 13 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 13 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 13 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 13 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 13 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 13 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 13 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 13 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 13 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 13 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 13 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 13 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 13 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 13 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 13 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 13 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 13 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 13 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 13 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 13 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 13 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 13 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 13 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 14 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 14 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 14 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 14 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 14 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 14 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 14 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 14 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 14 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 14 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 14 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 14 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 14 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 14 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 14 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 14 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 14 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 14 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 14 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 14 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 14 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 14 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 14 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 14 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 14 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 14 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 14 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 14 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 14 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 14 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 14 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 14 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 14 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 14 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 14 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 15 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 15 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 15 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 15 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 15 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 15 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 15 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 15 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 15 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 15 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 15 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 15 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 15 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 15 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 15 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 15 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 15 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 15 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 15 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 15 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 15 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 15 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 15 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 15 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 15 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 15 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 15 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 15 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 15 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 15 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 15 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 15 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 15 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 15 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 15 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 16 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 16 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 16 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 16 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 16 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 16 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 16 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 16 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 16 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 16 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 16 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 16 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 16 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 16 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 16 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 16 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 16 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 16 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 16 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 16 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 16 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 16 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 16 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 16 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 16 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 16 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 16 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 16 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 16 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 16 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 16 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 16 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 16 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 16 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 16 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 17 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 17 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 17 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 17 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 17 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 17 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 17 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 17 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 17 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 17 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 17 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 17 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 17 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 17 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 17 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 17 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 17 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 17 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 17 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 17 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 17 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 17 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 17 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 17 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 17 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 17 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 17 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 17 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 17 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 17 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 17 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 17 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 17 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 17 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 17 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 18 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 18 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 18 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 18 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 18 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 18 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 18 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 18 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 18 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 18 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 18 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 18 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 18 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 18 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 18 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 18 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 18 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 18 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 18 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 18 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 18 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 18 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 18 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 18 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 18 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 18 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 18 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 18 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 18 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 18 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 18 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 18 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 18 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 18 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 18 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 19 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 19 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 19 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 19 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 19 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 19 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 19 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 19 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 19 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 19 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 19 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 19 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 19 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 19 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 19 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 19 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 19 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 19 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 19 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 19 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 19 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 19 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 19 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 19 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 19 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 19 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 19 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 19 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 19 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 19 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 19 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 19 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 19 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 19 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 19 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 20 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 20 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 20 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 20 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 20 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 20 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 20 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 20 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 20 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 20 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 20 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 20 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 20 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 20 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 20 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 20 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 20 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 20 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 20 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 20 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 20 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 20 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 20 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 20 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 20 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 20 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 20 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 20 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 20 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 20 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 20 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 20 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 20 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 20 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 20 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 21 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 21 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 21 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 21 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 21 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 21 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 21 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 21 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 21 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 21 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 21 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 21 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 21 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 21 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 21 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 21 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 21 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 21 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 21 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 21 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 21 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 21 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 21 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 21 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 21 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 21 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 21 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 21 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 21 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 21 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 21 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 21 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 21 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 21 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 21 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 22 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 22 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 22 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 22 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 22 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 22 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 22 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 22 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 22 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 22 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 22 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 22 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 22 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 22 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 22 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 22 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 22 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 22 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 22 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 22 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 22 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 22 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 22 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 22 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 22 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 22 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 22 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 22 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 22 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 22 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 22 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 22 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 22 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 22 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 22 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 23 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 23 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 23 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 23 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 23 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 23 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 23 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 23 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 23 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 23 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 23 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 23 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 23 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 23 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 23 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 23 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 23 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 23 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 23 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 23 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 23 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 23 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 23 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 23 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 23 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 23 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 23 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 23 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 23 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 23 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 23 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 23 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 23 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 23 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 23 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
27001 | 24 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27002 | 24 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27003 | 24 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27004 | 24 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27005 | 24 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27006 | 24 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27007 | 24 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27008 | 24 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 24
27009 | 24 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27010 | 24 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27011 | 24 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27012 | 24 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27013 | 24 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27014 | 24 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27015 | 24 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27016 | 24 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 24
27017 | 24 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27018 | 24 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27019 | 24 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27020 | 24 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27021 | 24 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27022 | 24 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27023 | 24 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27024 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 24
27025 | 24 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27026 | 24 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27027 | 24 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27028 | 24 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27029 | 24 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27030 | 24 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27031 | 24 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27032 | 24 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 24
27033 | 24 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 24
27034 | 24 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 24
27035 | 24 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 24
27036 | 24 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 24
28001 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28002 | 1 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28003 | 1 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28004 | 1 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28005 | 1 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28006 | 1 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28007 | 1 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 16
28008 | 1 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 16
28009 | 1 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 16
28010 | 1 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 16
28011 | 1 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 16
28012 | 1 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 16
28013 | 1 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
28001 | 2 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28002 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28003 | 2 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28004 | 2 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28005 | 2 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28006 | 2 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28007 | 2 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 16
28008 | 2 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 16
28009 | 2 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 16
28010 | 2 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 16
28011 | 2 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 16
28012 | 2 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 16
28013 | 2 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
28001 | 3 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28002 | 3 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28003 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28004 | 3 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28005 | 3 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28006 | 3 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28007 | 3 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 16
28008 | 3 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 16
28009 | 3 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 16
28010 | 3 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 16
28011 | 3 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 16
28012 | 3 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 16
28013 | 3 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
28001 | 4 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28002 | 4 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28003 | 4 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28004 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28005 | 4 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28006 | 4 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28007 | 4 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 16
28008 | 4 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 16
28009 | 4 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 16
28010 | 4 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 16
28011 | 4 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 16
28012 | 4 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 16
28013 | 4 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
28001 | 5 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28002 | 5 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28003 | 5 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28004 | 5 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28005 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28006 | 5 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28007 | 5 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 16
28008 | 5 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 16
28009 | 5 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 16
28010 | 5 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 16
28011 | 5 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 16
28012 | 5 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 16
28013 | 5 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
28001 | 6 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28002 | 6 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28003 | 6 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28004 | 6 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28005 | 6 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28006 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28007 | 6 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 16
28008 | 6 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 16
28009 | 6 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 16
28010 | 6 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 16
28011 | 6 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 16
28012 | 6 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 16
28013 | 6 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
28001 | 7 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28002 | 7 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28003 | 7 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28004 | 7 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28005 | 7 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28006 | 7 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28007 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 16
28008 | 7 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 16
28009 | 7 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 16
28010 | 7 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 16
28011 | 7 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 16
28012 | 7 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 16
28013 | 7 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
28001 | 8 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28002 | 8 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28003 | 8 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28004 | 8 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28005 | 8 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28006 | 8 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28007 | 8 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 16
28008 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 16
28009 | 8 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 16
28010 | 8 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 16
28011 | 8 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 16
28012 | 8 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 16
28013 | 8 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
28001 | 9 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28002 | 9 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28003 | 9 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28004 | 9 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28005 | 9 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28006 | 9 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28007 | 9 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 16
28008 | 9 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 16
28009 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 16
28010 | 9 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 16
28011 | 9 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 16
28012 | 9 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 16
28013 | 9 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
28001 | 10 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28002 | 10 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28003 | 10 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28004 | 10 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28005 | 10 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28006 | 10 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28007 | 10 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 16
28008 | 10 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 16
28009 | 10 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 16
28010 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 16
28011 | 10 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 16
28012 | 10 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 16
28013 | 10 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
28001 | 11 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28002 | 11 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28003 | 11 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28004 | 11 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28005 | 11 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28006 | 11 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28007 | 11 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 16
28008 | 11 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 16
28009 | 11 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 16
28010 | 11 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 16
28011 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 16
28012 | 11 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 16
28013 | 11 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
28001 | 12 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28002 | 12 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28003 | 12 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28004 | 12 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28005 | 12 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28006 | 12 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28007 | 12 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 16
28008 | 12 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 16
28009 | 12 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 16
28010 | 12 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 16
28011 | 12 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 16
28012 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 16
28013 | 12 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
28001 | 13 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28002 | 13 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28003 | 13 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28004 | 13 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28005 | 13 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28006 | 13 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28007 | 13 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 16
28008 | 13 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 16
28009 | 13 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 16
28010 | 13 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 16
28011 | 13 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 16
28012 | 13 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 16
28013 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
28001 | 14 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28002 | 14 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28003 | 14 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28004 | 14 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28005 | 14 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28006 | 14 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28007 | 14 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 16
28008 | 14 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 16
28009 | 14 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 16
28010 | 14 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 16
28011 | 14 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 16
28012 | 14 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 16
28013 | 14 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
28001 | 15 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28002 | 15 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28003 | 15 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28004 | 15 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28005 | 15 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28006 | 15 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28007 | 15 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 16
28008 | 15 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 16
28009 | 15 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 16
28010 | 15 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 16
28011 | 15 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 16
28012 | 15 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 16
28013 | 15 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
28001 | 16 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28002 | 16 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16
28003 | 16 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28004 | 16 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
28005 | 16 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28006 | 16 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
28007 | 16 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 16
28008 | 16 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 16
28009 | 16 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 16
28010 | 16 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 16
28011 | 16 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 16
28012 | 16 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 16
28013 | 16 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30001 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30002 | 1 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30003 | 1 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30004 | 1 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30005 | 1 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30006 | 1 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30007 | 1 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30008 | 1 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30009 | 1 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 16
30010 | 1 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 16
30011 | 1 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 16
30012 | 1 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
30013 | 1 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 16
30014 | 1 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 16
30015 | 1 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 16
30016 | 1 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30017 | 1 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 16
30001 | 2 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30002 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30003 | 2 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30004 | 2 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30005 | 2 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30006 | 2 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30007 | 2 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30008 | 2 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30009 | 2 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 16
30010 | 2 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 16
30011 | 2 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 16
30012 | 2 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
30013 | 2 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 16
30014 | 2 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 16
30015 | 2 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 16
30016 | 2 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30017 | 2 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 16
30001 | 3 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30002 | 3 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30003 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30004 | 3 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30005 | 3 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30006 | 3 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30007 | 3 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30008 | 3 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30009 | 3 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 16
30010 | 3 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 16
30011 | 3 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 16
30012 | 3 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
30013 | 3 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 16
30014 | 3 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 16
30015 | 3 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 16
30016 | 3 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30017 | 3 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 16
30001 | 4 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30002 | 4 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30003 | 4 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30004 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30005 | 4 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30006 | 4 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30007 | 4 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30008 | 4 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30009 | 4 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 16
30010 | 4 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 16
30011 | 4 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 16
30012 | 4 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
30013 | 4 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 16
30014 | 4 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 16
30015 | 4 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 16
30016 | 4 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30017 | 4 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 16
30001 | 5 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30002 | 5 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30003 | 5 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30004 | 5 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30005 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30006 | 5 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30007 | 5 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30008 | 5 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30009 | 5 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 16
30010 | 5 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 16
30011 | 5 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 16
30012 | 5 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
30013 | 5 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 16
30014 | 5 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 16
30015 | 5 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 16
30016 | 5 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30017 | 5 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 16
30001 | 6 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30002 | 6 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30003 | 6 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30004 | 6 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30005 | 6 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30006 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30007 | 6 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30008 | 6 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30009 | 6 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 16
30010 | 6 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 16
30011 | 6 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 16
30012 | 6 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
30013 | 6 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 16
30014 | 6 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 16
30015 | 6 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 16
30016 | 6 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30017 | 6 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 16
30001 | 7 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30002 | 7 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30003 | 7 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30004 | 7 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30005 | 7 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30006 | 7 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30007 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30008 | 7 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30009 | 7 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 16
30010 | 7 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 16
30011 | 7 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 16
30012 | 7 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
30013 | 7 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 16
30014 | 7 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 16
30015 | 7 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 16
30016 | 7 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30017 | 7 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 16
30001 | 8 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30002 | 8 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30003 | 8 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30004 | 8 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30005 | 8 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30006 | 8 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30007 | 8 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30008 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30009 | 8 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 16
30010 | 8 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 16
30011 | 8 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 16
30012 | 8 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
30013 | 8 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 16
30014 | 8 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 16
30015 | 8 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 16
30016 | 8 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30017 | 8 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 16
30001 | 9 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30002 | 9 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30003 | 9 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30004 | 9 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30005 | 9 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30006 | 9 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30007 | 9 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30008 | 9 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30009 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 16
30010 | 9 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 16
30011 | 9 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 16
30012 | 9 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
30013 | 9 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 16
30014 | 9 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 16
30015 | 9 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 16
30016 | 9 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30017 | 9 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 16
30001 | 10 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30002 | 10 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30003 | 10 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30004 | 10 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30005 | 10 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30006 | 10 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30007 | 10 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30008 | 10 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30009 | 10 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 16
30010 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 16
30011 | 10 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 16
30012 | 10 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
30013 | 10 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 16
30014 | 10 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 16
30015 | 10 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 16
30016 | 10 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30017 | 10 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 16
30001 | 11 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30002 | 11 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30003 | 11 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30004 | 11 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30005 | 11 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30006 | 11 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30007 | 11 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30008 | 11 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30009 | 11 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 16
30010 | 11 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 16
30011 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 16
30012 | 11 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
30013 | 11 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 16
30014 | 11 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 16
30015 | 11 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 16
30016 | 11 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30017 | 11 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 16
30001 | 12 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30002 | 12 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30003 | 12 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30004 | 12 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30005 | 12 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30006 | 12 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30007 | 12 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30008 | 12 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30009 | 12 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 16
30010 | 12 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 16
30011 | 12 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 16
30012 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
30013 | 12 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 16
30014 | 12 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 16
30015 | 12 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 16
30016 | 12 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30017 | 12 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 16
30001 | 13 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30002 | 13 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30003 | 13 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30004 | 13 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30005 | 13 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30006 | 13 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30007 | 13 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30008 | 13 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30009 | 13 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 16
30010 | 13 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 16
30011 | 13 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 16
30012 | 13 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
30013 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 16
30014 | 13 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 16
30015 | 13 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 16
30016 | 13 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30017 | 13 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 16
30001 | 14 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30002 | 14 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30003 | 14 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30004 | 14 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30005 | 14 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30006 | 14 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30007 | 14 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30008 | 14 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30009 | 14 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 16
30010 | 14 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 16
30011 | 14 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 16
30012 | 14 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
30013 | 14 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 16
30014 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 16
30015 | 14 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 16
30016 | 14 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30017 | 14 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 16
30001 | 15 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30002 | 15 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30003 | 15 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30004 | 15 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30005 | 15 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30006 | 15 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30007 | 15 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30008 | 15 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30009 | 15 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 16
30010 | 15 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 16
30011 | 15 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 16
30012 | 15 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
30013 | 15 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 16
30014 | 15 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 16
30015 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 16
30016 | 15 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30017 | 15 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 16
30001 | 16 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30002 | 16 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
30003 | 16 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30004 | 16 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
30005 | 16 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30006 | 16 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
30007 | 16 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30008 | 16 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 16
30009 | 16 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 16
30010 | 16 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 16
30011 | 16 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 16
30012 | 16 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
30013 | 16 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 16
30014 | 16 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 16
30015 | 16 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 16
30016 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
30017 | 16 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 16
31001 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31002 | 1 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31003 | 1 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31004 | 1 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31005 | 1 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31006 | 1 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31007 | 1 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 16
31008 | 1 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 16
31009 | 1 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 16
31010 | 1 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 16
31011 | 1 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31012 | 1 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31013 | 1 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 16
31014 | 1 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31015 | 1 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 16
31016 | 1 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 16
31017 | 1 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 16
31018 | 1 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
31001 | 2 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31002 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31003 | 2 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31004 | 2 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31005 | 2 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31006 | 2 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31007 | 2 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 16
31008 | 2 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 16
31009 | 2 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 16
31010 | 2 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 16
31011 | 2 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31012 | 2 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31013 | 2 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 16
31014 | 2 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31015 | 2 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 16
31016 | 2 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 16
31017 | 2 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 16
31018 | 2 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
31001 | 3 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31002 | 3 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31003 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31004 | 3 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31005 | 3 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31006 | 3 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31007 | 3 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 16
31008 | 3 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 16
31009 | 3 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 16
31010 | 3 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 16
31011 | 3 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31012 | 3 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31013 | 3 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 16
31014 | 3 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31015 | 3 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 16
31016 | 3 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 16
31017 | 3 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 16
31018 | 3 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
31001 | 4 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31002 | 4 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31003 | 4 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31004 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31005 | 4 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31006 | 4 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31007 | 4 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 16
31008 | 4 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 16
31009 | 4 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 16
31010 | 4 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 16
31011 | 4 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31012 | 4 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31013 | 4 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 16
31014 | 4 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31015 | 4 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 16
31016 | 4 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 16
31017 | 4 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 16
31018 | 4 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
31001 | 5 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31002 | 5 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31003 | 5 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31004 | 5 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31005 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31006 | 5 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31007 | 5 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 16
31008 | 5 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 16
31009 | 5 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 16
31010 | 5 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 16
31011 | 5 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31012 | 5 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31013 | 5 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 16
31014 | 5 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31015 | 5 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 16
31016 | 5 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 16
31017 | 5 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 16
31018 | 5 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
31001 | 6 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31002 | 6 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31003 | 6 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31004 | 6 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31005 | 6 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31006 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31007 | 6 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 16
31008 | 6 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 16
31009 | 6 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 16
31010 | 6 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 16
31011 | 6 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31012 | 6 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31013 | 6 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 16
31014 | 6 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31015 | 6 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 16
31016 | 6 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 16
31017 | 6 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 16
31018 | 6 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
31001 | 7 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31002 | 7 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31003 | 7 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31004 | 7 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31005 | 7 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31006 | 7 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31007 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 16
31008 | 7 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 16
31009 | 7 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 16
31010 | 7 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 16
31011 | 7 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31012 | 7 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31013 | 7 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 16
31014 | 7 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31015 | 7 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 16
31016 | 7 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 16
31017 | 7 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 16
31018 | 7 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
31001 | 8 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31002 | 8 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31003 | 8 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31004 | 8 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31005 | 8 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31006 | 8 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31007 | 8 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 16
31008 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 16
31009 | 8 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 16
31010 | 8 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 16
31011 | 8 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31012 | 8 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31013 | 8 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 16
31014 | 8 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31015 | 8 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 16
31016 | 8 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 16
31017 | 8 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 16
31018 | 8 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
31001 | 9 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31002 | 9 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31003 | 9 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31004 | 9 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31005 | 9 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31006 | 9 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31007 | 9 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 16
31008 | 9 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 16
31009 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 16
31010 | 9 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 16
31011 | 9 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31012 | 9 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31013 | 9 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 16
31014 | 9 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31015 | 9 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 16
31016 | 9 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 16
31017 | 9 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 16
31018 | 9 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
31001 | 10 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31002 | 10 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31003 | 10 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31004 | 10 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31005 | 10 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31006 | 10 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31007 | 10 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 16
31008 | 10 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 16
31009 | 10 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 16
31010 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 16
31011 | 10 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31012 | 10 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31013 | 10 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 16
31014 | 10 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31015 | 10 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 16
31016 | 10 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 16
31017 | 10 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 16
31018 | 10 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
31001 | 11 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31002 | 11 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31003 | 11 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31004 | 11 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31005 | 11 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31006 | 11 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31007 | 11 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 16
31008 | 11 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 16
31009 | 11 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 16
31010 | 11 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 16
31011 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31012 | 11 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31013 | 11 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 16
31014 | 11 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31015 | 11 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 16
31016 | 11 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 16
31017 | 11 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 16
31018 | 11 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
31001 | 12 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31002 | 12 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31003 | 12 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31004 | 12 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31005 | 12 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31006 | 12 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31007 | 12 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 16
31008 | 12 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 16
31009 | 12 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 16
31010 | 12 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 16
31011 | 12 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31012 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31013 | 12 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 16
31014 | 12 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31015 | 12 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 16
31016 | 12 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 16
31017 | 12 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 16
31018 | 12 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
31001 | 13 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31002 | 13 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31003 | 13 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31004 | 13 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31005 | 13 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31006 | 13 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31007 | 13 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 16
31008 | 13 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 16
31009 | 13 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 16
31010 | 13 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 16
31011 | 13 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31012 | 13 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31013 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 16
31014 | 13 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31015 | 13 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 16
31016 | 13 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 16
31017 | 13 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 16
31018 | 13 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
31001 | 14 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31002 | 14 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31003 | 14 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31004 | 14 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31005 | 14 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31006 | 14 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31007 | 14 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 16
31008 | 14 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 16
31009 | 14 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 16
31010 | 14 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 16
31011 | 14 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31012 | 14 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31013 | 14 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 16
31014 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31015 | 14 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 16
31016 | 14 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 16
31017 | 14 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 16
31018 | 14 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
31001 | 15 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31002 | 15 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31003 | 15 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31004 | 15 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31005 | 15 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31006 | 15 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31007 | 15 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 16
31008 | 15 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 16
31009 | 15 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 16
31010 | 15 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 16
31011 | 15 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31012 | 15 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31013 | 15 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 16
31014 | 15 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31015 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 16
31016 | 15 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 16
31017 | 15 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 16
31018 | 15 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
31001 | 16 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31002 | 16 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16
31003 | 16 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31004 | 16 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16
31005 | 16 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31006 | 16 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16
31007 | 16 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 16
31008 | 16 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 16
31009 | 16 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 16
31010 | 16 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 16
31011 | 16 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31012 | 16 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31013 | 16 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 16
31014 | 16 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 16
31015 | 16 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 16
31016 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 16
31017 | 16 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 16
31018 | 16 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16
34001 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 8
34002 | 1 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
34003 | 1 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
34004 | 1 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | IEEE Float | R | 8
34005 | 1 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | Enumeration | R/W | 8
34006 | 1 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34007 | 1 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | IEEE Float | R | 8
34008 | 1 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34009 | 1 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 8
34010 | 1 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 8
34011 | 1 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 8
34012 | 1 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 8
34013 | 1 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 8
34014 | 1 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 8
34015 | 1 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 8
34016 | 1 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 8
34017 | 1 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 8
34018 | 1 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34019 | 1 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 8
34020 | 1 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 8
34021 | 1 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 8
34022 | 1 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 8
34023 | 1 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 8
34024 | 1 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 8
34025 | 1 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 8
34026 | 1 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 8
34027 | 1 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 8
34028 | 1 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8
34029 | 1 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 8
34001 | 2 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 8
34002 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
34003 | 2 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
34004 | 2 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | IEEE Float | R | 8
34005 | 2 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | Enumeration | R/W | 8
34006 | 2 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34007 | 2 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | IEEE Float | R | 8
34008 | 2 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34009 | 2 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 8
34010 | 2 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 8
34011 | 2 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 8
34012 | 2 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 8
34013 | 2 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 8
34014 | 2 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 8
34015 | 2 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 8
34016 | 2 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 8
34017 | 2 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 8
34018 | 2 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34019 | 2 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 8
34020 | 2 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 8
34021 | 2 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 8
34022 | 2 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 8
34023 | 2 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 8
34024 | 2 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 8
34025 | 2 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 8
34026 | 2 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 8
34027 | 2 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 8
34028 | 2 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8
34029 | 2 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 8
34001 | 3 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 8
34002 | 3 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
34003 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
34004 | 3 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | IEEE Float | R | 8
34005 | 3 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | Enumeration | R/W | 8
34006 | 3 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34007 | 3 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | IEEE Float | R | 8
34008 | 3 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34009 | 3 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 8
34010 | 3 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 8
34011 | 3 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 8
34012 | 3 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 8
34013 | 3 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 8
34014 | 3 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 8
34015 | 3 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 8
34016 | 3 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 8
34017 | 3 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 8
34018 | 3 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34019 | 3 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 8
34020 | 3 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 8
34021 | 3 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 8
34022 | 3 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 8
34023 | 3 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 8
34024 | 3 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 8
34025 | 3 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 8
34026 | 3 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 8
34027 | 3 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 8
34028 | 3 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8
34029 | 3 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 8
34001 | 4 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 8
34002 | 4 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
34003 | 4 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
34004 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | IEEE Float | R | 8
34005 | 4 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | Enumeration | R/W | 8
34006 | 4 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34007 | 4 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | IEEE Float | R | 8
34008 | 4 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34009 | 4 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 8
34010 | 4 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 8
34011 | 4 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 8
34012 | 4 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 8
34013 | 4 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 8
34014 | 4 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 8
34015 | 4 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 8
34016 | 4 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 8
34017 | 4 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 8
34018 | 4 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34019 | 4 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 8
34020 | 4 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 8
34021 | 4 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 8
34022 | 4 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 8
34023 | 4 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 8
34024 | 4 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 8
34025 | 4 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 8
34026 | 4 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 8
34027 | 4 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 8
34028 | 4 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8
34029 | 4 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 8
34001 | 5 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 8
34002 | 5 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
34003 | 5 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
34004 | 5 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | IEEE Float | R | 8
34005 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | Enumeration | R/W | 8
34006 | 5 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34007 | 5 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | IEEE Float | R | 8
34008 | 5 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34009 | 5 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 8
34010 | 5 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 8
34011 | 5 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 8
34012 | 5 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 8
34013 | 5 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 8
34014 | 5 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 8
34015 | 5 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 8
34016 | 5 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 8
34017 | 5 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 8
34018 | 5 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34019 | 5 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 8
34020 | 5 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 8
34021 | 5 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 8
34022 | 5 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 8
34023 | 5 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 8
34024 | 5 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 8
34025 | 5 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 8
34026 | 5 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 8
34027 | 5 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 8
34028 | 5 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8
34029 | 5 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 8
34001 | 6 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 8
34002 | 6 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
34003 | 6 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
34004 | 6 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | IEEE Float | R | 8
34005 | 6 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | Enumeration | R/W | 8
34006 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34007 | 6 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | IEEE Float | R | 8
34008 | 6 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34009 | 6 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 8
34010 | 6 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 8
34011 | 6 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 8
34012 | 6 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 8
34013 | 6 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 8
34014 | 6 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 8
34015 | 6 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 8
34016 | 6 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 8
34017 | 6 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 8
34018 | 6 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34019 | 6 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 8
34020 | 6 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 8
34021 | 6 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 8
34022 | 6 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 8
34023 | 6 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 8
34024 | 6 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 8
34025 | 6 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 8
34026 | 6 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 8
34027 | 6 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 8
34028 | 6 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8
34029 | 6 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 8
34001 | 7 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 8
34002 | 7 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
34003 | 7 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
34004 | 7 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | IEEE Float | R | 8
34005 | 7 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | Enumeration | R/W | 8
34006 | 7 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34007 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | IEEE Float | R | 8
34008 | 7 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34009 | 7 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 8
34010 | 7 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 8
34011 | 7 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 8
34012 | 7 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 8
34013 | 7 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 8
34014 | 7 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 8
34015 | 7 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 8
34016 | 7 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 8
34017 | 7 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 8
34018 | 7 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34019 | 7 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 8
34020 | 7 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 8
34021 | 7 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 8
34022 | 7 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 8
34023 | 7 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 8
34024 | 7 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 8
34025 | 7 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 8
34026 | 7 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 8
34027 | 7 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 8
34028 | 7 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8
34029 | 7 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 8
34001 | 8 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 8
34002 | 8 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8
34003 | 8 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8
34004 | 8 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | IEEE Float | R | 8
34005 | 8 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | Enumeration | R/W | 8
34006 | 8 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34007 | 8 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | IEEE Float | R | 8
34008 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34009 | 8 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 8
34010 | 8 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 8
34011 | 8 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 8
34012 | 8 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 8
34013 | 8 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 8
34014 | 8 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 8
34015 | 8 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 8
34016 | 8 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 8
34017 | 8 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 8
34018 | 8 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 8
34019 | 8 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 8
34020 | 8 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 8
34021 | 8 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 8
34022 | 8 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 8
34023 | 8 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 8
34024 | 8 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 8
34025 | 8 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 8
34026 | 8 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 8
34027 | 8 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 8
34028 | 8 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8
34029 | 8 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 8
35001 | 1 | Function | Base | Source Function A | Set the Source A for the receiver in the Special Output Function block. | None (61), Analog Input (142), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | Enumeration | R/W | 4
35002 | 1 | Function | Base | Source Function B | Set the Source B for the receiver in the Special Output Function block. | None (61), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | Enumeration | R/W | 4
35003 | 1 | Function | Base | Source Instance A | Set the Source Instance A for the receiver in the Special Output Function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4
35004 | 1 | Function | Base | Source Instance B | Set the Source Instance B for the receiver in the Special Output Function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4
35005 | 1 | Function | Base | Source Zone A | Set the Source Zone A for the receiver in the Special Output Function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4
35006 | 1 | Function | Base | Source Zone B | Set the Source Zone B for the receiver in the Special Output Function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4
35007 | 1 | Function | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 4
35008 | 1 | Function | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 4
35009 | 1 | Function | Base | Function | Set the Special Output Function block's purpose. | Off (62), Compressor Control (1506), Sequencer (1507), Motorized Valve (1508) | Off (62) | Enumeration | R/W | 4
35010 | 1 | Function | Base | Output Value 1 | Monitor the output value of the Special Output Function block transmitter 1. |  |  | IEEE Float | R | 4
35011 | 1 | Function | Base | Error | Monitor the error status for transmitter 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4
35012 | 1 | Function | Base | Output Value 2 | Monitor the output value of the Special Output Function block transmitter 2. |  |  | IEEE Float | R | 4
35013 | 1 | Function | Base | Error | Monitor the error status for transmitter 2. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4
35014 | 1 | Function | Base | Output Value 3 | Monitor the output value of the Special Output Function block transmitter 3. |  |  | IEEE Float | R | 4
35015 | 1 | Function | Base | Error | Monitor the error status for transmitter 3. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4
35016 | 1 | Function | Base | Output Value 4 | Monitor the output value of the Special Output Function block transmitter 4. |  |  | IEEE Float | R | 4
35017 | 1 | Function | Base | Error | Monitor the error status for transmitter 4. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4
35018 | 1 | Function | Base | Input A Turn On | Set the value of the signal at receiver A that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | IEEE Float | R/W | 4
35019 | 1 | Function | Base | Input A Turn Off | Set the value of the signal at receiver A that indicates there is no demand for the compressor to be on. | -100.00 to 100.00 | 5.0 | IEEE Float | R/W | 4
35020 | 1 | Function | Base | Input B Turn On | Set the value of the signal at receiver B that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | IEEE Float | R/W | 4
35021 | 1 | Function | Base | Input B Turn Off | Set the value of the signal at receiver B that indicates there is no demand for the compressor | -100.00 to 100.00 | 5.0 | IEEE Float | R/W | 4
35022 | 1 | Function | Base | Minimum On Time | Set the minimum amount of time the compressor must be on before it can be turned off again. | 0 to 9,999 | 20 | Unsigned 16-bit | R/W | 4
35023 | 1 | Function | Base | Minimum Off Time | Set the minimum amount of time the compressor is kept off before it can be turned on again. | 0 to 9,999 | 20 | Unsigned 16-bit | R/W | 4
35024 | 1 | Function | Base | Valve Travel Time | Set when used for motorized valve the time the valve takes to travel between fully closed and fully open. | 10 to 9,999 | 120 | Unsigned 16-bit | R/W | 4
35025 | 1 | Function | Base | Dead Band | Set when used for motorized valve the minimum amount for a single adjustment to the valve position. | 1.0 to 100.0 | 2.0 | IEEE Float | R/W | 4
35026 | 1 | Function | Base | Time Delay | Set when used for sequencer control minimum amount of time to wait between turning on one on-off output and the next. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 4
35027 | 1 | Function | Base | Output Order | Set when sequencer the method by which outputs 2, 3 and 4 are sequenced. | Linear (1509), Progressive (1510) | Linear (1509) | Enumeration | R/W | 4
35028 | 1 | Function | Base | Output 1 Size | Set when sequencer the proportion of the total power that is controlled by the proportional (vernier) output. | 0 to 99,999.0 | 10.0 | IEEE Float | R/W | 4
35029 | 1 | Function | Base | Output 2 Size | Set when sequencer the proportion of the total power that is switched by on-off output 2. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
35030 | 1 | Function | Base | Output 3 Size | Set when sequencer the proportion of the total power that is switched by on-off output 3. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
35031 | 1 | Function | Base | Output 4 Size | Set when sequencer the proportion of the total power that is switched by on-off output 4. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
35032 | 1 | Function | Base | Value | Monitor the Special Output Function value. | 0.000 to 100.000 |  | IEEE Float | R | 4
35035 | 1 | Function | Base | Off Delay | Set when used for compressor control an amount of time the output signal remains on after the Minimum On Time is satisfied and the signals at A and B indicate the compressor is no longer needed. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 4
35001 | 2 | Function | Base | Source Function A | Set the Source A for the receiver in the Special Output Function block. | None (61), Analog Input (142), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | Enumeration | R/W | 4
35002 | 2 | Function | Base | Source Function B | Set the Source B for the receiver in the Special Output Function block. | None (61), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | Enumeration | R/W | 4
35003 | 2 | Function | Base | Source Instance A | Set the Source Instance A for the receiver in the Special Output Function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4
35004 | 2 | Function | Base | Source Instance B | Set the Source Instance B for the receiver in the Special Output Function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4
35005 | 2 | Function | Base | Source Zone A | Set the Source Zone A for the receiver in the Special Output Function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4
35006 | 2 | Function | Base | Source Zone B | Set the Source Zone B for the receiver in the Special Output Function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4
35007 | 2 | Function | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 4
35008 | 2 | Function | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 4
35009 | 2 | Function | Base | Function | Set the Special Output Function block's purpose. | Off (62), Compressor Control (1506), Sequencer (1507), Motorized Valve (1508) | Off (62) | Enumeration | R/W | 4
35010 | 2 | Function | Base | Output Value 1 | Monitor the output value of the Special Output Function block transmitter 1. |  |  | IEEE Float | R | 4
35011 | 2 | Function | Base | Error | Monitor the error status for transmitter 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4
35012 | 2 | Function | Base | Output Value 2 | Monitor the output value of the Special Output Function block transmitter 2. |  |  | IEEE Float | R | 4
35013 | 2 | Function | Base | Error | Monitor the error status for transmitter 2. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4
35014 | 2 | Function | Base | Output Value 3 | Monitor the output value of the Special Output Function block transmitter 3. |  |  | IEEE Float | R | 4
35015 | 2 | Function | Base | Error | Monitor the error status for transmitter 3. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4
35016 | 2 | Function | Base | Output Value 4 | Monitor the output value of the Special Output Function block transmitter 4. |  |  | IEEE Float | R | 4
35017 | 2 | Function | Base | Error | Monitor the error status for transmitter 4. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4
35018 | 2 | Function | Base | Input A Turn On | Set the value of the signal at receiver A that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | IEEE Float | R/W | 4
35019 | 2 | Function | Base | Input A Turn Off | Set the value of the signal at receiver A that indicates there is no demand for the compressor to be on. | -100.00 to 100.00 | 5.0 | IEEE Float | R/W | 4
35020 | 2 | Function | Base | Input B Turn On | Set the value of the signal at receiver B that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | IEEE Float | R/W | 4
35021 | 2 | Function | Base | Input B Turn Off | Set the value of the signal at receiver B that indicates there is no demand for the compressor | -100.00 to 100.00 | 5.0 | IEEE Float | R/W | 4
35022 | 2 | Function | Base | Minimum On Time | Set the minimum amount of time the compressor must be on before it can be turned off again. | 0 to 9,999 | 20 | Unsigned 16-bit | R/W | 4
35023 | 2 | Function | Base | Minimum Off Time | Set the minimum amount of time the compressor is kept off before it can be turned on again. | 0 to 9,999 | 20 | Unsigned 16-bit | R/W | 4
35024 | 2 | Function | Base | Valve Travel Time | Set when used for motorized valve the time the valve takes to travel between fully closed and fully open. | 10 to 9,999 | 120 | Unsigned 16-bit | R/W | 4
35025 | 2 | Function | Base | Dead Band | Set when used for motorized valve the minimum amount for a single adjustment to the valve position. | 1.0 to 100.0 | 2.0 | IEEE Float | R/W | 4
35026 | 2 | Function | Base | Time Delay | Set when used for sequencer control minimum amount of time to wait between turning on one on-off output and the next. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 4
35027 | 2 | Function | Base | Output Order | Set when sequencer the method by which outputs 2, 3 and 4 are sequenced. | Linear (1509), Progressive (1510) | Linear (1509) | Enumeration | R/W | 4
35028 | 2 | Function | Base | Output 1 Size | Set when sequencer the proportion of the total power that is controlled by the proportional (vernier) output. | 0 to 99,999.0 | 10.0 | IEEE Float | R/W | 4
35029 | 2 | Function | Base | Output 2 Size | Set when sequencer the proportion of the total power that is switched by on-off output 2. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
35030 | 2 | Function | Base | Output 3 Size | Set when sequencer the proportion of the total power that is switched by on-off output 3. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
35031 | 2 | Function | Base | Output 4 Size | Set when sequencer the proportion of the total power that is switched by on-off output 4. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
35032 | 2 | Function | Base | Value | Monitor the Special Output Function value. | 0.000 to 100.000 |  | IEEE Float | R | 4
35035 | 2 | Function | Base | Off Delay | Set when used for compressor control an amount of time the output signal remains on after the Minimum On Time is satisfied and the signals at A and B indicate the compressor is no longer needed. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 4
35001 | 3 | Function | Base | Source Function A | Set the Source A for the receiver in the Special Output Function block. | None (61), Analog Input (142), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | Enumeration | R/W | 4
35002 | 3 | Function | Base | Source Function B | Set the Source B for the receiver in the Special Output Function block. | None (61), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | Enumeration | R/W | 4
35003 | 3 | Function | Base | Source Instance A | Set the Source Instance A for the receiver in the Special Output Function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4
35004 | 3 | Function | Base | Source Instance B | Set the Source Instance B for the receiver in the Special Output Function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4
35005 | 3 | Function | Base | Source Zone A | Set the Source Zone A for the receiver in the Special Output Function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4
35006 | 3 | Function | Base | Source Zone B | Set the Source Zone B for the receiver in the Special Output Function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4
35007 | 3 | Function | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 4
35008 | 3 | Function | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 4
35009 | 3 | Function | Base | Function | Set the Special Output Function block's purpose. | Off (62), Compressor Control (1506), Sequencer (1507), Motorized Valve (1508) | Off (62) | Enumeration | R/W | 4
35010 | 3 | Function | Base | Output Value 1 | Monitor the output value of the Special Output Function block transmitter 1. |  |  | IEEE Float | R | 4
35011 | 3 | Function | Base | Error | Monitor the error status for transmitter 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4
35012 | 3 | Function | Base | Output Value 2 | Monitor the output value of the Special Output Function block transmitter 2. |  |  | IEEE Float | R | 4
35013 | 3 | Function | Base | Error | Monitor the error status for transmitter 2. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4
35014 | 3 | Function | Base | Output Value 3 | Monitor the output value of the Special Output Function block transmitter 3. |  |  | IEEE Float | R | 4
35015 | 3 | Function | Base | Error | Monitor the error status for transmitter 3. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4
35016 | 3 | Function | Base | Output Value 4 | Monitor the output value of the Special Output Function block transmitter 4. |  |  | IEEE Float | R | 4
35017 | 3 | Function | Base | Error | Monitor the error status for transmitter 4. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4
35018 | 3 | Function | Base | Input A Turn On | Set the value of the signal at receiver A that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | IEEE Float | R/W | 4
35019 | 3 | Function | Base | Input A Turn Off | Set the value of the signal at receiver A that indicates there is no demand for the compressor to be on. | -100.00 to 100.00 | 5.0 | IEEE Float | R/W | 4
35020 | 3 | Function | Base | Input B Turn On | Set the value of the signal at receiver B that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | IEEE Float | R/W | 4
35021 | 3 | Function | Base | Input B Turn Off | Set the value of the signal at receiver B that indicates there is no demand for the compressor | -100.00 to 100.00 | 5.0 | IEEE Float | R/W | 4
35022 | 3 | Function | Base | Minimum On Time | Set the minimum amount of time the compressor must be on before it can be turned off again. | 0 to 9,999 | 20 | Unsigned 16-bit | R/W | 4
35023 | 3 | Function | Base | Minimum Off Time | Set the minimum amount of time the compressor is kept off before it can be turned on again. | 0 to 9,999 | 20 | Unsigned 16-bit | R/W | 4
35024 | 3 | Function | Base | Valve Travel Time | Set when used for motorized valve the time the valve takes to travel between fully closed and fully open. | 10 to 9,999 | 120 | Unsigned 16-bit | R/W | 4
35025 | 3 | Function | Base | Dead Band | Set when used for motorized valve the minimum amount for a single adjustment to the valve position. | 1.0 to 100.0 | 2.0 | IEEE Float | R/W | 4
35026 | 3 | Function | Base | Time Delay | Set when used for sequencer control minimum amount of time to wait between turning on one on-off output and the next. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 4
35027 | 3 | Function | Base | Output Order | Set when sequencer the method by which outputs 2, 3 and 4 are sequenced. | Linear (1509), Progressive (1510) | Linear (1509) | Enumeration | R/W | 4
35028 | 3 | Function | Base | Output 1 Size | Set when sequencer the proportion of the total power that is controlled by the proportional (vernier) output. | 0 to 99,999.0 | 10.0 | IEEE Float | R/W | 4
35029 | 3 | Function | Base | Output 2 Size | Set when sequencer the proportion of the total power that is switched by on-off output 2. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
35030 | 3 | Function | Base | Output 3 Size | Set when sequencer the proportion of the total power that is switched by on-off output 3. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
35031 | 3 | Function | Base | Output 4 Size | Set when sequencer the proportion of the total power that is switched by on-off output 4. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
35032 | 3 | Function | Base | Value | Monitor the Special Output Function value. | 0.000 to 100.000 |  | IEEE Float | R | 4
35035 | 3 | Function | Base | Off Delay | Set when used for compressor control an amount of time the output signal remains on after the Minimum On Time is satisfied and the signals at A and B indicate the compressor is no longer needed. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 4
35001 | 4 | Function | Base | Source Function A | Set the Source A for the receiver in the Special Output Function block. | None (61), Analog Input (142), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | Enumeration | R/W | 4
35002 | 4 | Function | Base | Source Function B | Set the Source B for the receiver in the Special Output Function block. | None (61), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | Enumeration | R/W | 4
35003 | 4 | Function | Base | Source Instance A | Set the Source Instance A for the receiver in the Special Output Function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4
35004 | 4 | Function | Base | Source Instance B | Set the Source Instance B for the receiver in the Special Output Function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4
35005 | 4 | Function | Base | Source Zone A | Set the Source Zone A for the receiver in the Special Output Function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4
35006 | 4 | Function | Base | Source Zone B | Set the Source Zone B for the receiver in the Special Output Function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4
35007 | 4 | Function | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 4
35008 | 4 | Function | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 4
35009 | 4 | Function | Base | Function | Set the Special Output Function block's purpose. | Off (62), Compressor Control (1506), Sequencer (1507), Motorized Valve (1508) | Off (62) | Enumeration | R/W | 4
35010 | 4 | Function | Base | Output Value 1 | Monitor the output value of the Special Output Function block transmitter 1. |  |  | IEEE Float | R | 4
35011 | 4 | Function | Base | Error | Monitor the error status for transmitter 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4
35012 | 4 | Function | Base | Output Value 2 | Monitor the output value of the Special Output Function block transmitter 2. |  |  | IEEE Float | R | 4
35013 | 4 | Function | Base | Error | Monitor the error status for transmitter 2. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4
35014 | 4 | Function | Base | Output Value 3 | Monitor the output value of the Special Output Function block transmitter 3. |  |  | IEEE Float | R | 4
35015 | 4 | Function | Base | Error | Monitor the error status for transmitter 3. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4
35016 | 4 | Function | Base | Output Value 4 | Monitor the output value of the Special Output Function block transmitter 4. |  |  | IEEE Float | R | 4
35017 | 4 | Function | Base | Error | Monitor the error status for transmitter 4. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4
35018 | 4 | Function | Base | Input A Turn On | Set the value of the signal at receiver A that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | IEEE Float | R/W | 4
35019 | 4 | Function | Base | Input A Turn Off | Set the value of the signal at receiver A that indicates there is no demand for the compressor to be on. | -100.00 to 100.00 | 5.0 | IEEE Float | R/W | 4
35020 | 4 | Function | Base | Input B Turn On | Set the value of the signal at receiver B that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | IEEE Float | R/W | 4
35021 | 4 | Function | Base | Input B Turn Off | Set the value of the signal at receiver B that indicates there is no demand for the compressor | -100.00 to 100.00 | 5.0 | IEEE Float | R/W | 4
35022 | 4 | Function | Base | Minimum On Time | Set the minimum amount of time the compressor must be on before it can be turned off again. | 0 to 9,999 | 20 | Unsigned 16-bit | R/W | 4
35023 | 4 | Function | Base | Minimum Off Time | Set the minimum amount of time the compressor is kept off before it can be turned on again. | 0 to 9,999 | 20 | Unsigned 16-bit | R/W | 4
35024 | 4 | Function | Base | Valve Travel Time | Set when used for motorized valve the time the valve takes to travel between fully closed and fully open. | 10 to 9,999 | 120 | Unsigned 16-bit | R/W | 4
35025 | 4 | Function | Base | Dead Band | Set when used for motorized valve the minimum amount for a single adjustment to the valve position. | 1.0 to 100.0 | 2.0 | IEEE Float | R/W | 4
35026 | 4 | Function | Base | Time Delay | Set when used for sequencer control minimum amount of time to wait between turning on one on-off output and the next. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 4
35027 | 4 | Function | Base | Output Order | Set when sequencer the method by which outputs 2, 3 and 4 are sequenced. | Linear (1509), Progressive (1510) | Linear (1509) | Enumeration | R/W | 4
35028 | 4 | Function | Base | Output 1 Size | Set when sequencer the proportion of the total power that is controlled by the proportional (vernier) output. | 0 to 99,999.0 | 10.0 | IEEE Float | R/W | 4
35029 | 4 | Function | Base | Output 2 Size | Set when sequencer the proportion of the total power that is switched by on-off output 2. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
35030 | 4 | Function | Base | Output 3 Size | Set when sequencer the proportion of the total power that is switched by on-off output 3. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
35031 | 4 | Function | Base | Output 4 Size | Set when sequencer the proportion of the total power that is switched by on-off output 4. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
35032 | 4 | Function | Base | Value | Monitor the Special Output Function value. | 0.000 to 100.000 |  | IEEE Float | R | 4
35035 | 4 | Function | Base | Off Delay | Set when used for compressor control an amount of time the output signal remains on after the Minimum On Time is satisfied and the signals at A and B indicate the compressor is no longer needed. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 4
36001 | 1 | Real Time Clock | Base | Time of Day | Monitor the time of day in seconds. | 0 to 86,399 |  | Unsigned 32-bit | R | 1
36003 | 1 | Real Time Clock | Base | Hours | Set the time of day (hours portion). | 0 to 23 |  | Unsigned 8-bit | R/W | 1
36004 | 1 | Real Time Clock | Base | Minutes | Set the time of day (minutes portion). | 0 to 59 |  | Unsigned 8-bit | R/W | 1
36005 | 1 | Real Time Clock | Base | Seconds | Set the time of day (seconds portion). | 0 to 59 |  | Unsigned 8-bit | R/W | 1
36006 | 1 | Real Time Clock | Base | Month | Set the time of day (month portion). | 1 to 12 |  | Unsigned 8-bit | R/W | 1
36007 | 1 | Real Time Clock | Base | Date | Set the time of day (date portion). | 1 to 31 |  | Unsigned 8-bit | R/W | 1
36008 | 1 | Real Time Clock | Base | Year | Set the time of day (year portion). | 2,008 to 2,100 |  | Unsigned 16-bit | R/W | 1
37002 | 1 | Data Logging | Base | Status | Monitor the datalogging status. | Not Ready (1660), OK (138), No Memory (1637), USB (1653) |  | Enumeration | R | 1
37003 | 1 | Data Logging | Base | Memory Full Action | Set action to take when memory is full. | Stop (1638), Overwrite (1639) | Stop (1638) | Enumeration | R/W | 1
37004 | 1 | Data Logging | Base | Available Logging Memory (MB) | Monitor the available memory usable for datalogging. | 0 to 4,294,967,295 |  | Unsigned 32-bit | R | 1
37005 | 1 | Data Logging | Base | Available Logging Time (Hours) | Monitor the time remaining before memory is full. | 0 to 4,294,967,295 |  | Unsigned 32-bit | R | 1
37006 | 1 | Data Logging | Base | Source Function A | Set source to trigger logging action. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1
37007 | 1 | Data Logging | Base | Source Instance A | Set source instance to trigger logging action. | 1 to 24 | 1 | Unsigned 8-bit | R/W | 1
37009 | 1 | Data Logging | Base | Source Value A | Monitor state of trigger for logging action. | Off (62), On (63) |  | Enumeration | R | 1
37012 | 1 | Data Logging | Base | Logging Status | Monitor data log action. | Recording (1990), Not Recording (1991) | Not Recording (1991) | Enumeration | R | 1
37014 | 1 | Data Logging | Base | File Size Limit (MB) | Set size of data log file. | 1 to 4,294,967,295 | 0 | Unsigned 32-bit | R/W | 1
37019 | 1 | Data Logging | Base | Date Format | Set date format recorded on each record. | MM/DD/YYYY (1631), DD/MM/YYYY (1632) | MM/DD/YYYY (1631) | Enumeration | R/W | 1
37020 | 1 | Data Logging | Base | Time Format | Set time format recorded on each record. | 12 Hour (1966), 24 Hour (1967) | 12 Hour (1966) | Enumeration | R/W | 1
37021 | 1 | Data Logging | Base | Log Action | Set data log action. | None (61), Start (1782), Stop (1638) |  | Enumeration | R/W | 1
37022 | 1 | Data Logging | Base | Log Interval | Set the interval at which to log data. | 0.1 sec (1971), 0.2 sec (1972), 0.5 sec (1973), 1 sec (1974), 2 sec (1975), 5 sec (1976), 10 sec (1977), 15 sec (1978), 30 sec (1979), 1 min (1980), 2 min (1985), 5 min (1981), 10 min (1986), 15 min (1987), 30 min (1988), 60 min (1989) | 5 min (1981) | Enumeration | R/W | 1
37023 | 1 | Data Logging | Base | Log To | Set location to store the data log file. | Internal (2057), USB Device (2058) | Internal (2057) | Enumeration | R/W | 1
37024 | 1 | Data Logging | Base | File Type | Set file type of the data log file. | Encrypted (2064), CSV (2063), Both (13) | Encrypted (2064) | Enumeration | R/W | 1
37032 | 1 | Data Logging | Base | Remote Transfer Interval In Hours | Set time before auto transfer occurs. | 0 to 65,535 | 0 | Unsigned 16-bit | R/W | 1
37033 | 1 | Data Logging | Base | Remote Transfer on Percent full | Set when to perform auto transfer based on memory fill. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 1
37034 | 1 | Data Logging | Base | Transfer Files Now by | Set to trigger data log transfer from internal memory to remote location.. | None (61), TFTP (2085), Samba (2086) | None (61) | Enumeration | R/W | 1
37038 | 1 | Data Logging | Base | Auto Transfer Type | Set where auto transfer should store files. | None (61), TFTP (2085), Samba (2086), USB (1653) | None (61) | Enumeration | R/W | 1
39001 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 1 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 1 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 1 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 1 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 1 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 1 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 1 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 1 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 1 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 2 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 2 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 2 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 2 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 2 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 2 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 2 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 2 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 2 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 3 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 3 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 3 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 3 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 3 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 3 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 3 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 3 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 3 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 3 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 4 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 4 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 4 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 4 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 4 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 4 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 4 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 4 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 4 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 5 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 5 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 5 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 5 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 5 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 5 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 5 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 5 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 5 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 6 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 6 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 6 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 6 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 6 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 6 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 6 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 6 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 6 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 7 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 7 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 7 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 7 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 7 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 7 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 7 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 7 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 7 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 8 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 8 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 8 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 8 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 8 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 8 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 8 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 8 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 8 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 9 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 9 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 9 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 9 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 9 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 9 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 9 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 9 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 9 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 10 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 10 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 10 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 10 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 10 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 10 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 10 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 10 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 10 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 10 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 11 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 11 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 11 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 11 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 11 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 11 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 11 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 11 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 11 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 11 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 12 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 12 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 12 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 12 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 12 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 12 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 12 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 12 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 12 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 13 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 13 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 13 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 13 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 13 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 13 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 13 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 13 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 13 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 14 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 14 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 14 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 14 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 14 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 14 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 14 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 14 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 14 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 14 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 15 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 15 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 15 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 15 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 15 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 15 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 15 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 15 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 15 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 15 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 16 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 16 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 16 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 16 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 16 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 16 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 16 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 16 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 16 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 16 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 17 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 17 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 17 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 17 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 17 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 17 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 17 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 17 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 17 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 17 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 18 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 18 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 18 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 18 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 18 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 18 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 18 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 18 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 18 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 18 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 19 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 19 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 19 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 19 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 19 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 19 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 19 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 19 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 19 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 19 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 20 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 20 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 20 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 20 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 20 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 20 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 20 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 20 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 20 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 20 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 21 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 21 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 21 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 21 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 21 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 21 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 21 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 21 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 21 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 21 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 22 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 22 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 22 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 22 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 22 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 22 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 22 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 22 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 22 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 22 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 23 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 23 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 23 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 23 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 23 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 23 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 23 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 23 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 23 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 23 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 24 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 24 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 24 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 24 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 24 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 24 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 24 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 24 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 24 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 24 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 25 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 25 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 25 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 25 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 25 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 25 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 25 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 25 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 25 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 25 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 26 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 26 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 26 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 26 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 26 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 26 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 26 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 26 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 26 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 26 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 27 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 27 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 27 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 27 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 27 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 27 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 27 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 27 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 27 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 27 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 28 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 28 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 28 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 28 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 28 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 28 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 28 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 28 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 28 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 28 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 29 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 29 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 29 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 29 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 29 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 29 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 29 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 29 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 29 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 29 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 30 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 30 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 30 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 30 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 30 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 30 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 30 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 30 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 30 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 30 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 31 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 31 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 31 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 31 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 31 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 31 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 31 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 31 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 31 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 31 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 32 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 32 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 32 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 32 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 32 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 32 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 32 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 32 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 32 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 32 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 33 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 33 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 33 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 33 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 33 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 33 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 33 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 33 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 33 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 33 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 34 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 34 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 34 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 34 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 34 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 34 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 34 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 34 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 34 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 34 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 35 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 35 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 35 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 35 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 35 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 35 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 35 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 35 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 35 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 35 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 36 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 36 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 36 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 36 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 36 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 36 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 36 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 36 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 36 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 36 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 37 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 37 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 37 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 37 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 37 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 37 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 37 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 37 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 37 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 37 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 38 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 38 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 38 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 38 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 38 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 38 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 38 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 38 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 38 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 38 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 39 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 39 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 39 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 39 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 39 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 39 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 39 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 39 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 39 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 39 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 40 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 40 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 40 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 40 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 40 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 40 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 40 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 40 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 40 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 40 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 41 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 41 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 41 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 41 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 41 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 41 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 41 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 41 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 41 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 41 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 42 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 42 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 42 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 42 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 42 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 42 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 42 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 42 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 42 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 42 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 43 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 43 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 43 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 43 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 43 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 43 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 43 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 43 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 43 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 43 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 44 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 44 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 44 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 44 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 44 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 44 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 44 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 44 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 44 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 44 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 45 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 45 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 45 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 45 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 45 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 45 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 45 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 45 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 45 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 45 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 46 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 46 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 46 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 46 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 46 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 46 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 46 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 46 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 46 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 46 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 47 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 47 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 47 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 47 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 47 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 47 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 47 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 47 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 47 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 47 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 48 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 48 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 48 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 48 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 48 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 48 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 48 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 48 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 48 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 48 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 49 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 49 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 49 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 49 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 49 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 49 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 49 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 49 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 49 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 49 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 50 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 50 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 50 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 50 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 50 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 50 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 50 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 50 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 50 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 50 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 51 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 51 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 51 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 51 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 51 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 51 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 51 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 51 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 51 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 51 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 52 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 52 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 52 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 52 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 52 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 52 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 52 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 52 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 52 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 52 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 53 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 53 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 53 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 53 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 53 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 53 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 53 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 53 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 53 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 53 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 54 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 54 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 54 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 54 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 54 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 54 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 54 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 54 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 54 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 54 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 55 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 55 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 55 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 55 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 55 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 55 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 55 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 55 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 55 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 55 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 56 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 56 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 56 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 56 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 56 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 56 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 56 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 56 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 56 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 56 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 57 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 57 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 57 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 57 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 57 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 57 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 57 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 57 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 57 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 57 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 58 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 58 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 58 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 58 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 58 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 58 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 58 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 58 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 58 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 58 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 59 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 59 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 59 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 59 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 59 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 59 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 59 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 59 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 59 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 59 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 60 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 60 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 60 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 60 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 60 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 60 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 60 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 60 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 60 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 60 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 61 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 61 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 61 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 61 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 61 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 61 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 61 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 61 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 61 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 61 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 62 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 62 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 62 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 62 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 62 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 62 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 62 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 62 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 62 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 62 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 63 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 63 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 63 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 63 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 63 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 63 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 63 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 63 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 63 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 63 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 64 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 64 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 64 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 64 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 64 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 64 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 64 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 64 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 64 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 64 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 65 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 65 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 65 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 65 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 65 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 65 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 65 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 65 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 65 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 65 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 66 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 66 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 66 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 66 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 66 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 66 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 66 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 66 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 66 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 66 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 67 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 67 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 67 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 67 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 67 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 67 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 67 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 67 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 67 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 67 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 68 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 68 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 68 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 68 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 68 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 68 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 68 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 68 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 68 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 68 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 69 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 69 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 69 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 69 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 69 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 69 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 69 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 69 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 69 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 69 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 70 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 70 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 70 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 70 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 70 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 70 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 70 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 70 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 70 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 70 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 71 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 71 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 71 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 71 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 71 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 71 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 71 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 71 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 71 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 71 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 72 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 72 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 72 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 72 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 72 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 72 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 72 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 72 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 72 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 72 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 73 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 73 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 73 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 73 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 73 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 73 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 73 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 73 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 73 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 73 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 74 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 74 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 74 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 74 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 74 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 74 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 74 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 74 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 74 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 74 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 75 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 75 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 75 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 75 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 75 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 75 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 75 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 75 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 75 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 75 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 76 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 76 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 76 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 76 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 76 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 76 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 76 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 76 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 76 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 76 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 77 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 77 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 77 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 77 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 77 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 77 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 77 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 77 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 77 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 77 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 78 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 78 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 78 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 78 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 78 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 78 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 78 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 78 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 78 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 78 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 79 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 79 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 79 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 79 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 79 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 79 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 79 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 79 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 79 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 79 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 80 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 80 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 80 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 80 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 80 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 80 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 80 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 80 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 80 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 80 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 81 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 81 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 81 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 81 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 81 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 81 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 81 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 81 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 81 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 81 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 82 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 82 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 82 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 82 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 82 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 82 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 82 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 82 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 82 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 82 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 83 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 83 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 83 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 83 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 83 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 83 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 83 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 83 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 83 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 83 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 84 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 84 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 84 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 84 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 84 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 84 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 84 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 84 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 84 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 84 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 85 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 85 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 85 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 85 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 85 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 85 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 85 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 85 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 85 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 85 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 86 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 86 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 86 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 86 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 86 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 86 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 86 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 86 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 86 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 86 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 87 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 87 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 87 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 87 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 87 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 87 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 87 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 87 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 87 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 87 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 88 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 88 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 88 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 88 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 88 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 88 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 88 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 88 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 88 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 88 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 89 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 89 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 89 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 89 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 89 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 89 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 89 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 89 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 89 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 89 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 90 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 90 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 90 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 90 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 90 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 90 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 90 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 90 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 90 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 90 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 91 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 91 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 91 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 91 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 91 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 91 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 91 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 91 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 91 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 91 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 92 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 92 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 92 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 92 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 92 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 92 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 92 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 92 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 92 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 92 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 93 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 93 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 93 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 93 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 93 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 93 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 93 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 93 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 93 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 93 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 94 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 94 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 94 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 94 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 94 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 94 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 94 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 94 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 94 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 94 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 95 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 95 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 95 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 95 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 95 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 95 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 95 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 95 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 95 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 95 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 96 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 96 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 96 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 96 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 96 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 96 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 96 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 96 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 96 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 96 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 97 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 97 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 97 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 97 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 97 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 97 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 97 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 97 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 97 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 97 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 98 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 98 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 98 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 98 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 98 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 98 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 98 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 98 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 98 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 98 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 99 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 99 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 99 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 99 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 99 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 99 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 99 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 99 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 99 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 99 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 100 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 100 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 100 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 100 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 100 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 100 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 100 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 100 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 100 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 100 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 101 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 101 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 101 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 101 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 101 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 101 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 101 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 101 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 101 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 101 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 102 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 102 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 102 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 102 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 102 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 102 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 102 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 102 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 102 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 102 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 103 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 103 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 103 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 103 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 103 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 103 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 103 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 103 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 103 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 103 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 104 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 104 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 104 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 104 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 104 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 104 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 104 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 104 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 104 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 104 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 105 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 105 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 105 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 105 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 105 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 105 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 105 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 105 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 105 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 105 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 106 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 106 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 106 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 106 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 106 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 106 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 106 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 106 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 106 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 106 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 107 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 107 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 107 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 107 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 107 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 107 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 107 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 107 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 107 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 107 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 108 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 108 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 108 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 108 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 108 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 108 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 108 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 108 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 108 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 108 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 109 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 109 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 109 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 109 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 109 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 109 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 109 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 109 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 109 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 109 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 110 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 110 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 110 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 110 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 110 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 110 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 110 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 110 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 110 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 110 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 111 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 111 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 111 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 111 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 111 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 111 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 111 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 111 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 111 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 111 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 112 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 112 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 112 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 112 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 112 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 112 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 112 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 112 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 112 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 112 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 113 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 113 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 113 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 113 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 113 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 113 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 113 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 113 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 113 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 113 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 114 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 114 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 114 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 114 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 114 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 114 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 114 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 114 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 114 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 114 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 115 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 115 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 115 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 115 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 115 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 115 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 115 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 115 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 115 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 115 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 116 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 116 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 116 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 116 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 116 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 116 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 116 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 116 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 116 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 116 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 117 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 117 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 117 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 117 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 117 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 117 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 117 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 117 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 117 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 117 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 118 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 118 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 118 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 118 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 118 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 118 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 118 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 118 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 118 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 118 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 119 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 119 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 119 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 119 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 119 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 119 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 119 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 119 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 119 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 119 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 120 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 120 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 120 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 120 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 120 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 120 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 120 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 120 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 120 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 120 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 121 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 121 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 121 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 121 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 121 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 121 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 121 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 121 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 121 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 121 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 122 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 122 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 122 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 122 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 122 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 122 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 122 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 122 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 122 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 122 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 123 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 123 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 123 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 123 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 123 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 123 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 123 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 123 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 123 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 123 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 124 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 124 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 124 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 124 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 124 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 124 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 124 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 124 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 124 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 124 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 125 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 125 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 125 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 125 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 125 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 125 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 125 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 125 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 125 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 125 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 126 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 126 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 126 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 126 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 126 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 126 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 126 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 126 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 126 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 126 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 127 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 127 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 127 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 127 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 127 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 127 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 127 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 127 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 127 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 127 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39001 | 128 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 128
39002 | 128 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 128
39004 | 128 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 128
39005 | 128 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39006 | 128 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 128
39007 | 128 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 128
39008 | 128 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 128
39009 | 128 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 128
39012 | 128 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
39013 | 128 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 128
44003 | 1 | Cascade | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 2
44004 | 1 | Cascade | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 2
44005 | 1 | Cascade | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | Enumeration | R | 2
44006 | 1 | Cascade | Base | Control Action | Set the heat/cool control method. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | Enumeration | R/W | 2
44007 | 1 | Cascade | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | Enumeration | R/W | 2
44008 | 1 | Cascade | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | IEEE Float | R/W | 2
44009 | 1 | Cascade | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | Enumeration | R/W | 2
44010 | 1 | Cascade | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | Enumeration | R | 2
44011 | 1 | Cascade | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | Enumeration | R/W | 2
44012 | 1 | Cascade | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | Unsigned 16-bit | R/W | 2
44013 | 1 | Cascade | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 2
44014 | 1 | Cascade | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | Enumeration | R | 2
44015 | 1 | Cascade | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 2
44016 | 1 | Cascade | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 2
44017 | 1 | Cascade | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 2
44018 | 1 | Cascade | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | IEEE Float | R/W | 2
44019 | 1 | Cascade | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | IEEE Float | R/W | 2
44020 | 1 | Cascade | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | IEEE Float | R/W | 2
44021 | 1 | Cascade | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | IEEE Float | R/W | 2
44022 | 1 | Cascade | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | IEEE Float | R/W | 2
44023 | 1 | Cascade | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 2
44024 | 1 | Cascade | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 2
44025 | 1 | Cascade | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | IEEE Float | R/W | 2
44026 | 1 | Cascade | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 2
44027 | 1 | Cascade | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | Enumeration | R/W | 2
44028 | 1 | Cascade | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 2
44029 | 1 | Cascade | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | Enumeration | R/W | 2
44030 | 1 | Cascade | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 2
44036 | 1 | Cascade | Base | Profile End Action | Set profile end action for control loop when end step is not specified. | User (100), Off (62), Hold (47) | User (100) | Enumeration | R/W | 2
44037 | 1 | Cascade | Base | Function | Set the type of cascade to implement. | Process (75), Deviation (1807) | Process (75) | Enumeration | R/W | 2
44040 | 1 | Cascade | Base | Range Low | Set the value represented for low power converted to a temperature set point for the inner loop. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44041 | 1 | Cascade | Base | Range High | Set the value represented for high power converted to a temperature set point for the inner loop. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 2
44043 | 1 | Cascade | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | Enumeration | R/W | 2
44050 | 1 | Cascade | Base | Inner Loop Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 2
44051 | 1 | Cascade | Base | Inner Loop Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 2
44057 | 1 | Cascade | Base | Inner Loop PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | Unsigned 8-bit | R | 2
44058 | 1 | Cascade | Base | Heat Proportional Band Inner Loop 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44059 | 1 | Cascade | Base | Cool Proportional Band Inner Loop 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44060 | 1 | Cascade | Base | Integral Inner Loop 1 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44061 | 1 | Cascade | Base | Derivative Inner Loop 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44062 | 1 | Cascade | Base | Heat Proportional Band Inner Loop 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44063 | 1 | Cascade | Base | Cool Proportional Band Inner Loop 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44064 | 1 | Cascade | Base | Integral Inner Loop 2 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44065 | 1 | Cascade | Base | Derivative Inner Loop 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44066 | 1 | Cascade | Base | Heat Proportional Band Inner Loop 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44067 | 1 | Cascade | Base | Cool Proportional Band Inner Loop 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44068 | 1 | Cascade | Base | Integral Inner Loop 3 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44069 | 1 | Cascade | Base | Derivative Inner Loop 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44070 | 1 | Cascade | Base | Heat Proportional Band Inner Loop 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44071 | 1 | Cascade | Base | Cool Proportional Band Inner Loop 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44072 | 1 | Cascade | Base | Integral Inner Loop 4 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44073 | 1 | Cascade | Base | Derivative Inner Loop 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44074 | 1 | Cascade | Base | Heat Proportional Band Inner Loop 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44075 | 1 | Cascade | Base | Cool Proportional Band Inner Loop 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44076 | 1 | Cascade | Base | Integral Inner Loop 5 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44077 | 1 | Cascade | Base | Derivative Inner Loop 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44078 | 1 | Cascade | Base | Inner Loop Deadband | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 2
44079 | 1 | Cascade | Base | Inner Loop On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 2
44080 | 1 | Cascade | Base | Inner Loop On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 2
44081 | 1 | Cascade | Base | Inner Loop Set Point Closed | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2
44100 | 1 | Cascade | Base | Outer Loop Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 2
44101 | 1 | Cascade | Base | Outer Loop Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 2
44102 | 1 | Cascade | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | Enumeration | R/W | 2
44103 | 1 | Cascade | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. |  |  | IEEE Float | R/W | 2
44104 | 1 | Cascade | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. |  |  | IEEE Float | R/W | 2
44105 | 1 | Cascade | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. |  |  | IEEE Float | R/W | 2
44106 | 1 | Cascade | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. |  |  | IEEE Float | R/W | 2
44108 | 1 | Cascade | Base | Heat Proportional Band Outer Loop 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44109 | 1 | Cascade | Base | Cool Proportional Band Outer Loop 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44110 | 1 | Cascade | Base | Integral Outer Loop 1 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44111 | 1 | Cascade | Base | Derivative Outer Loop 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44112 | 1 | Cascade | Base | Heat Proportional Band Outer Loop 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44113 | 1 | Cascade | Base | Cool Proportional Band Outer Loop 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44114 | 1 | Cascade | Base | Integral Outer Loop 2 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44115 | 1 | Cascade | Base | Derivative Outer Loop 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44116 | 1 | Cascade | Base | Heat Proportional Band Outer Loop 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44117 | 1 | Cascade | Base | Cool Proportional Band Outer Loop 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44118 | 1 | Cascade | Base | Integral Outer Loop 3 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44119 | 1 | Cascade | Base | Derivative Outer Loop 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44120 | 1 | Cascade | Base | Heat Proportional Band Outer Loop 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44121 | 1 | Cascade | Base | Cool Proportional Band Outer Loop 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44122 | 1 | Cascade | Base | Integral Outer Loop 4 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44123 | 1 | Cascade | Base | Derivative Outer Loop 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44124 | 1 | Cascade | Base | Heat Proportional Band Outer Loop 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44125 | 1 | Cascade | Base | Cool Proportional Band Outer Loop 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44126 | 1 | Cascade | Base | Integral Outer Loop 5 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44127 | 1 | Cascade | Base | Derivative Outer Loop 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44128 | 1 | Cascade | Base | Outer Loop Deadband | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 2
44131 | 1 | Cascade | Base | Outer Loop Set Point Closed | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2
44141 | 1 | Cascade | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | Unsigned 8-bit | R/W | 2
44150 | 1 | Cascade | Base | Cascade Heat Power | Monitor the requested PID heat power. | 0.0 to 100.0 |  | IEEE Float | R | 2
44152 | 1 | Cascade | Base | Cascade Cool Power | Monitor the requested PID cool power. | -100.0 to 0.0 |  | IEEE Float | R | 2
44154 | 1 | Cascade | Base | Cascade Power | Monitor the requested PID total power. | -100.0 to 100.0 |  | IEEE Float | R | 2
44163 | 1 | Cascade | Base | Source Value A | Monitor process value feedback for the outer loop while in auto mode. |  |  | IEEE Float | R | 2
44167 | 1 | Cascade | Base | Source Value B | Monitor the source input value used by the inner control loop while in auto mode. |  |  | IEEE Float | R | 2
44171 | 1 | Cascade | Base | Source Value C | Monitor the remote set point value. |  |  | IEEE Float | R | 2
44175 | 1 | Cascade | Base | Source Value D | Monitor set point from the profile engine when profiling is used. |  |  | IEEE Float | R | 2
44206 | 1 | Cascade | Base | Simple Set Point Enable | Set to switch off cascade feature. | On (63), Off (62) | Off (62) | Enumeration | R/W | 2
44207 | 1 | Cascade | Base | Cascade Control Mode Is Off | Monitor Cascade Control Mode is Off | On (63), Off (62) |  | Enumeration | R | 2
44208 | 1 | Cascade | Base | Set Point | Monitor Closed Loop Set Point |  |  | IEEE Float | R | 2
44003 | 2 | Cascade | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 2
44004 | 2 | Cascade | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 2
44005 | 2 | Cascade | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | Enumeration | R | 2
44006 | 2 | Cascade | Base | Control Action | Set the heat/cool control method. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | Enumeration | R/W | 2
44007 | 2 | Cascade | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | Enumeration | R/W | 2
44008 | 2 | Cascade | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | IEEE Float | R/W | 2
44009 | 2 | Cascade | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | Enumeration | R/W | 2
44010 | 2 | Cascade | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | Enumeration | R | 2
44011 | 2 | Cascade | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | Enumeration | R/W | 2
44012 | 2 | Cascade | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | Unsigned 16-bit | R/W | 2
44013 | 2 | Cascade | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 2
44014 | 2 | Cascade | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | Enumeration | R | 2
44015 | 2 | Cascade | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 2
44016 | 2 | Cascade | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 2
44017 | 2 | Cascade | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 2
44018 | 2 | Cascade | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | IEEE Float | R/W | 2
44019 | 2 | Cascade | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | IEEE Float | R/W | 2
44020 | 2 | Cascade | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | IEEE Float | R/W | 2
44021 | 2 | Cascade | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | IEEE Float | R/W | 2
44022 | 2 | Cascade | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | IEEE Float | R/W | 2
44023 | 2 | Cascade | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 2
44024 | 2 | Cascade | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 2
44025 | 2 | Cascade | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | IEEE Float | R/W | 2
44026 | 2 | Cascade | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 2
44027 | 2 | Cascade | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | Enumeration | R/W | 2
44028 | 2 | Cascade | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 2
44029 | 2 | Cascade | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | Enumeration | R/W | 2
44030 | 2 | Cascade | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 2
44036 | 2 | Cascade | Base | Profile End Action | Set profile end action for control loop when end step is not specified. | User (100), Off (62), Hold (47) | User (100) | Enumeration | R/W | 2
44037 | 2 | Cascade | Base | Function | Set the type of cascade to implement. | Process (75), Deviation (1807) | Process (75) | Enumeration | R/W | 2
44040 | 2 | Cascade | Base | Range Low | Set the value represented for low power converted to a temperature set point for the inner loop. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44041 | 2 | Cascade | Base | Range High | Set the value represented for high power converted to a temperature set point for the inner loop. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 2
44043 | 2 | Cascade | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | Enumeration | R/W | 2
44050 | 2 | Cascade | Base | Inner Loop Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 2
44051 | 2 | Cascade | Base | Inner Loop Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 2
44057 | 2 | Cascade | Base | Inner Loop PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | Unsigned 8-bit | R | 2
44058 | 2 | Cascade | Base | Heat Proportional Band Inner Loop 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44059 | 2 | Cascade | Base | Cool Proportional Band Inner Loop 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44060 | 2 | Cascade | Base | Integral Inner Loop 1 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44061 | 2 | Cascade | Base | Derivative Inner Loop 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44062 | 2 | Cascade | Base | Heat Proportional Band Inner Loop 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44063 | 2 | Cascade | Base | Cool Proportional Band Inner Loop 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44064 | 2 | Cascade | Base | Integral Inner Loop 2 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44065 | 2 | Cascade | Base | Derivative Inner Loop 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44066 | 2 | Cascade | Base | Heat Proportional Band Inner Loop 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44067 | 2 | Cascade | Base | Cool Proportional Band Inner Loop 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44068 | 2 | Cascade | Base | Integral Inner Loop 3 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44069 | 2 | Cascade | Base | Derivative Inner Loop 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44070 | 2 | Cascade | Base | Heat Proportional Band Inner Loop 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44071 | 2 | Cascade | Base | Cool Proportional Band Inner Loop 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44072 | 2 | Cascade | Base | Integral Inner Loop 4 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44073 | 2 | Cascade | Base | Derivative Inner Loop 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44074 | 2 | Cascade | Base | Heat Proportional Band Inner Loop 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44075 | 2 | Cascade | Base | Cool Proportional Band Inner Loop 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44076 | 2 | Cascade | Base | Integral Inner Loop 5 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44077 | 2 | Cascade | Base | Derivative Inner Loop 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44078 | 2 | Cascade | Base | Inner Loop Deadband | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 2
44079 | 2 | Cascade | Base | Inner Loop On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 2
44080 | 2 | Cascade | Base | Inner Loop On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 2
44081 | 2 | Cascade | Base | Inner Loop Set Point Closed | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2
44100 | 2 | Cascade | Base | Outer Loop Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 2
44101 | 2 | Cascade | Base | Outer Loop Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 2
44102 | 2 | Cascade | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | Enumeration | R/W | 2
44103 | 2 | Cascade | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. |  |  | IEEE Float | R/W | 2
44104 | 2 | Cascade | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. |  |  | IEEE Float | R/W | 2
44105 | 2 | Cascade | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. |  |  | IEEE Float | R/W | 2
44106 | 2 | Cascade | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. |  |  | IEEE Float | R/W | 2
44108 | 2 | Cascade | Base | Heat Proportional Band Outer Loop 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44109 | 2 | Cascade | Base | Cool Proportional Band Outer Loop 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44110 | 2 | Cascade | Base | Integral Outer Loop 1 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44111 | 2 | Cascade | Base | Derivative Outer Loop 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44112 | 2 | Cascade | Base | Heat Proportional Band Outer Loop 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44113 | 2 | Cascade | Base | Cool Proportional Band Outer Loop 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44114 | 2 | Cascade | Base | Integral Outer Loop 2 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44115 | 2 | Cascade | Base | Derivative Outer Loop 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44116 | 2 | Cascade | Base | Heat Proportional Band Outer Loop 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44117 | 2 | Cascade | Base | Cool Proportional Band Outer Loop 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44118 | 2 | Cascade | Base | Integral Outer Loop 3 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44119 | 2 | Cascade | Base | Derivative Outer Loop 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44120 | 2 | Cascade | Base | Heat Proportional Band Outer Loop 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44121 | 2 | Cascade | Base | Cool Proportional Band Outer Loop 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44122 | 2 | Cascade | Base | Integral Outer Loop 4 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44123 | 2 | Cascade | Base | Derivative Outer Loop 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44124 | 2 | Cascade | Base | Heat Proportional Band Outer Loop 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44125 | 2 | Cascade | Base | Cool Proportional Band Outer Loop 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2
44126 | 2 | Cascade | Base | Integral Outer Loop 5 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2
44127 | 2 | Cascade | Base | Derivative Outer Loop 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2
44128 | 2 | Cascade | Base | Outer Loop Deadband | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 2
44131 | 2 | Cascade | Base | Outer Loop Set Point Closed | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2
44141 | 2 | Cascade | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | Unsigned 8-bit | R/W | 2
44150 | 2 | Cascade | Base | Cascade Heat Power | Monitor the requested PID heat power. | 0.0 to 100.0 |  | IEEE Float | R | 2
44152 | 2 | Cascade | Base | Cascade Cool Power | Monitor the requested PID cool power. | -100.0 to 0.0 |  | IEEE Float | R | 2
44154 | 2 | Cascade | Base | Cascade Power | Monitor the requested PID total power. | -100.0 to 100.0 |  | IEEE Float | R | 2
44163 | 2 | Cascade | Base | Source Value A | Monitor process value feedback for the outer loop while in auto mode. |  |  | IEEE Float | R | 2
44167 | 2 | Cascade | Base | Source Value B | Monitor the source input value used by the inner control loop while in auto mode. |  |  | IEEE Float | R | 2
44171 | 2 | Cascade | Base | Source Value C | Monitor the remote set point value. |  |  | IEEE Float | R | 2
44175 | 2 | Cascade | Base | Source Value D | Monitor the set point used by the control loop while a profile is active. |  |  | IEEE Float | R | 2
44206 | 2 | Cascade | Base | Simple Set Point Enable | Set to switch off cascade feature. | On (63), Off (62) | Off (62) | Enumeration | R/W | 2
44207 | 2 | Cascade | Base | Cascade Control Mode Is Off | Monitor Cascade Control Mode is Off | On (63), Off (62) |  | Enumeration | R | 2
44208 | 2 | Cascade | Base | Set Point | Monitor Closed Loop Set Point |  |  | IEEE Float | R | 2
46001 | 1 | Function Key | Base | Function | Set the soft key action. | Momentary (1714), Toggle (1713), On Pulse (1471) | Momentary (1714) | Enumeration | R/W | 4
46002 | 1 | Function Key | Base | Time | Set the pulse time If function is On Pulse. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 4
46003 | 1 | Function Key | Base | Input State | Monitor the key state. | On (63), Off (62) |  | Enumeration | R | 4
46006 | 1 | Function Key | Base | Key Action | Set when the action occurs. | Down (1457), Up (1456) | Up (1456) | Enumeration | R/W | 4
46007 | 1 | Function Key | Base | Error | Monitor the error for key actions. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 4
46008 | 1 | Function Key | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 4
46001 | 2 | Function Key | Base | Function | Set the soft key action. | Momentary (1714), Toggle (1713), On Pulse (1471) | Momentary (1714) | Enumeration | R/W | 4
46002 | 2 | Function Key | Base | Time | Set the pulse time If function is On Pulse. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 4
46003 | 2 | Function Key | Base | Input State | Monitor the key state. | On (63), Off (62) |  | Enumeration | R | 4
46006 | 2 | Function Key | Base | Key Action | Set when the action occurs. | Down (1457), Up (1456) | Up (1456) | Enumeration | R/W | 4
46007 | 2 | Function Key | Base | Error | Monitor the error for key actions. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 4
46008 | 2 | Function Key | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 4
46001 | 3 | Function Key | Base | Function | Set the soft key action. | Momentary (1714), Toggle (1713), On Pulse (1471) | Momentary (1714) | Enumeration | R/W | 4
46002 | 3 | Function Key | Base | Time | Set the pulse time If function is On Pulse. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 4
46003 | 3 | Function Key | Base | Input State | Monitor the key state. | On (63), Off (62) |  | Enumeration | R | 4
46006 | 3 | Function Key | Base | Key Action | Set when the action occurs. | Down (1457), Up (1456) | Up (1456) | Enumeration | R/W | 4
46007 | 3 | Function Key | Base | Error | Monitor the error for key actions. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 4
46008 | 3 | Function Key | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 4
46001 | 4 | Function Key | Base | Function | Set the soft key action. | Momentary (1714), Toggle (1713), On Pulse (1471) | Momentary (1714) | Enumeration | R/W | 4
46002 | 4 | Function Key | Base | Time | Set the pulse time If function is On Pulse. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 4
46003 | 4 | Function Key | Base | Input State | Monitor the key state. | On (63), Off (62) |  | Enumeration | R | 4
46006 | 4 | Function Key | Base | Key Action | Set when the action occurs. | Down (1457), Up (1456) | Up (1456) | Enumeration | R/W | 4
46007 | 4 | Function Key | Base | Error | Monitor the error for key actions. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 4
46008 | 4 | Function Key | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 4
55001 | 1 | Universal Input | 1 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 1 | Universal Input | 1 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 1 | Universal Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 1 | Universal Input | 1 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 1 | Universal Input | 1 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 1 | Universal Input | 1 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 1 | Universal Input | 1 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 1 | Universal Input | 1 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 1 | Universal Input | 1 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 1 | Universal Input | 1 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 1 | Universal Input | 1 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 1 | Universal Input | 1 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 1 | Universal Input | 1 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 1 | Universal Input | 1 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 1 | Universal Input | 1 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 1 | Universal Input | 1 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 1 | Universal Input | 1 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 1 | Universal Input | 1 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 1 | Universal Input | 1 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 1 | Universal Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 1 | Universal Input | 1 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 1 | Universal Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 1 | Universal Input | 1 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 1 | Universal Input | 1 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 1 | Universal Input | 1 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 1 | Universal Input | 1 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 1 | Universal Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 1 | Universal Input | 1 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 2 | Universal Input | 1 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 2 | Universal Input | 1 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 2 | Universal Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 2 | Universal Input | 1 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 2 | Universal Input | 1 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 2 | Universal Input | 1 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 2 | Universal Input | 1 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 2 | Universal Input | 1 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 2 | Universal Input | 1 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 2 | Universal Input | 1 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 2 | Universal Input | 1 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 2 | Universal Input | 1 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 2 | Universal Input | 1 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 2 | Universal Input | 1 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 2 | Universal Input | 1 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 2 | Universal Input | 1 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 2 | Universal Input | 1 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 2 | Universal Input | 1 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 2 | Universal Input | 1 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 2 | Universal Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 2 | Universal Input | 1 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 2 | Universal Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 2 | Universal Input | 1 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 2 | Universal Input | 1 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 2 | Universal Input | 1 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 2 | Universal Input | 1 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 2 | Universal Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 2 | Universal Input | 1 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 3 | Universal Input | 1 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 3 | Universal Input | 1 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 3 | Universal Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 3 | Universal Input | 1 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 3 | Universal Input | 1 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 3 | Universal Input | 1 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 3 | Universal Input | 1 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 3 | Universal Input | 1 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 3 | Universal Input | 1 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 3 | Universal Input | 1 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 3 | Universal Input | 1 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 3 | Universal Input | 1 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 3 | Universal Input | 1 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 3 | Universal Input | 1 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 3 | Universal Input | 1 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 3 | Universal Input | 1 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 3 | Universal Input | 1 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 3 | Universal Input | 1 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 3 | Universal Input | 1 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 3 | Universal Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 3 | Universal Input | 1 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 3 | Universal Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 3 | Universal Input | 1 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 3 | Universal Input | 1 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 3 | Universal Input | 1 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 3 | Universal Input | 1 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 3 | Universal Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 3 | Universal Input | 1 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 4 | Universal Input | 1 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 4 | Universal Input | 1 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 4 | Universal Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 4 | Universal Input | 1 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 4 | Universal Input | 1 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 4 | Universal Input | 1 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 4 | Universal Input | 1 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 4 | Universal Input | 1 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 4 | Universal Input | 1 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 4 | Universal Input | 1 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 4 | Universal Input | 1 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 4 | Universal Input | 1 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 4 | Universal Input | 1 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 4 | Universal Input | 1 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 4 | Universal Input | 1 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 4 | Universal Input | 1 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 4 | Universal Input | 1 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 4 | Universal Input | 1 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 4 | Universal Input | 1 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 4 | Universal Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 4 | Universal Input | 1 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 4 | Universal Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 4 | Universal Input | 1 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 4 | Universal Input | 1 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 4 | Universal Input | 1 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 4 | Universal Input | 1 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 4 | Universal Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 4 | Universal Input | 1 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 11 | Universal Input | 2 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 11 | Universal Input | 2 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 11 | Universal Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 11 | Universal Input | 2 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 11 | Universal Input | 2 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 11 | Universal Input | 2 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 11 | Universal Input | 2 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 11 | Universal Input | 2 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 11 | Universal Input | 2 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 11 | Universal Input | 2 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 11 | Universal Input | 2 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 11 | Universal Input | 2 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 11 | Universal Input | 2 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 11 | Universal Input | 2 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 11 | Universal Input | 2 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 11 | Universal Input | 2 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 11 | Universal Input | 2 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 11 | Universal Input | 2 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 11 | Universal Input | 2 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 11 | Universal Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 11 | Universal Input | 2 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 11 | Universal Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 11 | Universal Input | 2 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 11 | Universal Input | 2 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 11 | Universal Input | 2 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 11 | Universal Input | 2 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 11 | Universal Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 11 | Universal Input | 2 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 12 | Universal Input | 2 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 12 | Universal Input | 2 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 12 | Universal Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 12 | Universal Input | 2 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 12 | Universal Input | 2 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 12 | Universal Input | 2 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 12 | Universal Input | 2 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 12 | Universal Input | 2 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 12 | Universal Input | 2 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 12 | Universal Input | 2 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 12 | Universal Input | 2 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 12 | Universal Input | 2 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 12 | Universal Input | 2 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 12 | Universal Input | 2 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 12 | Universal Input | 2 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 12 | Universal Input | 2 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 12 | Universal Input | 2 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 12 | Universal Input | 2 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 12 | Universal Input | 2 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 12 | Universal Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 12 | Universal Input | 2 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 12 | Universal Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 12 | Universal Input | 2 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 12 | Universal Input | 2 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 12 | Universal Input | 2 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 12 | Universal Input | 2 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 12 | Universal Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 12 | Universal Input | 2 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 13 | Universal Input | 2 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 13 | Universal Input | 2 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 13 | Universal Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 13 | Universal Input | 2 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 13 | Universal Input | 2 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 13 | Universal Input | 2 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 13 | Universal Input | 2 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 13 | Universal Input | 2 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 13 | Universal Input | 2 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 13 | Universal Input | 2 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 13 | Universal Input | 2 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 13 | Universal Input | 2 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 13 | Universal Input | 2 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 13 | Universal Input | 2 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 13 | Universal Input | 2 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 13 | Universal Input | 2 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 13 | Universal Input | 2 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 13 | Universal Input | 2 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 13 | Universal Input | 2 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 13 | Universal Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 13 | Universal Input | 2 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 13 | Universal Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 13 | Universal Input | 2 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 13 | Universal Input | 2 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 13 | Universal Input | 2 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 13 | Universal Input | 2 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 13 | Universal Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 13 | Universal Input | 2 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 14 | Universal Input | 2 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 14 | Universal Input | 2 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 14 | Universal Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 14 | Universal Input | 2 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 14 | Universal Input | 2 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 14 | Universal Input | 2 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 14 | Universal Input | 2 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 14 | Universal Input | 2 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 14 | Universal Input | 2 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 14 | Universal Input | 2 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 14 | Universal Input | 2 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 14 | Universal Input | 2 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 14 | Universal Input | 2 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 14 | Universal Input | 2 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 14 | Universal Input | 2 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 14 | Universal Input | 2 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 14 | Universal Input | 2 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 14 | Universal Input | 2 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 14 | Universal Input | 2 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 14 | Universal Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 14 | Universal Input | 2 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 14 | Universal Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 14 | Universal Input | 2 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 14 | Universal Input | 2 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 14 | Universal Input | 2 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 14 | Universal Input | 2 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 14 | Universal Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 14 | Universal Input | 2 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 21 | Universal Input | 3 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 21 | Universal Input | 3 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 21 | Universal Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 21 | Universal Input | 3 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 21 | Universal Input | 3 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 21 | Universal Input | 3 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 21 | Universal Input | 3 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 21 | Universal Input | 3 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 21 | Universal Input | 3 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 21 | Universal Input | 3 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 21 | Universal Input | 3 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 21 | Universal Input | 3 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 21 | Universal Input | 3 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 21 | Universal Input | 3 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 21 | Universal Input | 3 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 21 | Universal Input | 3 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 21 | Universal Input | 3 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 21 | Universal Input | 3 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 21 | Universal Input | 3 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 21 | Universal Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 21 | Universal Input | 3 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 21 | Universal Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 21 | Universal Input | 3 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 21 | Universal Input | 3 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 21 | Universal Input | 3 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 21 | Universal Input | 3 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 21 | Universal Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 21 | Universal Input | 3 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 22 | Universal Input | 3 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 22 | Universal Input | 3 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 22 | Universal Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 22 | Universal Input | 3 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 22 | Universal Input | 3 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 22 | Universal Input | 3 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 22 | Universal Input | 3 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 22 | Universal Input | 3 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 22 | Universal Input | 3 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 22 | Universal Input | 3 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 22 | Universal Input | 3 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 22 | Universal Input | 3 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 22 | Universal Input | 3 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 22 | Universal Input | 3 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 22 | Universal Input | 3 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 22 | Universal Input | 3 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 22 | Universal Input | 3 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 22 | Universal Input | 3 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 22 | Universal Input | 3 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 22 | Universal Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 22 | Universal Input | 3 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 22 | Universal Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 22 | Universal Input | 3 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 22 | Universal Input | 3 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 22 | Universal Input | 3 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 22 | Universal Input | 3 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 22 | Universal Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 22 | Universal Input | 3 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 23 | Universal Input | 3 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 23 | Universal Input | 3 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 23 | Universal Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 23 | Universal Input | 3 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 23 | Universal Input | 3 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 23 | Universal Input | 3 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 23 | Universal Input | 3 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 23 | Universal Input | 3 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 23 | Universal Input | 3 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 23 | Universal Input | 3 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 23 | Universal Input | 3 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 23 | Universal Input | 3 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 23 | Universal Input | 3 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 23 | Universal Input | 3 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 23 | Universal Input | 3 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 23 | Universal Input | 3 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 23 | Universal Input | 3 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 23 | Universal Input | 3 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 23 | Universal Input | 3 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 23 | Universal Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 23 | Universal Input | 3 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 23 | Universal Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 23 | Universal Input | 3 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 23 | Universal Input | 3 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 23 | Universal Input | 3 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 23 | Universal Input | 3 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 23 | Universal Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 23 | Universal Input | 3 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 24 | Universal Input | 3 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 24 | Universal Input | 3 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 24 | Universal Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 24 | Universal Input | 3 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 24 | Universal Input | 3 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 24 | Universal Input | 3 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 24 | Universal Input | 3 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 24 | Universal Input | 3 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 24 | Universal Input | 3 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 24 | Universal Input | 3 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 24 | Universal Input | 3 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 24 | Universal Input | 3 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 24 | Universal Input | 3 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 24 | Universal Input | 3 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 24 | Universal Input | 3 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 24 | Universal Input | 3 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 24 | Universal Input | 3 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 24 | Universal Input | 3 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 24 | Universal Input | 3 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 24 | Universal Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 24 | Universal Input | 3 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 24 | Universal Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 24 | Universal Input | 3 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 24 | Universal Input | 3 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 24 | Universal Input | 3 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 24 | Universal Input | 3 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 24 | Universal Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 24 | Universal Input | 3 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 31 | Universal Input | 4 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 31 | Universal Input | 4 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 31 | Universal Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 31 | Universal Input | 4 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 31 | Universal Input | 4 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 31 | Universal Input | 4 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 31 | Universal Input | 4 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 31 | Universal Input | 4 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 31 | Universal Input | 4 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 31 | Universal Input | 4 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 31 | Universal Input | 4 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 31 | Universal Input | 4 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 31 | Universal Input | 4 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 31 | Universal Input | 4 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 31 | Universal Input | 4 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 31 | Universal Input | 4 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 31 | Universal Input | 4 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 31 | Universal Input | 4 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 31 | Universal Input | 4 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 31 | Universal Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 31 | Universal Input | 4 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 31 | Universal Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 31 | Universal Input | 4 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 31 | Universal Input | 4 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 31 | Universal Input | 4 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 31 | Universal Input | 4 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 31 | Universal Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 31 | Universal Input | 4 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 32 | Universal Input | 4 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 32 | Universal Input | 4 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 32 | Universal Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 32 | Universal Input | 4 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 32 | Universal Input | 4 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 32 | Universal Input | 4 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 32 | Universal Input | 4 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 32 | Universal Input | 4 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 32 | Universal Input | 4 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 32 | Universal Input | 4 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 32 | Universal Input | 4 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 32 | Universal Input | 4 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 32 | Universal Input | 4 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 32 | Universal Input | 4 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 32 | Universal Input | 4 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 32 | Universal Input | 4 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 32 | Universal Input | 4 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 32 | Universal Input | 4 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 32 | Universal Input | 4 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 32 | Universal Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 32 | Universal Input | 4 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 32 | Universal Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 32 | Universal Input | 4 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 32 | Universal Input | 4 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 32 | Universal Input | 4 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 32 | Universal Input | 4 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 32 | Universal Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 32 | Universal Input | 4 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 33 | Universal Input | 4 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 33 | Universal Input | 4 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 33 | Universal Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 33 | Universal Input | 4 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 33 | Universal Input | 4 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 33 | Universal Input | 4 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 33 | Universal Input | 4 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 33 | Universal Input | 4 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 33 | Universal Input | 4 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 33 | Universal Input | 4 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 33 | Universal Input | 4 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 33 | Universal Input | 4 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 33 | Universal Input | 4 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 33 | Universal Input | 4 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 33 | Universal Input | 4 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 33 | Universal Input | 4 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 33 | Universal Input | 4 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 33 | Universal Input | 4 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 33 | Universal Input | 4 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 33 | Universal Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 33 | Universal Input | 4 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 33 | Universal Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 33 | Universal Input | 4 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 33 | Universal Input | 4 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 33 | Universal Input | 4 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 33 | Universal Input | 4 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 33 | Universal Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 33 | Universal Input | 4 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 34 | Universal Input | 4 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 34 | Universal Input | 4 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 34 | Universal Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 34 | Universal Input | 4 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 34 | Universal Input | 4 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 34 | Universal Input | 4 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 34 | Universal Input | 4 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 34 | Universal Input | 4 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 34 | Universal Input | 4 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 34 | Universal Input | 4 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 34 | Universal Input | 4 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 34 | Universal Input | 4 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 34 | Universal Input | 4 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 34 | Universal Input | 4 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 34 | Universal Input | 4 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 34 | Universal Input | 4 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 34 | Universal Input | 4 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 34 | Universal Input | 4 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 34 | Universal Input | 4 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 34 | Universal Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 34 | Universal Input | 4 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 34 | Universal Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 34 | Universal Input | 4 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 34 | Universal Input | 4 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 34 | Universal Input | 4 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 34 | Universal Input | 4 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 34 | Universal Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 34 | Universal Input | 4 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 41 | Universal Input | 5 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 41 | Universal Input | 5 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 41 | Universal Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 41 | Universal Input | 5 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 41 | Universal Input | 5 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 41 | Universal Input | 5 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 41 | Universal Input | 5 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 41 | Universal Input | 5 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 41 | Universal Input | 5 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 41 | Universal Input | 5 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 41 | Universal Input | 5 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 41 | Universal Input | 5 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 41 | Universal Input | 5 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 41 | Universal Input | 5 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 41 | Universal Input | 5 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 41 | Universal Input | 5 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 41 | Universal Input | 5 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 41 | Universal Input | 5 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 41 | Universal Input | 5 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 41 | Universal Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 41 | Universal Input | 5 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 41 | Universal Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 41 | Universal Input | 5 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 41 | Universal Input | 5 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 41 | Universal Input | 5 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 41 | Universal Input | 5 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 41 | Universal Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 41 | Universal Input | 5 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 42 | Universal Input | 5 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 42 | Universal Input | 5 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 42 | Universal Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 42 | Universal Input | 5 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 42 | Universal Input | 5 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 42 | Universal Input | 5 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 42 | Universal Input | 5 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 42 | Universal Input | 5 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 42 | Universal Input | 5 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 42 | Universal Input | 5 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 42 | Universal Input | 5 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 42 | Universal Input | 5 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 42 | Universal Input | 5 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 42 | Universal Input | 5 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 42 | Universal Input | 5 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 42 | Universal Input | 5 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 42 | Universal Input | 5 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 42 | Universal Input | 5 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 42 | Universal Input | 5 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 42 | Universal Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 42 | Universal Input | 5 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 42 | Universal Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 42 | Universal Input | 5 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 42 | Universal Input | 5 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 42 | Universal Input | 5 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 42 | Universal Input | 5 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 42 | Universal Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 42 | Universal Input | 5 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 43 | Universal Input | 5 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 43 | Universal Input | 5 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 43 | Universal Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 43 | Universal Input | 5 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 43 | Universal Input | 5 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 43 | Universal Input | 5 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 43 | Universal Input | 5 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 43 | Universal Input | 5 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 43 | Universal Input | 5 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 43 | Universal Input | 5 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 43 | Universal Input | 5 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 43 | Universal Input | 5 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 43 | Universal Input | 5 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 43 | Universal Input | 5 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 43 | Universal Input | 5 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 43 | Universal Input | 5 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 43 | Universal Input | 5 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 43 | Universal Input | 5 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 43 | Universal Input | 5 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 43 | Universal Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 43 | Universal Input | 5 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 43 | Universal Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 43 | Universal Input | 5 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 43 | Universal Input | 5 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 43 | Universal Input | 5 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 43 | Universal Input | 5 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 43 | Universal Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 43 | Universal Input | 5 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 44 | Universal Input | 5 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 44 | Universal Input | 5 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 44 | Universal Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 44 | Universal Input | 5 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 44 | Universal Input | 5 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 44 | Universal Input | 5 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 44 | Universal Input | 5 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 44 | Universal Input | 5 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 44 | Universal Input | 5 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 44 | Universal Input | 5 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 44 | Universal Input | 5 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 44 | Universal Input | 5 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 44 | Universal Input | 5 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 44 | Universal Input | 5 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 44 | Universal Input | 5 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 44 | Universal Input | 5 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 44 | Universal Input | 5 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 44 | Universal Input | 5 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 44 | Universal Input | 5 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 44 | Universal Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 44 | Universal Input | 5 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 44 | Universal Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 44 | Universal Input | 5 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 44 | Universal Input | 5 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 44 | Universal Input | 5 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 44 | Universal Input | 5 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 44 | Universal Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 44 | Universal Input | 5 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 51 | Universal Input | 6 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 51 | Universal Input | 6 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 51 | Universal Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 51 | Universal Input | 6 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 51 | Universal Input | 6 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 51 | Universal Input | 6 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 51 | Universal Input | 6 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 51 | Universal Input | 6 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 51 | Universal Input | 6 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 51 | Universal Input | 6 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 51 | Universal Input | 6 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 51 | Universal Input | 6 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 51 | Universal Input | 6 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 51 | Universal Input | 6 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 51 | Universal Input | 6 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 51 | Universal Input | 6 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 51 | Universal Input | 6 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 51 | Universal Input | 6 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 51 | Universal Input | 6 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 51 | Universal Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 51 | Universal Input | 6 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 51 | Universal Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 51 | Universal Input | 6 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 51 | Universal Input | 6 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 51 | Universal Input | 6 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 51 | Universal Input | 6 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 51 | Universal Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 51 | Universal Input | 6 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 52 | Universal Input | 6 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 52 | Universal Input | 6 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 52 | Universal Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 52 | Universal Input | 6 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 52 | Universal Input | 6 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 52 | Universal Input | 6 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 52 | Universal Input | 6 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 52 | Universal Input | 6 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 52 | Universal Input | 6 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 52 | Universal Input | 6 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 52 | Universal Input | 6 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 52 | Universal Input | 6 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 52 | Universal Input | 6 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 52 | Universal Input | 6 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 52 | Universal Input | 6 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 52 | Universal Input | 6 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 52 | Universal Input | 6 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 52 | Universal Input | 6 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 52 | Universal Input | 6 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 52 | Universal Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 52 | Universal Input | 6 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 52 | Universal Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 52 | Universal Input | 6 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 52 | Universal Input | 6 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 52 | Universal Input | 6 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 52 | Universal Input | 6 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 52 | Universal Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 52 | Universal Input | 6 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 53 | Universal Input | 6 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 53 | Universal Input | 6 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 53 | Universal Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 53 | Universal Input | 6 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 53 | Universal Input | 6 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 53 | Universal Input | 6 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 53 | Universal Input | 6 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 53 | Universal Input | 6 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 53 | Universal Input | 6 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 53 | Universal Input | 6 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 53 | Universal Input | 6 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 53 | Universal Input | 6 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 53 | Universal Input | 6 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 53 | Universal Input | 6 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 53 | Universal Input | 6 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 53 | Universal Input | 6 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 53 | Universal Input | 6 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 53 | Universal Input | 6 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 53 | Universal Input | 6 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 53 | Universal Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 53 | Universal Input | 6 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 53 | Universal Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 53 | Universal Input | 6 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 53 | Universal Input | 6 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 53 | Universal Input | 6 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 53 | Universal Input | 6 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 53 | Universal Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 53 | Universal Input | 6 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
55001 | 54 | Universal Input | 6 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55002 | 54 | Universal Input | 6 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
55003 | 54 | Universal Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
55004 | 54 | Universal Input | 6 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55005 | 54 | Universal Input | 6 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 60
55006 | 54 | Universal Input | 6 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
55007 | 54 | Universal Input | 6 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 60
55008 | 54 | Universal Input | 6 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55009 | 54 | Universal Input | 6 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 60
55010 | 54 | Universal Input | 6 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55011 | 54 | Universal Input | 6 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 60
55012 | 54 | Universal Input | 6 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 60
55013 | 54 | Universal Input | 6 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 60
55014 | 54 | Universal Input | 6 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
55015 | 54 | Universal Input | 6 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 60
55016 | 54 | Universal Input | 6 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55017 | 54 | Universal Input | 6 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
55018 | 54 | Universal Input | 6 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
55028 | 54 | Universal Input | 6 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
55029 | 54 | Universal Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55030 | 54 | Universal Input | 6 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
55031 | 54 | Universal Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
55035 | 54 | Universal Input | 6 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55036 | 54 | Universal Input | 6 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
55037 | 54 | Universal Input | 6 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55038 | 54 | Universal Input | 6 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
55047 | 54 | Universal Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
55048 | 54 | Universal Input | 6 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 60
56001 | 1 | Thermistor Input | 1 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 1 | Thermistor Input | 1 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 1 | Thermistor Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 1 | Thermistor Input | 1 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 1 | Thermistor Input | 1 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 1 | Thermistor Input | 1 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 1 | Thermistor Input | 1 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 1 | Thermistor Input | 1 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 1 | Thermistor Input | 1 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 1 | Thermistor Input | 1 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 1 | Thermistor Input | 1 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 1 | Thermistor Input | 1 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 1 | Thermistor Input | 1 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 1 | Thermistor Input | 1 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 1 | Thermistor Input | 1 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 1 | Thermistor Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 1 | Thermistor Input | 1 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 1 | Thermistor Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 1 | Thermistor Input | 1 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 1 | Thermistor Input | 1 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 1 | Thermistor Input | 1 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 1 | Thermistor Input | 1 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 1 | Thermistor Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 2 | Thermistor Input | 1 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 2 | Thermistor Input | 1 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 2 | Thermistor Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 2 | Thermistor Input | 1 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 2 | Thermistor Input | 1 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 2 | Thermistor Input | 1 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 2 | Thermistor Input | 1 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 2 | Thermistor Input | 1 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 2 | Thermistor Input | 1 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 2 | Thermistor Input | 1 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 2 | Thermistor Input | 1 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 2 | Thermistor Input | 1 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 2 | Thermistor Input | 1 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 2 | Thermistor Input | 1 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 2 | Thermistor Input | 1 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 2 | Thermistor Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 2 | Thermistor Input | 1 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 2 | Thermistor Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 2 | Thermistor Input | 1 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 2 | Thermistor Input | 1 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 2 | Thermistor Input | 1 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 2 | Thermistor Input | 1 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 2 | Thermistor Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 3 | Thermistor Input | 1 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 3 | Thermistor Input | 1 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 3 | Thermistor Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 3 | Thermistor Input | 1 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 3 | Thermistor Input | 1 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 3 | Thermistor Input | 1 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 3 | Thermistor Input | 1 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 3 | Thermistor Input | 1 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 3 | Thermistor Input | 1 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 3 | Thermistor Input | 1 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 3 | Thermistor Input | 1 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 3 | Thermistor Input | 1 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 3 | Thermistor Input | 1 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 3 | Thermistor Input | 1 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 3 | Thermistor Input | 1 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 3 | Thermistor Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 3 | Thermistor Input | 1 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 3 | Thermistor Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 3 | Thermistor Input | 1 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 3 | Thermistor Input | 1 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 3 | Thermistor Input | 1 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 3 | Thermistor Input | 1 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 3 | Thermistor Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 4 | Thermistor Input | 1 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 4 | Thermistor Input | 1 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 4 | Thermistor Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 4 | Thermistor Input | 1 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 4 | Thermistor Input | 1 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 4 | Thermistor Input | 1 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 4 | Thermistor Input | 1 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 4 | Thermistor Input | 1 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 4 | Thermistor Input | 1 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 4 | Thermistor Input | 1 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 4 | Thermistor Input | 1 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 4 | Thermistor Input | 1 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 4 | Thermistor Input | 1 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 4 | Thermistor Input | 1 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 4 | Thermistor Input | 1 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 4 | Thermistor Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 4 | Thermistor Input | 1 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 4 | Thermistor Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 4 | Thermistor Input | 1 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 4 | Thermistor Input | 1 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 4 | Thermistor Input | 1 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 4 | Thermistor Input | 1 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 4 | Thermistor Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 11 | Thermistor Input | 2 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 11 | Thermistor Input | 2 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 11 | Thermistor Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 11 | Thermistor Input | 2 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 11 | Thermistor Input | 2 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 11 | Thermistor Input | 2 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 11 | Thermistor Input | 2 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 11 | Thermistor Input | 2 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 11 | Thermistor Input | 2 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 11 | Thermistor Input | 2 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 11 | Thermistor Input | 2 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 11 | Thermistor Input | 2 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 11 | Thermistor Input | 2 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 11 | Thermistor Input | 2 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 11 | Thermistor Input | 2 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 11 | Thermistor Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 11 | Thermistor Input | 2 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 11 | Thermistor Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 11 | Thermistor Input | 2 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 11 | Thermistor Input | 2 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 11 | Thermistor Input | 2 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 11 | Thermistor Input | 2 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 11 | Thermistor Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 12 | Thermistor Input | 2 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 12 | Thermistor Input | 2 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 12 | Thermistor Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 12 | Thermistor Input | 2 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 12 | Thermistor Input | 2 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 12 | Thermistor Input | 2 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 12 | Thermistor Input | 2 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 12 | Thermistor Input | 2 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 12 | Thermistor Input | 2 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 12 | Thermistor Input | 2 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 12 | Thermistor Input | 2 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 12 | Thermistor Input | 2 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 12 | Thermistor Input | 2 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 12 | Thermistor Input | 2 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 12 | Thermistor Input | 2 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 12 | Thermistor Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 12 | Thermistor Input | 2 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 12 | Thermistor Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 12 | Thermistor Input | 2 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 12 | Thermistor Input | 2 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 12 | Thermistor Input | 2 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 12 | Thermistor Input | 2 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 12 | Thermistor Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 13 | Thermistor Input | 2 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 13 | Thermistor Input | 2 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 13 | Thermistor Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 13 | Thermistor Input | 2 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 13 | Thermistor Input | 2 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 13 | Thermistor Input | 2 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 13 | Thermistor Input | 2 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 13 | Thermistor Input | 2 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 13 | Thermistor Input | 2 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 13 | Thermistor Input | 2 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 13 | Thermistor Input | 2 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 13 | Thermistor Input | 2 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 13 | Thermistor Input | 2 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 13 | Thermistor Input | 2 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 13 | Thermistor Input | 2 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 13 | Thermistor Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 13 | Thermistor Input | 2 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 13 | Thermistor Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 13 | Thermistor Input | 2 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 13 | Thermistor Input | 2 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 13 | Thermistor Input | 2 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 13 | Thermistor Input | 2 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 13 | Thermistor Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 14 | Thermistor Input | 2 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 14 | Thermistor Input | 2 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 14 | Thermistor Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 14 | Thermistor Input | 2 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 14 | Thermistor Input | 2 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 14 | Thermistor Input | 2 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 14 | Thermistor Input | 2 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 14 | Thermistor Input | 2 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 14 | Thermistor Input | 2 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 14 | Thermistor Input | 2 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 14 | Thermistor Input | 2 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 14 | Thermistor Input | 2 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 14 | Thermistor Input | 2 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 14 | Thermistor Input | 2 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 14 | Thermistor Input | 2 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 14 | Thermistor Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 14 | Thermistor Input | 2 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 14 | Thermistor Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 14 | Thermistor Input | 2 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 14 | Thermistor Input | 2 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 14 | Thermistor Input | 2 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 14 | Thermistor Input | 2 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 14 | Thermistor Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 21 | Thermistor Input | 3 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 21 | Thermistor Input | 3 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 21 | Thermistor Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 21 | Thermistor Input | 3 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 21 | Thermistor Input | 3 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 21 | Thermistor Input | 3 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 21 | Thermistor Input | 3 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 21 | Thermistor Input | 3 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 21 | Thermistor Input | 3 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 21 | Thermistor Input | 3 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 21 | Thermistor Input | 3 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 21 | Thermistor Input | 3 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 21 | Thermistor Input | 3 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 21 | Thermistor Input | 3 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 21 | Thermistor Input | 3 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 21 | Thermistor Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 21 | Thermistor Input | 3 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 21 | Thermistor Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 21 | Thermistor Input | 3 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 21 | Thermistor Input | 3 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 21 | Thermistor Input | 3 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 21 | Thermistor Input | 3 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 21 | Thermistor Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 22 | Thermistor Input | 3 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 22 | Thermistor Input | 3 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 22 | Thermistor Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 22 | Thermistor Input | 3 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 22 | Thermistor Input | 3 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 22 | Thermistor Input | 3 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 22 | Thermistor Input | 3 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 22 | Thermistor Input | 3 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 22 | Thermistor Input | 3 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 22 | Thermistor Input | 3 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 22 | Thermistor Input | 3 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 22 | Thermistor Input | 3 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 22 | Thermistor Input | 3 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 22 | Thermistor Input | 3 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 22 | Thermistor Input | 3 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 22 | Thermistor Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 22 | Thermistor Input | 3 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 22 | Thermistor Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 22 | Thermistor Input | 3 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 22 | Thermistor Input | 3 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 22 | Thermistor Input | 3 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 22 | Thermistor Input | 3 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 22 | Thermistor Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 23 | Thermistor Input | 3 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 23 | Thermistor Input | 3 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 23 | Thermistor Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 23 | Thermistor Input | 3 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 23 | Thermistor Input | 3 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 23 | Thermistor Input | 3 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 23 | Thermistor Input | 3 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 23 | Thermistor Input | 3 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 23 | Thermistor Input | 3 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 23 | Thermistor Input | 3 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 23 | Thermistor Input | 3 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 23 | Thermistor Input | 3 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 23 | Thermistor Input | 3 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 23 | Thermistor Input | 3 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 23 | Thermistor Input | 3 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 23 | Thermistor Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 23 | Thermistor Input | 3 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 23 | Thermistor Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 23 | Thermistor Input | 3 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 23 | Thermistor Input | 3 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 23 | Thermistor Input | 3 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 23 | Thermistor Input | 3 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 23 | Thermistor Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 24 | Thermistor Input | 3 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 24 | Thermistor Input | 3 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 24 | Thermistor Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 24 | Thermistor Input | 3 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 24 | Thermistor Input | 3 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 24 | Thermistor Input | 3 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 24 | Thermistor Input | 3 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 24 | Thermistor Input | 3 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 24 | Thermistor Input | 3 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 24 | Thermistor Input | 3 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 24 | Thermistor Input | 3 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 24 | Thermistor Input | 3 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 24 | Thermistor Input | 3 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 24 | Thermistor Input | 3 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 24 | Thermistor Input | 3 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 24 | Thermistor Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 24 | Thermistor Input | 3 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 24 | Thermistor Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 24 | Thermistor Input | 3 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 24 | Thermistor Input | 3 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 24 | Thermistor Input | 3 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 24 | Thermistor Input | 3 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 24 | Thermistor Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 31 | Thermistor Input | 4 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 31 | Thermistor Input | 4 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 31 | Thermistor Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 31 | Thermistor Input | 4 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 31 | Thermistor Input | 4 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 31 | Thermistor Input | 4 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 31 | Thermistor Input | 4 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 31 | Thermistor Input | 4 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 31 | Thermistor Input | 4 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 31 | Thermistor Input | 4 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 31 | Thermistor Input | 4 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 31 | Thermistor Input | 4 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 31 | Thermistor Input | 4 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 31 | Thermistor Input | 4 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 31 | Thermistor Input | 4 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 31 | Thermistor Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 31 | Thermistor Input | 4 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 31 | Thermistor Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 31 | Thermistor Input | 4 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 31 | Thermistor Input | 4 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 31 | Thermistor Input | 4 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 31 | Thermistor Input | 4 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 31 | Thermistor Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 32 | Thermistor Input | 4 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 32 | Thermistor Input | 4 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 32 | Thermistor Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 32 | Thermistor Input | 4 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 32 | Thermistor Input | 4 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 32 | Thermistor Input | 4 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 32 | Thermistor Input | 4 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 32 | Thermistor Input | 4 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 32 | Thermistor Input | 4 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 32 | Thermistor Input | 4 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 32 | Thermistor Input | 4 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 32 | Thermistor Input | 4 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 32 | Thermistor Input | 4 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 32 | Thermistor Input | 4 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 32 | Thermistor Input | 4 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 32 | Thermistor Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 32 | Thermistor Input | 4 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 32 | Thermistor Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 32 | Thermistor Input | 4 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 32 | Thermistor Input | 4 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 32 | Thermistor Input | 4 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 32 | Thermistor Input | 4 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 32 | Thermistor Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 33 | Thermistor Input | 4 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 33 | Thermistor Input | 4 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 33 | Thermistor Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 33 | Thermistor Input | 4 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 33 | Thermistor Input | 4 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 33 | Thermistor Input | 4 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 33 | Thermistor Input | 4 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 33 | Thermistor Input | 4 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 33 | Thermistor Input | 4 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 33 | Thermistor Input | 4 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 33 | Thermistor Input | 4 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 33 | Thermistor Input | 4 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 33 | Thermistor Input | 4 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 33 | Thermistor Input | 4 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 33 | Thermistor Input | 4 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 33 | Thermistor Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 33 | Thermistor Input | 4 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 33 | Thermistor Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 33 | Thermistor Input | 4 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 33 | Thermistor Input | 4 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 33 | Thermistor Input | 4 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 33 | Thermistor Input | 4 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 33 | Thermistor Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 34 | Thermistor Input | 4 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 34 | Thermistor Input | 4 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 34 | Thermistor Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 34 | Thermistor Input | 4 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 34 | Thermistor Input | 4 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 34 | Thermistor Input | 4 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 34 | Thermistor Input | 4 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 34 | Thermistor Input | 4 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 34 | Thermistor Input | 4 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 34 | Thermistor Input | 4 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 34 | Thermistor Input | 4 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 34 | Thermistor Input | 4 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 34 | Thermistor Input | 4 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 34 | Thermistor Input | 4 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 34 | Thermistor Input | 4 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 34 | Thermistor Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 34 | Thermistor Input | 4 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 34 | Thermistor Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 34 | Thermistor Input | 4 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 34 | Thermistor Input | 4 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 34 | Thermistor Input | 4 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 34 | Thermistor Input | 4 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 34 | Thermistor Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 41 | Thermistor Input | 5 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 41 | Thermistor Input | 5 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 41 | Thermistor Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 41 | Thermistor Input | 5 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 41 | Thermistor Input | 5 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 41 | Thermistor Input | 5 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 41 | Thermistor Input | 5 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 41 | Thermistor Input | 5 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 41 | Thermistor Input | 5 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 41 | Thermistor Input | 5 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 41 | Thermistor Input | 5 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 41 | Thermistor Input | 5 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 41 | Thermistor Input | 5 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 41 | Thermistor Input | 5 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 41 | Thermistor Input | 5 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 41 | Thermistor Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 41 | Thermistor Input | 5 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 41 | Thermistor Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 41 | Thermistor Input | 5 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 41 | Thermistor Input | 5 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 41 | Thermistor Input | 5 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 41 | Thermistor Input | 5 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 41 | Thermistor Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 42 | Thermistor Input | 5 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 42 | Thermistor Input | 5 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 42 | Thermistor Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 42 | Thermistor Input | 5 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 42 | Thermistor Input | 5 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 42 | Thermistor Input | 5 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 42 | Thermistor Input | 5 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 42 | Thermistor Input | 5 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 42 | Thermistor Input | 5 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 42 | Thermistor Input | 5 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 42 | Thermistor Input | 5 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 42 | Thermistor Input | 5 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 42 | Thermistor Input | 5 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 42 | Thermistor Input | 5 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 42 | Thermistor Input | 5 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 42 | Thermistor Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 42 | Thermistor Input | 5 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 42 | Thermistor Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 42 | Thermistor Input | 5 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 42 | Thermistor Input | 5 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 42 | Thermistor Input | 5 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 42 | Thermistor Input | 5 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 42 | Thermistor Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 43 | Thermistor Input | 5 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 43 | Thermistor Input | 5 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 43 | Thermistor Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 43 | Thermistor Input | 5 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 43 | Thermistor Input | 5 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 43 | Thermistor Input | 5 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 43 | Thermistor Input | 5 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 43 | Thermistor Input | 5 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 43 | Thermistor Input | 5 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 43 | Thermistor Input | 5 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 43 | Thermistor Input | 5 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 43 | Thermistor Input | 5 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 43 | Thermistor Input | 5 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 43 | Thermistor Input | 5 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 43 | Thermistor Input | 5 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 43 | Thermistor Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 43 | Thermistor Input | 5 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 43 | Thermistor Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 43 | Thermistor Input | 5 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 43 | Thermistor Input | 5 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 43 | Thermistor Input | 5 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 43 | Thermistor Input | 5 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 43 | Thermistor Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 44 | Thermistor Input | 5 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 44 | Thermistor Input | 5 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 44 | Thermistor Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 44 | Thermistor Input | 5 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 44 | Thermistor Input | 5 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 44 | Thermistor Input | 5 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 44 | Thermistor Input | 5 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 44 | Thermistor Input | 5 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 44 | Thermistor Input | 5 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 44 | Thermistor Input | 5 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 44 | Thermistor Input | 5 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 44 | Thermistor Input | 5 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 44 | Thermistor Input | 5 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 44 | Thermistor Input | 5 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 44 | Thermistor Input | 5 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 44 | Thermistor Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 44 | Thermistor Input | 5 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 44 | Thermistor Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 44 | Thermistor Input | 5 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 44 | Thermistor Input | 5 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 44 | Thermistor Input | 5 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 44 | Thermistor Input | 5 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 44 | Thermistor Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 51 | Thermistor Input | 6 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 51 | Thermistor Input | 6 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 51 | Thermistor Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 51 | Thermistor Input | 6 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 51 | Thermistor Input | 6 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 51 | Thermistor Input | 6 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 51 | Thermistor Input | 6 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 51 | Thermistor Input | 6 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 51 | Thermistor Input | 6 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 51 | Thermistor Input | 6 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 51 | Thermistor Input | 6 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 51 | Thermistor Input | 6 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 51 | Thermistor Input | 6 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 51 | Thermistor Input | 6 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 51 | Thermistor Input | 6 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 51 | Thermistor Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 51 | Thermistor Input | 6 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 51 | Thermistor Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 51 | Thermistor Input | 6 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 51 | Thermistor Input | 6 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 51 | Thermistor Input | 6 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 51 | Thermistor Input | 6 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 51 | Thermistor Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 52 | Thermistor Input | 6 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 52 | Thermistor Input | 6 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 52 | Thermistor Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 52 | Thermistor Input | 6 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 52 | Thermistor Input | 6 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 52 | Thermistor Input | 6 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 52 | Thermistor Input | 6 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 52 | Thermistor Input | 6 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 52 | Thermistor Input | 6 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 52 | Thermistor Input | 6 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 52 | Thermistor Input | 6 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 52 | Thermistor Input | 6 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 52 | Thermistor Input | 6 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 52 | Thermistor Input | 6 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 52 | Thermistor Input | 6 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 52 | Thermistor Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 52 | Thermistor Input | 6 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 52 | Thermistor Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 52 | Thermistor Input | 6 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 52 | Thermistor Input | 6 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 52 | Thermistor Input | 6 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 52 | Thermistor Input | 6 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 52 | Thermistor Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 53 | Thermistor Input | 6 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 53 | Thermistor Input | 6 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 53 | Thermistor Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 53 | Thermistor Input | 6 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 53 | Thermistor Input | 6 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 53 | Thermistor Input | 6 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 53 | Thermistor Input | 6 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 53 | Thermistor Input | 6 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 53 | Thermistor Input | 6 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 53 | Thermistor Input | 6 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 53 | Thermistor Input | 6 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 53 | Thermistor Input | 6 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 53 | Thermistor Input | 6 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 53 | Thermistor Input | 6 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 53 | Thermistor Input | 6 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 53 | Thermistor Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 53 | Thermistor Input | 6 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 53 | Thermistor Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 53 | Thermistor Input | 6 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 53 | Thermistor Input | 6 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 53 | Thermistor Input | 6 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 53 | Thermistor Input | 6 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 53 | Thermistor Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
56001 | 54 | Thermistor Input | 6 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56002 | 54 | Thermistor Input | 6 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
56003 | 54 | Thermistor Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
56004 | 54 | Thermistor Input | 6 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56005 | 54 | Thermistor Input | 6 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 60
56006 | 54 | Thermistor Input | 6 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 60
56007 | 54 | Thermistor Input | 6 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 60
56008 | 54 | Thermistor Input | 6 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 60
56009 | 54 | Thermistor Input | 6 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 60
56010 | 54 | Thermistor Input | 6 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 60
56014 | 54 | Thermistor Input | 6 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
56016 | 54 | Thermistor Input | 6 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56017 | 54 | Thermistor Input | 6 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
56018 | 54 | Thermistor Input | 6 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
56028 | 54 | Thermistor Input | 6 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
56029 | 54 | Thermistor Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56030 | 54 | Thermistor Input | 6 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
56031 | 54 | Thermistor Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
56035 | 54 | Thermistor Input | 6 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56036 | 54 | Thermistor Input | 6 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
56037 | 54 | Thermistor Input | 6 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56038 | 54 | Thermistor Input | 6 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 60
56047 | 54 | Thermistor Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
57001 | 1 | Temperature Input | 1 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57002 | 1 | Temperature Input | 1 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
57003 | 1 | Temperature Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
57004 | 1 | Temperature Input | 1 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57005 | 1 | Temperature Input | 1 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | Enumeration | R/W | 60
57006 | 1 | Temperature Input | 1 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
57007 | 1 | Temperature Input | 1 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | Enumeration | R/W | 60
57014 | 1 | Temperature Input | 1 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
57016 | 1 | Temperature Input | 1 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
57017 | 1 | Temperature Input | 1 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
57018 | 1 | Temperature Input | 1 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
57028 | 1 | Temperature Input | 1 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
57029 | 1 | Temperature Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57030 | 1 | Temperature Input | 1 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
57031 | 1 | Temperature Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57035 | 1 | Temperature Input | 1 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
57047 | 1 | Temperature Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
57001 | 11 | Temperature Input | 2 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57002 | 11 | Temperature Input | 2 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
57003 | 11 | Temperature Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
57004 | 11 | Temperature Input | 2 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57005 | 11 | Temperature Input | 2 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | Enumeration | R/W | 60
57006 | 11 | Temperature Input | 2 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
57007 | 11 | Temperature Input | 2 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | Enumeration | R/W | 60
57014 | 11 | Temperature Input | 2 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
57016 | 11 | Temperature Input | 2 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
57017 | 11 | Temperature Input | 2 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
57018 | 11 | Temperature Input | 2 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
57028 | 11 | Temperature Input | 2 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
57029 | 11 | Temperature Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57030 | 11 | Temperature Input | 2 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
57031 | 11 | Temperature Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57035 | 11 | Temperature Input | 2 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
57047 | 11 | Temperature Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
57001 | 21 | Temperature Input | 3 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57002 | 21 | Temperature Input | 3 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
57003 | 21 | Temperature Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
57004 | 21 | Temperature Input | 3 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57005 | 21 | Temperature Input | 3 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | Enumeration | R/W | 60
57006 | 21 | Temperature Input | 3 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
57007 | 21 | Temperature Input | 3 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | Enumeration | R/W | 60
57014 | 21 | Temperature Input | 3 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
57016 | 21 | Temperature Input | 3 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
57017 | 21 | Temperature Input | 3 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
57018 | 21 | Temperature Input | 3 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
57028 | 21 | Temperature Input | 3 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
57029 | 21 | Temperature Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57030 | 21 | Temperature Input | 3 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
57031 | 21 | Temperature Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57035 | 21 | Temperature Input | 3 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
57047 | 21 | Temperature Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
57001 | 31 | Temperature Input | 4 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57002 | 31 | Temperature Input | 4 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
57003 | 31 | Temperature Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
57004 | 31 | Temperature Input | 4 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57005 | 31 | Temperature Input | 4 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | Enumeration | R/W | 60
57006 | 31 | Temperature Input | 4 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
57007 | 31 | Temperature Input | 4 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | Enumeration | R/W | 60
57014 | 31 | Temperature Input | 4 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
57016 | 31 | Temperature Input | 4 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
57017 | 31 | Temperature Input | 4 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
57018 | 31 | Temperature Input | 4 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
57028 | 31 | Temperature Input | 4 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
57029 | 31 | Temperature Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57030 | 31 | Temperature Input | 4 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
57031 | 31 | Temperature Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57035 | 31 | Temperature Input | 4 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
57047 | 31 | Temperature Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
57001 | 41 | Temperature Input | 5 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57002 | 41 | Temperature Input | 5 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
57003 | 41 | Temperature Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
57004 | 41 | Temperature Input | 5 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57005 | 41 | Temperature Input | 5 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | Enumeration | R/W | 60
57006 | 41 | Temperature Input | 5 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
57007 | 41 | Temperature Input | 5 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | Enumeration | R/W | 60
57014 | 41 | Temperature Input | 5 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
57016 | 41 | Temperature Input | 5 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
57017 | 41 | Temperature Input | 5 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
57018 | 41 | Temperature Input | 5 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
57028 | 41 | Temperature Input | 5 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
57029 | 41 | Temperature Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57030 | 41 | Temperature Input | 5 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
57031 | 41 | Temperature Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57035 | 41 | Temperature Input | 5 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
57047 | 41 | Temperature Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
57001 | 51 | Temperature Input | 6 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57002 | 51 | Temperature Input | 6 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 60
57003 | 51 | Temperature Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 60
57004 | 51 | Temperature Input | 6 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57005 | 51 | Temperature Input | 6 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | Enumeration | R/W | 60
57006 | 51 | Temperature Input | 6 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 60
57007 | 51 | Temperature Input | 6 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | Enumeration | R/W | 60
57014 | 51 | Temperature Input | 6 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 60
57016 | 51 | Temperature Input | 6 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
57017 | 51 | Temperature Input | 6 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 60
57018 | 51 | Temperature Input | 6 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 60
57028 | 51 | Temperature Input | 6 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 60
57029 | 51 | Temperature Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57030 | 51 | Temperature Input | 6 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 60
57031 | 51 | Temperature Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 60
57035 | 51 | Temperature Input | 6 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 60
57047 | 51 | Temperature Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
60001 | 2 | Digital Input | 1 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | Enumeration | R/W | 60
60011 | 2 | Digital Input | 1 | Input State | Monitor input state. | On (63), Off (62) |  | Enumeration | R | 60
60018 | 2 | Digital Input | 1 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
60019 | 2 | Digital Input | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
60001 | 12 | Digital Input | 2 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | Enumeration | R/W | 60
60011 | 12 | Digital Input | 2 | Input State | Monitor input state. | On (63), Off (62) |  | Enumeration | R | 60
60018 | 12 | Digital Input | 2 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
60019 | 12 | Digital Input | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
60001 | 22 | Digital Input | 3 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | Enumeration | R/W | 60
60011 | 22 | Digital Input | 3 | Input State | Monitor input state. | On (63), Off (62) |  | Enumeration | R | 60
60018 | 22 | Digital Input | 3 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
60019 | 22 | Digital Input | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
60001 | 32 | Digital Input | 4 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | Enumeration | R/W | 60
60011 | 32 | Digital Input | 4 | Input State | Monitor input state. | On (63), Off (62) |  | Enumeration | R | 60
60018 | 32 | Digital Input | 4 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
60019 | 32 | Digital Input | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
60001 | 42 | Digital Input | 5 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | Enumeration | R/W | 60
60011 | 42 | Digital Input | 5 | Input State | Monitor input state. | On (63), Off (62) |  | Enumeration | R | 60
60018 | 42 | Digital Input | 5 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
60019 | 42 | Digital Input | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
60001 | 52 | Digital Input | 6 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | Enumeration | R/W | 60
60011 | 52 | Digital Input | 6 | Input State | Monitor input state. | On (63), Off (62) |  | Enumeration | R | 60
60018 | 52 | Digital Input | 6 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
60019 | 52 | Digital Input | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 1 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 1 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 1 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 1 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 1 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 1 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 1 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 1 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 1 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 1 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 1 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 1 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 1 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 1 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 1 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 1 | Digital I/O | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 2 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 2 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 2 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 2 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 2 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 2 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 2 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 2 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 2 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 2 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 2 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 2 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 2 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 2 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 2 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 2 | Digital I/O | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 3 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 3 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 3 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 3 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 3 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 3 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 3 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 3 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 3 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 3 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 3 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 3 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 3 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 3 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 3 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 3 | Digital I/O | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 4 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 4 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 4 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 4 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 4 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 4 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 4 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 4 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 4 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 4 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 4 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 4 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 4 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 4 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 4 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 4 | Digital I/O | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 5 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 5 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 5 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 5 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 5 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 5 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 5 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 5 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 5 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 5 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 5 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 5 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 5 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 5 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 5 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 5 | Digital I/O | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 6 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 6 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 6 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 6 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 6 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 6 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 6 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 6 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 6 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 6 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 6 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 6 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 6 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 6 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 6 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 6 | Digital I/O | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 11 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 11 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 11 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 11 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 11 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 11 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 11 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 11 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 11 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 11 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 11 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 11 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 11 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 11 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 11 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 11 | Digital I/O | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 12 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 12 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 12 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 12 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 12 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 12 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 12 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 12 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 12 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 12 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 12 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 12 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 12 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 12 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 12 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 12 | Digital I/O | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 13 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 13 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 13 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 13 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 13 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 13 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 13 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 13 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 13 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 13 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 13 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 13 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 13 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 13 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 13 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 13 | Digital I/O | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 14 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 14 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 14 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 14 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 14 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 14 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 14 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 14 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 14 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 14 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 14 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 14 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 14 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 14 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 14 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 14 | Digital I/O | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 15 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 15 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 15 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 15 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 15 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 15 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 15 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 15 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 15 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 15 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 15 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 15 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 15 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 15 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 15 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 15 | Digital I/O | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 16 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 16 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 16 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 16 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 16 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 16 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 16 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 16 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 16 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 16 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 16 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 16 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 16 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 16 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 16 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 16 | Digital I/O | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 21 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 21 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 21 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 21 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 21 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 21 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 21 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 21 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 21 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 21 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 21 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 21 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 21 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 21 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 21 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 21 | Digital I/O | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 22 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 22 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 22 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 22 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 22 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 22 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 22 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 22 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 22 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 22 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 22 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 22 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 22 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 22 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 22 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 22 | Digital I/O | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 23 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 23 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 23 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 23 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 23 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 23 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 23 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 23 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 23 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 23 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 23 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 23 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 23 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 23 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 23 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 23 | Digital I/O | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 24 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 24 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 24 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 24 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 24 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 24 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 24 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 24 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 24 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 24 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 24 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 24 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 24 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 24 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 24 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 24 | Digital I/O | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 25 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 25 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 25 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 25 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 25 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 25 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 25 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 25 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 25 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 25 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 25 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 25 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 25 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 25 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 25 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 25 | Digital I/O | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 26 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 26 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 26 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 26 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 26 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 26 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 26 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 26 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 26 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 26 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 26 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 26 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 26 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 26 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 26 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 26 | Digital I/O | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 31 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 31 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 31 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 31 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 31 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 31 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 31 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 31 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 31 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 31 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 31 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 31 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 31 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 31 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 31 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 31 | Digital I/O | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 32 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 32 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 32 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 32 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 32 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 32 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 32 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 32 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 32 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 32 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 32 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 32 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 32 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 32 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 32 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 32 | Digital I/O | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 33 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 33 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 33 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 33 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 33 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 33 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 33 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 33 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 33 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 33 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 33 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 33 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 33 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 33 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 33 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 33 | Digital I/O | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 34 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 34 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 34 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 34 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 34 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 34 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 34 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 34 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 34 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 34 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 34 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 34 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 34 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 34 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 34 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 34 | Digital I/O | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 35 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 35 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 35 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 35 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 35 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 35 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 35 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 35 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 35 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 35 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 35 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 35 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 35 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 35 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 35 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 35 | Digital I/O | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 36 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 36 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 36 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 36 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 36 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 36 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 36 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 36 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 36 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 36 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 36 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 36 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 36 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 36 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 36 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 36 | Digital I/O | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 41 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 41 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 41 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 41 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 41 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 41 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 41 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 41 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 41 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 41 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 41 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 41 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 41 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 41 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 41 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 41 | Digital I/O | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 42 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 42 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 42 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 42 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 42 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 42 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 42 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 42 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 42 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 42 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 42 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 42 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 42 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 42 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 42 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 42 | Digital I/O | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 43 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 43 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 43 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 43 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 43 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 43 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 43 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 43 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 43 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 43 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 43 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 43 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 43 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 43 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 43 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 43 | Digital I/O | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 44 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 44 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 44 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 44 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 44 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 44 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 44 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 44 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 44 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 44 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 44 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 44 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 44 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 44 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 44 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 44 | Digital I/O | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 45 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 45 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 45 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 45 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 45 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 45 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 45 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 45 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 45 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 45 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 45 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 45 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 45 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 45 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 45 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 45 | Digital I/O | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 46 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 46 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 46 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 46 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 46 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 46 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 46 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 46 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 46 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 46 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 46 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 46 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 46 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 46 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 46 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 46 | Digital I/O | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 51 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 51 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 51 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 51 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 51 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 51 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 51 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 51 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 51 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 51 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 51 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 51 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 51 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 51 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 51 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 51 | Digital I/O | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 52 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 52 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 52 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 52 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 52 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 52 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 52 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 52 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 52 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 52 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 52 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 52 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 52 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 52 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 52 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 52 | Digital I/O | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 53 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 53 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 53 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 53 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 53 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 53 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 53 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 53 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 53 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 53 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 53 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 53 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 53 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 53 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 53 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 53 | Digital I/O | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 54 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 54 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 54 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 54 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 54 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 54 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 54 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 54 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 54 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 54 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 54 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 54 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 54 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 54 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 54 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 54 | Digital I/O | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 55 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 55 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 55 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 55 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 55 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 55 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 55 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 55 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 55 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 55 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 55 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 55 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 55 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 55 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 55 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 55 | Digital I/O | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
61001 | 56 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 60
61002 | 56 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
61003 | 56 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
61004 | 56 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
61005 | 56 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
61006 | 56 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
61007 | 56 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
61008 | 56 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
61009 | 56 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
61010 | 56 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
61011 | 56 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 60
61012 | 56 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
61013 | 56 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
61015 | 56 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
61018 | 56 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 60
61019 | 56 | Digital I/O | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62002 | 1 | Digital Output Fast | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 1 | Digital Output Fast | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 1 | Digital Output Fast | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 1 | Digital Output Fast | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 1 | Digital Output Fast | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 1 | Digital Output Fast | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 1 | Digital Output Fast | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 1 | Digital Output Fast | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 1 | Digital Output Fast | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 1 | Digital Output Fast | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 1 | Digital Output Fast | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 1 | Digital Output Fast | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 1 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 1 | Digital Output Fast | 1 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 2 | Digital Output Fast | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 2 | Digital Output Fast | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 2 | Digital Output Fast | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 2 | Digital Output Fast | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 2 | Digital Output Fast | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 2 | Digital Output Fast | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 2 | Digital Output Fast | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 2 | Digital Output Fast | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 2 | Digital Output Fast | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 2 | Digital Output Fast | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 2 | Digital Output Fast | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 2 | Digital Output Fast | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 2 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 2 | Digital Output Fast | 1 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 3 | Digital Output Fast | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 3 | Digital Output Fast | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 3 | Digital Output Fast | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 3 | Digital Output Fast | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 3 | Digital Output Fast | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 3 | Digital Output Fast | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 3 | Digital Output Fast | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 3 | Digital Output Fast | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 3 | Digital Output Fast | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 3 | Digital Output Fast | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 3 | Digital Output Fast | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 3 | Digital Output Fast | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 3 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 3 | Digital Output Fast | 1 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 4 | Digital Output Fast | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 4 | Digital Output Fast | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 4 | Digital Output Fast | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 4 | Digital Output Fast | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 4 | Digital Output Fast | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 4 | Digital Output Fast | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 4 | Digital Output Fast | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 4 | Digital Output Fast | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 4 | Digital Output Fast | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 4 | Digital Output Fast | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 4 | Digital Output Fast | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 4 | Digital Output Fast | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 4 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 4 | Digital Output Fast | 1 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 11 | Digital Output Fast | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 11 | Digital Output Fast | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 11 | Digital Output Fast | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 11 | Digital Output Fast | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 11 | Digital Output Fast | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 11 | Digital Output Fast | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 11 | Digital Output Fast | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 11 | Digital Output Fast | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 11 | Digital Output Fast | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 11 | Digital Output Fast | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 11 | Digital Output Fast | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 11 | Digital Output Fast | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 11 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 11 | Digital Output Fast | 2 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 12 | Digital Output Fast | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 12 | Digital Output Fast | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 12 | Digital Output Fast | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 12 | Digital Output Fast | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 12 | Digital Output Fast | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 12 | Digital Output Fast | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 12 | Digital Output Fast | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 12 | Digital Output Fast | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 12 | Digital Output Fast | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 12 | Digital Output Fast | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 12 | Digital Output Fast | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 12 | Digital Output Fast | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 12 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 12 | Digital Output Fast | 2 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 13 | Digital Output Fast | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 13 | Digital Output Fast | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 13 | Digital Output Fast | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 13 | Digital Output Fast | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 13 | Digital Output Fast | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 13 | Digital Output Fast | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 13 | Digital Output Fast | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 13 | Digital Output Fast | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 13 | Digital Output Fast | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 13 | Digital Output Fast | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 13 | Digital Output Fast | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 13 | Digital Output Fast | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 13 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 13 | Digital Output Fast | 2 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 14 | Digital Output Fast | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 14 | Digital Output Fast | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 14 | Digital Output Fast | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 14 | Digital Output Fast | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 14 | Digital Output Fast | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 14 | Digital Output Fast | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 14 | Digital Output Fast | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 14 | Digital Output Fast | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 14 | Digital Output Fast | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 14 | Digital Output Fast | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 14 | Digital Output Fast | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 14 | Digital Output Fast | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 14 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 14 | Digital Output Fast | 2 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 21 | Digital Output Fast | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 21 | Digital Output Fast | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 21 | Digital Output Fast | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 21 | Digital Output Fast | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 21 | Digital Output Fast | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 21 | Digital Output Fast | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 21 | Digital Output Fast | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 21 | Digital Output Fast | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 21 | Digital Output Fast | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 21 | Digital Output Fast | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 21 | Digital Output Fast | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 21 | Digital Output Fast | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 21 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 21 | Digital Output Fast | 3 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 22 | Digital Output Fast | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 22 | Digital Output Fast | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 22 | Digital Output Fast | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 22 | Digital Output Fast | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 22 | Digital Output Fast | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 22 | Digital Output Fast | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 22 | Digital Output Fast | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 22 | Digital Output Fast | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 22 | Digital Output Fast | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 22 | Digital Output Fast | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 22 | Digital Output Fast | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 22 | Digital Output Fast | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 22 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 22 | Digital Output Fast | 3 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 23 | Digital Output Fast | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 23 | Digital Output Fast | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 23 | Digital Output Fast | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 23 | Digital Output Fast | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 23 | Digital Output Fast | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 23 | Digital Output Fast | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 23 | Digital Output Fast | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 23 | Digital Output Fast | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 23 | Digital Output Fast | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 23 | Digital Output Fast | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 23 | Digital Output Fast | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 23 | Digital Output Fast | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 23 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 23 | Digital Output Fast | 3 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 24 | Digital Output Fast | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 24 | Digital Output Fast | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 24 | Digital Output Fast | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 24 | Digital Output Fast | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 24 | Digital Output Fast | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 24 | Digital Output Fast | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 24 | Digital Output Fast | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 24 | Digital Output Fast | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 24 | Digital Output Fast | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 24 | Digital Output Fast | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 24 | Digital Output Fast | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 24 | Digital Output Fast | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 24 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 24 | Digital Output Fast | 3 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 31 | Digital Output Fast | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 31 | Digital Output Fast | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 31 | Digital Output Fast | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 31 | Digital Output Fast | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 31 | Digital Output Fast | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 31 | Digital Output Fast | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 31 | Digital Output Fast | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 31 | Digital Output Fast | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 31 | Digital Output Fast | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 31 | Digital Output Fast | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 31 | Digital Output Fast | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 31 | Digital Output Fast | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 31 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 31 | Digital Output Fast | 4 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 32 | Digital Output Fast | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 32 | Digital Output Fast | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 32 | Digital Output Fast | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 32 | Digital Output Fast | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 32 | Digital Output Fast | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 32 | Digital Output Fast | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 32 | Digital Output Fast | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 32 | Digital Output Fast | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 32 | Digital Output Fast | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 32 | Digital Output Fast | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 32 | Digital Output Fast | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 32 | Digital Output Fast | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 32 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 32 | Digital Output Fast | 4 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 33 | Digital Output Fast | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 33 | Digital Output Fast | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 33 | Digital Output Fast | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 33 | Digital Output Fast | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 33 | Digital Output Fast | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 33 | Digital Output Fast | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 33 | Digital Output Fast | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 33 | Digital Output Fast | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 33 | Digital Output Fast | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 33 | Digital Output Fast | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 33 | Digital Output Fast | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 33 | Digital Output Fast | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 33 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 33 | Digital Output Fast | 4 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 34 | Digital Output Fast | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 34 | Digital Output Fast | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 34 | Digital Output Fast | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 34 | Digital Output Fast | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 34 | Digital Output Fast | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 34 | Digital Output Fast | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 34 | Digital Output Fast | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 34 | Digital Output Fast | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 34 | Digital Output Fast | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 34 | Digital Output Fast | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 34 | Digital Output Fast | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 34 | Digital Output Fast | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 34 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 34 | Digital Output Fast | 4 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 41 | Digital Output Fast | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 41 | Digital Output Fast | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 41 | Digital Output Fast | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 41 | Digital Output Fast | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 41 | Digital Output Fast | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 41 | Digital Output Fast | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 41 | Digital Output Fast | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 41 | Digital Output Fast | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 41 | Digital Output Fast | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 41 | Digital Output Fast | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 41 | Digital Output Fast | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 41 | Digital Output Fast | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 41 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 41 | Digital Output Fast | 5 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 42 | Digital Output Fast | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 42 | Digital Output Fast | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 42 | Digital Output Fast | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 42 | Digital Output Fast | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 42 | Digital Output Fast | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 42 | Digital Output Fast | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 42 | Digital Output Fast | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 42 | Digital Output Fast | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 42 | Digital Output Fast | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 42 | Digital Output Fast | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 42 | Digital Output Fast | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 42 | Digital Output Fast | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 42 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 42 | Digital Output Fast | 5 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 43 | Digital Output Fast | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 43 | Digital Output Fast | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 43 | Digital Output Fast | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 43 | Digital Output Fast | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 43 | Digital Output Fast | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 43 | Digital Output Fast | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 43 | Digital Output Fast | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 43 | Digital Output Fast | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 43 | Digital Output Fast | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 43 | Digital Output Fast | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 43 | Digital Output Fast | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 43 | Digital Output Fast | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 43 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 43 | Digital Output Fast | 5 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 44 | Digital Output Fast | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 44 | Digital Output Fast | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 44 | Digital Output Fast | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 44 | Digital Output Fast | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 44 | Digital Output Fast | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 44 | Digital Output Fast | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 44 | Digital Output Fast | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 44 | Digital Output Fast | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 44 | Digital Output Fast | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 44 | Digital Output Fast | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 44 | Digital Output Fast | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 44 | Digital Output Fast | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 44 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 44 | Digital Output Fast | 5 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 51 | Digital Output Fast | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 51 | Digital Output Fast | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 51 | Digital Output Fast | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 51 | Digital Output Fast | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 51 | Digital Output Fast | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 51 | Digital Output Fast | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 51 | Digital Output Fast | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 51 | Digital Output Fast | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 51 | Digital Output Fast | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 51 | Digital Output Fast | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 51 | Digital Output Fast | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 51 | Digital Output Fast | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 51 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 51 | Digital Output Fast | 6 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 52 | Digital Output Fast | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 52 | Digital Output Fast | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 52 | Digital Output Fast | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 52 | Digital Output Fast | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 52 | Digital Output Fast | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 52 | Digital Output Fast | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 52 | Digital Output Fast | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 52 | Digital Output Fast | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 52 | Digital Output Fast | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 52 | Digital Output Fast | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 52 | Digital Output Fast | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 52 | Digital Output Fast | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 52 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 52 | Digital Output Fast | 6 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 53 | Digital Output Fast | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 53 | Digital Output Fast | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 53 | Digital Output Fast | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 53 | Digital Output Fast | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 53 | Digital Output Fast | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 53 | Digital Output Fast | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 53 | Digital Output Fast | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 53 | Digital Output Fast | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 53 | Digital Output Fast | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 53 | Digital Output Fast | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 53 | Digital Output Fast | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 53 | Digital Output Fast | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 53 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 53 | Digital Output Fast | 6 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
62002 | 54 | Digital Output Fast | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 60
62003 | 54 | Digital Output Fast | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 60
62004 | 54 | Digital Output Fast | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 60
62005 | 54 | Digital Output Fast | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
62006 | 54 | Digital Output Fast | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
62007 | 54 | Digital Output Fast | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
62008 | 54 | Digital Output Fast | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
62009 | 54 | Digital Output Fast | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
62010 | 54 | Digital Output Fast | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
62012 | 54 | Digital Output Fast | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
62013 | 54 | Digital Output Fast | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
62015 | 54 | Digital Output Fast | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
62019 | 54 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
62020 | 54 | Digital Output Fast | 6 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 60
63005 | 1 | Digital Output Limit | 1 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 60
63006 | 1 | Digital Output Limit | 1 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 60
63007 | 1 | Digital Output Limit | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
63012 | 1 | Digital Output Limit | 1 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
63013 | 1 | Digital Output Limit | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
63015 | 1 | Digital Output Limit | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
63019 | 1 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
63020 | 1 | Digital Output Limit | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 60
63005 | 2 | Digital Output Limit | 1 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 60
63006 | 2 | Digital Output Limit | 1 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 60
63007 | 2 | Digital Output Limit | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
63012 | 2 | Digital Output Limit | 1 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
63013 | 2 | Digital Output Limit | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
63015 | 2 | Digital Output Limit | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
63019 | 2 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
63020 | 2 | Digital Output Limit | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 60
63005 | 11 | Digital Output Limit | 2 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 60
63006 | 11 | Digital Output Limit | 2 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 60
63007 | 11 | Digital Output Limit | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
63012 | 11 | Digital Output Limit | 2 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
63013 | 11 | Digital Output Limit | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
63015 | 11 | Digital Output Limit | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
63019 | 11 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
63020 | 11 | Digital Output Limit | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 60
63005 | 12 | Digital Output Limit | 2 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 60
63006 | 12 | Digital Output Limit | 2 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 60
63007 | 12 | Digital Output Limit | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
63012 | 12 | Digital Output Limit | 2 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
63013 | 12 | Digital Output Limit | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
63015 | 12 | Digital Output Limit | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
63019 | 12 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
63020 | 12 | Digital Output Limit | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 60
63005 | 21 | Digital Output Limit | 3 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 60
63006 | 21 | Digital Output Limit | 3 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 60
63007 | 21 | Digital Output Limit | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
63012 | 21 | Digital Output Limit | 3 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
63013 | 21 | Digital Output Limit | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
63015 | 21 | Digital Output Limit | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
63019 | 21 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
63020 | 21 | Digital Output Limit | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 60
63005 | 22 | Digital Output Limit | 3 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 60
63006 | 22 | Digital Output Limit | 3 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 60
63007 | 22 | Digital Output Limit | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
63012 | 22 | Digital Output Limit | 3 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
63013 | 22 | Digital Output Limit | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
63015 | 22 | Digital Output Limit | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
63019 | 22 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
63020 | 22 | Digital Output Limit | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 60
63005 | 31 | Digital Output Limit | 4 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 60
63006 | 31 | Digital Output Limit | 4 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 60
63007 | 31 | Digital Output Limit | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
63012 | 31 | Digital Output Limit | 4 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
63013 | 31 | Digital Output Limit | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
63015 | 31 | Digital Output Limit | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
63019 | 31 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
63020 | 31 | Digital Output Limit | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 60
63005 | 32 | Digital Output Limit | 4 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 60
63006 | 32 | Digital Output Limit | 4 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 60
63007 | 32 | Digital Output Limit | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
63012 | 32 | Digital Output Limit | 4 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
63013 | 32 | Digital Output Limit | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
63015 | 32 | Digital Output Limit | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
63019 | 32 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
63020 | 32 | Digital Output Limit | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 60
63005 | 41 | Digital Output Limit | 5 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 60
63006 | 41 | Digital Output Limit | 5 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 60
63007 | 41 | Digital Output Limit | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
63012 | 41 | Digital Output Limit | 5 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
63013 | 41 | Digital Output Limit | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
63015 | 41 | Digital Output Limit | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
63019 | 41 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
63020 | 41 | Digital Output Limit | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 60
63005 | 42 | Digital Output Limit | 5 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 60
63006 | 42 | Digital Output Limit | 5 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 60
63007 | 42 | Digital Output Limit | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
63012 | 42 | Digital Output Limit | 5 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
63013 | 42 | Digital Output Limit | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
63015 | 42 | Digital Output Limit | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
63019 | 42 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
63020 | 42 | Digital Output Limit | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 60
63005 | 51 | Digital Output Limit | 6 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 60
63006 | 51 | Digital Output Limit | 6 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 60
63007 | 51 | Digital Output Limit | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
63012 | 51 | Digital Output Limit | 6 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
63013 | 51 | Digital Output Limit | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
63015 | 51 | Digital Output Limit | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
63019 | 51 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
63020 | 51 | Digital Output Limit | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 60
63005 | 52 | Digital Output Limit | 6 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 60
63006 | 52 | Digital Output Limit | 6 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 60
63007 | 52 | Digital Output Limit | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
63012 | 52 | Digital Output Limit | 6 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 60
63013 | 52 | Digital Output Limit | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
63015 | 52 | Digital Output Limit | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
63019 | 52 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
63020 | 52 | Digital Output Limit | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 60
64002 | 1 | Digital Output Slow | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 1 | Digital Output Slow | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 1 | Digital Output Slow | 1 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 1 | Digital Output Slow | 1 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 1 | Digital Output Slow | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 1 | Digital Output Slow | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 1 | Digital Output Slow | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 1 | Digital Output Slow | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 1 | Digital Output Slow | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 1 | Digital Output Slow | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 1 | Digital Output Slow | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 1 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 1 | Digital Output Slow | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 2 | Digital Output Slow | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 2 | Digital Output Slow | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 2 | Digital Output Slow | 1 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 2 | Digital Output Slow | 1 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 2 | Digital Output Slow | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 2 | Digital Output Slow | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 2 | Digital Output Slow | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 2 | Digital Output Slow | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 2 | Digital Output Slow | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 2 | Digital Output Slow | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 2 | Digital Output Slow | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 2 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 2 | Digital Output Slow | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 3 | Digital Output Slow | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 3 | Digital Output Slow | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 3 | Digital Output Slow | 1 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 3 | Digital Output Slow | 1 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 3 | Digital Output Slow | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 3 | Digital Output Slow | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 3 | Digital Output Slow | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 3 | Digital Output Slow | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 3 | Digital Output Slow | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 3 | Digital Output Slow | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 3 | Digital Output Slow | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 3 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 3 | Digital Output Slow | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 4 | Digital Output Slow | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 4 | Digital Output Slow | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 4 | Digital Output Slow | 1 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 4 | Digital Output Slow | 1 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 4 | Digital Output Slow | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 4 | Digital Output Slow | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 4 | Digital Output Slow | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 4 | Digital Output Slow | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 4 | Digital Output Slow | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 4 | Digital Output Slow | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 4 | Digital Output Slow | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 4 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 4 | Digital Output Slow | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 11 | Digital Output Slow | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 11 | Digital Output Slow | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 11 | Digital Output Slow | 2 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 11 | Digital Output Slow | 2 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 11 | Digital Output Slow | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 11 | Digital Output Slow | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 11 | Digital Output Slow | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 11 | Digital Output Slow | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 11 | Digital Output Slow | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 11 | Digital Output Slow | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 11 | Digital Output Slow | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 11 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 11 | Digital Output Slow | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 12 | Digital Output Slow | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 12 | Digital Output Slow | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 12 | Digital Output Slow | 2 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 12 | Digital Output Slow | 2 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 12 | Digital Output Slow | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 12 | Digital Output Slow | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 12 | Digital Output Slow | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 12 | Digital Output Slow | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 12 | Digital Output Slow | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 12 | Digital Output Slow | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 12 | Digital Output Slow | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 12 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 12 | Digital Output Slow | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 13 | Digital Output Slow | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 13 | Digital Output Slow | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 13 | Digital Output Slow | 2 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 13 | Digital Output Slow | 2 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 13 | Digital Output Slow | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 13 | Digital Output Slow | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 13 | Digital Output Slow | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 13 | Digital Output Slow | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 13 | Digital Output Slow | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 13 | Digital Output Slow | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 13 | Digital Output Slow | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 13 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 13 | Digital Output Slow | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 14 | Digital Output Slow | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 14 | Digital Output Slow | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 14 | Digital Output Slow | 2 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 14 | Digital Output Slow | 2 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 14 | Digital Output Slow | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 14 | Digital Output Slow | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 14 | Digital Output Slow | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 14 | Digital Output Slow | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 14 | Digital Output Slow | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 14 | Digital Output Slow | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 14 | Digital Output Slow | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 14 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 14 | Digital Output Slow | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 21 | Digital Output Slow | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 21 | Digital Output Slow | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 21 | Digital Output Slow | 3 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 21 | Digital Output Slow | 3 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 21 | Digital Output Slow | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 21 | Digital Output Slow | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 21 | Digital Output Slow | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 21 | Digital Output Slow | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 21 | Digital Output Slow | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 21 | Digital Output Slow | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 21 | Digital Output Slow | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 21 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 21 | Digital Output Slow | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 22 | Digital Output Slow | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 22 | Digital Output Slow | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 22 | Digital Output Slow | 3 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 22 | Digital Output Slow | 3 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 22 | Digital Output Slow | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 22 | Digital Output Slow | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 22 | Digital Output Slow | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 22 | Digital Output Slow | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 22 | Digital Output Slow | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 22 | Digital Output Slow | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 22 | Digital Output Slow | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 22 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 22 | Digital Output Slow | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 23 | Digital Output Slow | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 23 | Digital Output Slow | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 23 | Digital Output Slow | 3 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 23 | Digital Output Slow | 3 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 23 | Digital Output Slow | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 23 | Digital Output Slow | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 23 | Digital Output Slow | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 23 | Digital Output Slow | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 23 | Digital Output Slow | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 23 | Digital Output Slow | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 23 | Digital Output Slow | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 23 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 23 | Digital Output Slow | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 24 | Digital Output Slow | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 24 | Digital Output Slow | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 24 | Digital Output Slow | 3 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 24 | Digital Output Slow | 3 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 24 | Digital Output Slow | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 24 | Digital Output Slow | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 24 | Digital Output Slow | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 24 | Digital Output Slow | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 24 | Digital Output Slow | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 24 | Digital Output Slow | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 24 | Digital Output Slow | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 24 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 24 | Digital Output Slow | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 31 | Digital Output Slow | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 31 | Digital Output Slow | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 31 | Digital Output Slow | 4 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 31 | Digital Output Slow | 4 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 31 | Digital Output Slow | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 31 | Digital Output Slow | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 31 | Digital Output Slow | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 31 | Digital Output Slow | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 31 | Digital Output Slow | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 31 | Digital Output Slow | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 31 | Digital Output Slow | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 31 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 31 | Digital Output Slow | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 32 | Digital Output Slow | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 32 | Digital Output Slow | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 32 | Digital Output Slow | 4 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 32 | Digital Output Slow | 4 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 32 | Digital Output Slow | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 32 | Digital Output Slow | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 32 | Digital Output Slow | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 32 | Digital Output Slow | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 32 | Digital Output Slow | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 32 | Digital Output Slow | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 32 | Digital Output Slow | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 32 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 32 | Digital Output Slow | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 33 | Digital Output Slow | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 33 | Digital Output Slow | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 33 | Digital Output Slow | 4 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 33 | Digital Output Slow | 4 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 33 | Digital Output Slow | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 33 | Digital Output Slow | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 33 | Digital Output Slow | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 33 | Digital Output Slow | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 33 | Digital Output Slow | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 33 | Digital Output Slow | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 33 | Digital Output Slow | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 33 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 33 | Digital Output Slow | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 34 | Digital Output Slow | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 34 | Digital Output Slow | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 34 | Digital Output Slow | 4 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 34 | Digital Output Slow | 4 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 34 | Digital Output Slow | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 34 | Digital Output Slow | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 34 | Digital Output Slow | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 34 | Digital Output Slow | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 34 | Digital Output Slow | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 34 | Digital Output Slow | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 34 | Digital Output Slow | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 34 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 34 | Digital Output Slow | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 41 | Digital Output Slow | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 41 | Digital Output Slow | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 41 | Digital Output Slow | 5 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 41 | Digital Output Slow | 5 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 41 | Digital Output Slow | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 41 | Digital Output Slow | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 41 | Digital Output Slow | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 41 | Digital Output Slow | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 41 | Digital Output Slow | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 41 | Digital Output Slow | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 41 | Digital Output Slow | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 41 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 41 | Digital Output Slow | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 42 | Digital Output Slow | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 42 | Digital Output Slow | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 42 | Digital Output Slow | 5 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 42 | Digital Output Slow | 5 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 42 | Digital Output Slow | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 42 | Digital Output Slow | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 42 | Digital Output Slow | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 42 | Digital Output Slow | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 42 | Digital Output Slow | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 42 | Digital Output Slow | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 42 | Digital Output Slow | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 42 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 42 | Digital Output Slow | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 43 | Digital Output Slow | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 43 | Digital Output Slow | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 43 | Digital Output Slow | 5 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 43 | Digital Output Slow | 5 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 43 | Digital Output Slow | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 43 | Digital Output Slow | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 43 | Digital Output Slow | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 43 | Digital Output Slow | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 43 | Digital Output Slow | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 43 | Digital Output Slow | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 43 | Digital Output Slow | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 43 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 43 | Digital Output Slow | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 44 | Digital Output Slow | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 44 | Digital Output Slow | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 44 | Digital Output Slow | 5 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 44 | Digital Output Slow | 5 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 44 | Digital Output Slow | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 44 | Digital Output Slow | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 44 | Digital Output Slow | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 44 | Digital Output Slow | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 44 | Digital Output Slow | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 44 | Digital Output Slow | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 44 | Digital Output Slow | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 44 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 44 | Digital Output Slow | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 51 | Digital Output Slow | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 51 | Digital Output Slow | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 51 | Digital Output Slow | 6 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 51 | Digital Output Slow | 6 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 51 | Digital Output Slow | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 51 | Digital Output Slow | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 51 | Digital Output Slow | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 51 | Digital Output Slow | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 51 | Digital Output Slow | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 51 | Digital Output Slow | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 51 | Digital Output Slow | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 51 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 51 | Digital Output Slow | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 52 | Digital Output Slow | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 52 | Digital Output Slow | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 52 | Digital Output Slow | 6 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 52 | Digital Output Slow | 6 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 52 | Digital Output Slow | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 52 | Digital Output Slow | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 52 | Digital Output Slow | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 52 | Digital Output Slow | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 52 | Digital Output Slow | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 52 | Digital Output Slow | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 52 | Digital Output Slow | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 52 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 52 | Digital Output Slow | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 53 | Digital Output Slow | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 53 | Digital Output Slow | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 53 | Digital Output Slow | 6 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 53 | Digital Output Slow | 6 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 53 | Digital Output Slow | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 53 | Digital Output Slow | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 53 | Digital Output Slow | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 53 | Digital Output Slow | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 53 | Digital Output Slow | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 53 | Digital Output Slow | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 53 | Digital Output Slow | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 53 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 53 | Digital Output Slow | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
64002 | 54 | Digital Output Slow | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 60
64003 | 54 | Digital Output Slow | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 60
64005 | 54 | Digital Output Slow | 6 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 60
64006 | 54 | Digital Output Slow | 6 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 60
64007 | 54 | Digital Output Slow | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 60
64008 | 54 | Digital Output Slow | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 60
64009 | 54 | Digital Output Slow | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 60
64010 | 54 | Digital Output Slow | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 60
64012 | 54 | Digital Output Slow | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 60
64013 | 54 | Digital Output Slow | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 60
64015 | 54 | Digital Output Slow | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 60
64019 | 54 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 60
64020 | 54 | Digital Output Slow | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 60
69001 | 1 | Modbus | 6 | Display Units | Set the units for temperature measurement via comms. | F (30), C (15) | F (30) | Enumeration | R/W | 1
69002 | 1 | Modbus | 6 | Non-Volatile Save | Set to save/not save changes via comms. | No (59), Yes (106) | No (59) | Enumeration | R/W | 1
69003 | 1 | Modbus | 6 | Baud Rate | Set the baud rate to match device connected. | 9600 (188), 19200 (189), 38400 (190) | 9600 (188) | Enumeration | R/W | 1
69004 | 1 | Modbus | 6 | Parity | Set the parity to match device connected. | None (61), Even (191), Odd (192) | None (61) | Enumeration | R/W | 1
69005 | 1 | Modbus | 6 | Modbus Address | Set the Modbus ID for unique number on network. | 1 to 247 | 1 | Unsigned 8-bit | R/W | 1
69007 | 1 | Modbus | 6 | Modbus Word Order | Set the Modbus Word Order. | High Low (1330), Low High (1331) | Low High (1331) | Enumeration | R/W | 1
69008 | 1 | Modbus | 6 | Data Map | Set which Modbus mapping to apply. | 1 to 2 | 1 | Unsigned 8-bit | R/W | 1
70001 | 1 | Ethernet | Base | Display Units | Set the units for temperature measurement via comms. | F (30), C (15) | F (30) | Enumeration | R/W | 1
70002 | 1 | Ethernet | Base | Non-Volatile Save | Set to save/not save changes via comms. | No (59), Yes (106) | No (59) | Enumeration | R/W | 1
70003 | 1 | Ethernet | Base | Modbus TCP Enable | Set to enable Modbus TCP protocol communications. | No (59), Yes (106) | Yes (106) | Enumeration | R/W | 1
70004 | 1 | Ethernet | Base | Modbus Word Order | Set the Modbus Word Order. | High Low (1330), Low High (1331) | Low High (1331) | Enumeration | R/W | 1
70005 | 1 | Ethernet | Base | EtherNet/IP Enable | Set to enable EtherNet/IP protocol communications. | No (59), Yes (106) | Yes (106) | Enumeration | R/W | 1
70006 | 1 | Ethernet | Base | Data Map | Set which Modbus mapping to apply. | 1 to 2 | 1 | Unsigned 8-bit | R/W | 1
70016 | 1 | Ethernet | Base | IP Address Mode | Set for IP address assignment method. | DHCP (1281), Fixed (1284) | DHCP (1281) | Enumeration | R/W | 1
70017 | 1 | Ethernet | Base | IP Fixed Address Part 1 | Set the IP address of this module when fixed. | 0 to 255 | 192 | Unsigned 8-bit | R/W | 1
70018 | 1 | Ethernet | Base | IP Fixed Address Part 2 | Set the IP address of this module when fixed. | 0 to 255 | 168 | Unsigned 8-bit | R/W | 1
70019 | 1 | Ethernet | Base | IP Fixed Address Part 3 | Set the IP address of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 1
70020 | 1 | Ethernet | Base | IP Fixed Address Part 4 | Set the IP address of this module when fixed. | 0 to 255 | 222 | Unsigned 8-bit | R/W | 1
70021 | 1 | Ethernet | Base | IP Fixed Address Part 5 | Set the IP address of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 1
70022 | 1 | Ethernet | Base | IP Fixed Address Part 6 | Set the IP address of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 1
70023 | 1 | Ethernet | Base | IP Fixed Subnet Part 1 | Set the IP address subnet of this module when fixed. | 0 to 255 | 255 | Unsigned 8-bit | R/W | 1
70024 | 1 | Ethernet | Base | IP Fixed Subnet Part 2 | Set the IP address subnet of this module when fixed. | 0 to 255 | 255 | Unsigned 8-bit | R/W | 1
70025 | 1 | Ethernet | Base | IP Fixed Subnet Part 3 | Set the IP address subnet of this module when fixed. | 0 to 255 | 255 | Unsigned 8-bit | R/W | 1
70026 | 1 | Ethernet | Base | IP Fixed Subnet Part 4 | Set the IP address subnet of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 1
70027 | 1 | Ethernet | Base | IP Fixed Subnet Part 5 | Set the IP address subnet of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 1
70028 | 1 | Ethernet | Base | IP Fixed Subnet Part 6 | Set the IP address subnet of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 1
70029 | 1 | Ethernet | Base | Fixed IP Gateway Part 1 | Set the IP gateway of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 1
70030 | 1 | Ethernet | Base | Fixed IP Gateway Part 2 | Set the IP gateway of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 1
70031 | 1 | Ethernet | Base | Fixed IP Gateway Part 3 | Set the IP gateway of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 1
70032 | 1 | Ethernet | Base | Fixed IP Gateway Part 4 | Set the IP gateway of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 1
70033 | 1 | Ethernet | Base | Fixed IP Gateway Part 5 | Set the IP gateway of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 1
70034 | 1 | Ethernet | Base | Fixed IP Gateway Part 6 | Set the IP gateway of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 1
70035 | 1 | Ethernet | Base | Actual IP Addressing Mode | Monitor the actual IP address assignment method. | None (61), DHCP (1281), Fixed (1284), Fail (32) | Fixed (1284) | Enumeration | R | 1
70039 | 1 | Ethernet | Base | IP Actual Address Part 1 | Monitor the actual IP address assigned. | 0 to 255 | 0 | Unsigned 8-bit | R | 1
70040 | 1 | Ethernet | Base | IP Actual Address Part 2 | Monitor the actual IP address assigned. | 0 to 255 | 0 | Unsigned 8-bit | R | 1
70041 | 1 | Ethernet | Base | IP Actual Address Part 3 | Monitor the actual IP address assigned. | 0 to 255 | 0 | Unsigned 8-bit | R | 1
70042 | 1 | Ethernet | Base | IP Actual Address Part 4 | Monitor the actual IP address assigned. | 0 to 255 | 0 | Unsigned 8-bit | R | 1
70043 | 1 | Ethernet | Base | IP Actual Address Part 5 | Monitor the actual IP address assigned. | 0 to 255 | 0 | Unsigned 8-bit | R | 1
70044 | 1 | Ethernet | Base | IP Actual Address Part 6 | Monitor the actual IP address assigned. | 0 to 255 | 0 | Unsigned 8-bit | R | 1
70045 | 1 | Ethernet | Base | MAC Address | Monitor the Media Access Control ID. | 0 to 255 | 0 | Unsigned 8-bit | R | 1
70046 | 1 | Ethernet | Base | MAC Address | Monitor the Media Access Control ID. | 0 to 255 | 0 | Unsigned 8-bit | R | 1
70047 | 1 | Ethernet | Base | MAC Address | Monitor the Media Access Control ID. | 0 to 255 | 0 | Unsigned 8-bit | R | 1
70048 | 1 | Ethernet | Base | MAC Address | Monitor the Media Access Control ID. | 0 to 255 | 0 | Unsigned 8-bit | R | 1
70049 | 1 | Ethernet | Base | MAC Address | Monitor the Media Access Control ID. | 0 to 255 | 0 | Unsigned 8-bit | R | 1
70050 | 1 | Ethernet | Base | MAC Address | Monitor the Media Access Control ID. | 0 to 255 | 0 | Unsigned 8-bit | R | 1
70052 | 1 | Ethernet | Base | IP Version | Monitor the IP version in effect. | IP Version 4 (1279), IP Version 6 (1280) | IP Version 4 (1279) | Enumeration | R/W | 1
74001 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 14
74002 | 1 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 14
74003 | 1 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 14
74004 | 1 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 14
74005 | 1 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 14
74006 | 1 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 14
74007 | 1 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 14
74008 | 1 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 14
74009 | 1 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 14
74010 | 1 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14
74011 | 1 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 14
74012 | 1 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 14
74013 | 1 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 14
74014 | 1 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 14
74015 | 1 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74016 | 1 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74017 | 1 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74018 | 1 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74019 | 1 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74020 | 1 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74021 | 1 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74022 | 1 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74023 | 1 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74024 | 1 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74025 | 1 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74026 | 1 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74027 | 1 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74028 | 1 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74029 | 1 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 14
74030 | 1 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74031 | 1 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74032 | 1 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74033 | 1 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74034 | 1 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 14
74035 | 1 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74036 | 1 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74037 | 1 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74038 | 1 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74039 | 1 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 14
74040 | 1 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74043 | 1 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14
74044 | 1 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 14
74045 | 1 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 14
74001 | 2 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 14
74002 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 14
74003 | 2 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 14
74004 | 2 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 14
74005 | 2 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 14
74006 | 2 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 14
74007 | 2 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 14
74008 | 2 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 14
74009 | 2 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 14
74010 | 2 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14
74011 | 2 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 14
74012 | 2 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 14
74013 | 2 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 14
74014 | 2 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 14
74015 | 2 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74016 | 2 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74017 | 2 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74018 | 2 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74019 | 2 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74020 | 2 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74021 | 2 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74022 | 2 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74023 | 2 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74024 | 2 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74025 | 2 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74026 | 2 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74027 | 2 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74028 | 2 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74029 | 2 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 14
74030 | 2 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74031 | 2 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74032 | 2 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74033 | 2 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74034 | 2 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 14
74035 | 2 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74036 | 2 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74037 | 2 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74038 | 2 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74039 | 2 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 14
74040 | 2 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74043 | 2 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14
74044 | 2 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 14
74045 | 2 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 14
74001 | 3 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 14
74002 | 3 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 14
74003 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 14
74004 | 3 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 14
74005 | 3 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 14
74006 | 3 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 14
74007 | 3 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 14
74008 | 3 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 14
74009 | 3 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 14
74010 | 3 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14
74011 | 3 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 14
74012 | 3 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 14
74013 | 3 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 14
74014 | 3 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 14
74015 | 3 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74016 | 3 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74017 | 3 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74018 | 3 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74019 | 3 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74020 | 3 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74021 | 3 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74022 | 3 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74023 | 3 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74024 | 3 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74025 | 3 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74026 | 3 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74027 | 3 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74028 | 3 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74029 | 3 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 14
74030 | 3 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74031 | 3 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74032 | 3 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74033 | 3 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74034 | 3 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 14
74035 | 3 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74036 | 3 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74037 | 3 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74038 | 3 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74039 | 3 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 14
74040 | 3 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74043 | 3 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14
74044 | 3 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 14
74045 | 3 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 14
74001 | 4 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 14
74002 | 4 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 14
74003 | 4 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 14
74004 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 14
74005 | 4 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 14
74006 | 4 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 14
74007 | 4 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 14
74008 | 4 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 14
74009 | 4 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 14
74010 | 4 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14
74011 | 4 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 14
74012 | 4 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 14
74013 | 4 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 14
74014 | 4 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 14
74015 | 4 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74016 | 4 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74017 | 4 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74018 | 4 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74019 | 4 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74020 | 4 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74021 | 4 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74022 | 4 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74023 | 4 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74024 | 4 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74025 | 4 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74026 | 4 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74027 | 4 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74028 | 4 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74029 | 4 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 14
74030 | 4 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74031 | 4 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74032 | 4 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74033 | 4 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74034 | 4 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 14
74035 | 4 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74036 | 4 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74037 | 4 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74038 | 4 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74039 | 4 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 14
74040 | 4 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74043 | 4 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14
74044 | 4 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 14
74045 | 4 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 14
74001 | 5 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 14
74002 | 5 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 14
74003 | 5 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 14
74004 | 5 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 14
74005 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 14
74006 | 5 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 14
74007 | 5 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 14
74008 | 5 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 14
74009 | 5 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 14
74010 | 5 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14
74011 | 5 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 14
74012 | 5 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 14
74013 | 5 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 14
74014 | 5 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 14
74015 | 5 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74016 | 5 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74017 | 5 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74018 | 5 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74019 | 5 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74020 | 5 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74021 | 5 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74022 | 5 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74023 | 5 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74024 | 5 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74025 | 5 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74026 | 5 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74027 | 5 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74028 | 5 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74029 | 5 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 14
74030 | 5 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74031 | 5 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74032 | 5 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74033 | 5 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74034 | 5 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 14
74035 | 5 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74036 | 5 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74037 | 5 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74038 | 5 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74039 | 5 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 14
74040 | 5 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74043 | 5 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14
74044 | 5 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 14
74045 | 5 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 14
74001 | 6 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 14
74002 | 6 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 14
74003 | 6 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 14
74004 | 6 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 14
74005 | 6 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 14
74006 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 14
74007 | 6 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 14
74008 | 6 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 14
74009 | 6 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 14
74010 | 6 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14
74011 | 6 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 14
74012 | 6 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 14
74013 | 6 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 14
74014 | 6 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 14
74015 | 6 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74016 | 6 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74017 | 6 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74018 | 6 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74019 | 6 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74020 | 6 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74021 | 6 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74022 | 6 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74023 | 6 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74024 | 6 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74025 | 6 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74026 | 6 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74027 | 6 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74028 | 6 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74029 | 6 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 14
74030 | 6 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74031 | 6 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74032 | 6 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74033 | 6 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74034 | 6 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 14
74035 | 6 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74036 | 6 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74037 | 6 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74038 | 6 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74039 | 6 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 14
74040 | 6 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74043 | 6 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14
74044 | 6 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 14
74045 | 6 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 14
74001 | 7 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 14
74002 | 7 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 14
74003 | 7 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 14
74004 | 7 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 14
74005 | 7 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 14
74006 | 7 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 14
74007 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 14
74008 | 7 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 14
74009 | 7 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 14
74010 | 7 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14
74011 | 7 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 14
74012 | 7 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 14
74013 | 7 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 14
74014 | 7 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 14
74015 | 7 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74016 | 7 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74017 | 7 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74018 | 7 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74019 | 7 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74020 | 7 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74021 | 7 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74022 | 7 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74023 | 7 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74024 | 7 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74025 | 7 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74026 | 7 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74027 | 7 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74028 | 7 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74029 | 7 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 14
74030 | 7 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74031 | 7 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74032 | 7 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74033 | 7 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74034 | 7 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 14
74035 | 7 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74036 | 7 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74037 | 7 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74038 | 7 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74039 | 7 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 14
74040 | 7 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74043 | 7 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14
74044 | 7 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 14
74045 | 7 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 14
74001 | 8 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 14
74002 | 8 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 14
74003 | 8 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 14
74004 | 8 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 14
74005 | 8 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 14
74006 | 8 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 14
74007 | 8 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 14
74008 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 14
74009 | 8 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 14
74010 | 8 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14
74011 | 8 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 14
74012 | 8 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 14
74013 | 8 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 14
74014 | 8 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 14
74015 | 8 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74016 | 8 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74017 | 8 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74018 | 8 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74019 | 8 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74020 | 8 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74021 | 8 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74022 | 8 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74023 | 8 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74024 | 8 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74025 | 8 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74026 | 8 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74027 | 8 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74028 | 8 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74029 | 8 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 14
74030 | 8 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74031 | 8 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74032 | 8 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74033 | 8 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74034 | 8 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 14
74035 | 8 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74036 | 8 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74037 | 8 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74038 | 8 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74039 | 8 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 14
74040 | 8 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74043 | 8 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14
74044 | 8 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 14
74045 | 8 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 14
74001 | 9 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 14
74002 | 9 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 14
74003 | 9 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 14
74004 | 9 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 14
74005 | 9 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 14
74006 | 9 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 14
74007 | 9 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 14
74008 | 9 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 14
74009 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 14
74010 | 9 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14
74011 | 9 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 14
74012 | 9 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 14
74013 | 9 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 14
74014 | 9 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 14
74015 | 9 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74016 | 9 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74017 | 9 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74018 | 9 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74019 | 9 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74020 | 9 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74021 | 9 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74022 | 9 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74023 | 9 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74024 | 9 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74025 | 9 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74026 | 9 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74027 | 9 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74028 | 9 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74029 | 9 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 14
74030 | 9 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74031 | 9 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74032 | 9 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74033 | 9 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74034 | 9 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 14
74035 | 9 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74036 | 9 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74037 | 9 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74038 | 9 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74039 | 9 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 14
74040 | 9 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74043 | 9 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14
74044 | 9 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 14
74045 | 9 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 14
74001 | 10 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 14
74002 | 10 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 14
74003 | 10 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 14
74004 | 10 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 14
74005 | 10 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 14
74006 | 10 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 14
74007 | 10 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 14
74008 | 10 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 14
74009 | 10 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 14
74010 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14
74011 | 10 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 14
74012 | 10 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 14
74013 | 10 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 14
74014 | 10 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 14
74015 | 10 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74016 | 10 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74017 | 10 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74018 | 10 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74019 | 10 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74020 | 10 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74021 | 10 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74022 | 10 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74023 | 10 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74024 | 10 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74025 | 10 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74026 | 10 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74027 | 10 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74028 | 10 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74029 | 10 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 14
74030 | 10 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74031 | 10 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74032 | 10 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74033 | 10 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74034 | 10 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 14
74035 | 10 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74036 | 10 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74037 | 10 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74038 | 10 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74039 | 10 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 14
74040 | 10 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74043 | 10 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14
74044 | 10 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 14
74045 | 10 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 14
74001 | 11 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 14
74002 | 11 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 14
74003 | 11 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 14
74004 | 11 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 14
74005 | 11 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 14
74006 | 11 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 14
74007 | 11 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 14
74008 | 11 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 14
74009 | 11 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 14
74010 | 11 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14
74011 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 14
74012 | 11 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 14
74013 | 11 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 14
74014 | 11 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 14
74015 | 11 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74016 | 11 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74017 | 11 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74018 | 11 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74019 | 11 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74020 | 11 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74021 | 11 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74022 | 11 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74023 | 11 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74024 | 11 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74025 | 11 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74026 | 11 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74027 | 11 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74028 | 11 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74029 | 11 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 14
74030 | 11 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74031 | 11 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74032 | 11 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74033 | 11 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74034 | 11 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 14
74035 | 11 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74036 | 11 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74037 | 11 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74038 | 11 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74039 | 11 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 14
74040 | 11 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74043 | 11 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14
74044 | 11 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 14
74045 | 11 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 14
74001 | 12 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 14
74002 | 12 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 14
74003 | 12 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 14
74004 | 12 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 14
74005 | 12 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 14
74006 | 12 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 14
74007 | 12 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 14
74008 | 12 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 14
74009 | 12 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 14
74010 | 12 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14
74011 | 12 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 14
74012 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 14
74013 | 12 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 14
74014 | 12 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 14
74015 | 12 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74016 | 12 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74017 | 12 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74018 | 12 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74019 | 12 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74020 | 12 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74021 | 12 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74022 | 12 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74023 | 12 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74024 | 12 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74025 | 12 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74026 | 12 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74027 | 12 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74028 | 12 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74029 | 12 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 14
74030 | 12 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74031 | 12 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74032 | 12 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74033 | 12 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74034 | 12 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 14
74035 | 12 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74036 | 12 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74037 | 12 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74038 | 12 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74039 | 12 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 14
74040 | 12 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74043 | 12 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14
74044 | 12 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 14
74045 | 12 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 14
74001 | 13 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 14
74002 | 13 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 14
74003 | 13 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 14
74004 | 13 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 14
74005 | 13 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 14
74006 | 13 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 14
74007 | 13 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 14
74008 | 13 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 14
74009 | 13 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 14
74010 | 13 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14
74011 | 13 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 14
74012 | 13 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 14
74013 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 14
74014 | 13 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 14
74015 | 13 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74016 | 13 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74017 | 13 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74018 | 13 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74019 | 13 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74020 | 13 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74021 | 13 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74022 | 13 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74023 | 13 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74024 | 13 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74025 | 13 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74026 | 13 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74027 | 13 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74028 | 13 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74029 | 13 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 14
74030 | 13 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74031 | 13 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74032 | 13 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74033 | 13 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74034 | 13 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 14
74035 | 13 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74036 | 13 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74037 | 13 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74038 | 13 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74039 | 13 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 14
74040 | 13 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74043 | 13 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14
74044 | 13 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 14
74045 | 13 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 14
74001 | 14 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 14
74002 | 14 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 14
74003 | 14 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 14
74004 | 14 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 14
74005 | 14 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 14
74006 | 14 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 14
74007 | 14 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 14
74008 | 14 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 14
74009 | 14 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 14
74010 | 14 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14
74011 | 14 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 14
74012 | 14 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 14
74013 | 14 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 14
74014 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 14
74015 | 14 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74016 | 14 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74017 | 14 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 14
74018 | 14 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74019 | 14 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74020 | 14 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74021 | 14 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74022 | 14 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14
74023 | 14 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74024 | 14 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74025 | 14 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 14
74026 | 14 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74027 | 14 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74028 | 14 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74029 | 14 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 14
74030 | 14 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74031 | 14 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74032 | 14 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74033 | 14 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74034 | 14 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 14
74035 | 14 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74036 | 14 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14
74037 | 14 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14
74038 | 14 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14
74039 | 14 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 14
74040 | 14 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 14
74043 | 14 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14
74044 | 14 | Alarm | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 14
74045 | 14 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 14
75001 | 1 | Control Loop | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 4
75002 | 1 | Control Loop | Base | Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 4
75003 | 1 | Control Loop | Base | Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 4
75004 | 1 | Control Loop | Base | Integral 1 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75005 | 1 | Control Loop | Base | Derivative 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75006 | 1 | Control Loop | Base | Dead Band | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 4
75007 | 1 | Control Loop | Base | Heat Proportional Band 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75008 | 1 | Control Loop | Base | On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 4
75009 | 1 | Control Loop | Base | Cool Proportional Band 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75010 | 1 | Control Loop | Base | On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 4
75011 | 1 | Control Loop | Base | TRU-TUNE+ Enable | Set to enable or disable the TRU-TUNE+® adaptive tuning feature. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
75012 | 1 | Control Loop | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | Enumeration | R/W | 4
75013 | 1 | Control Loop | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | IEEE Float | R/W | 4
75014 | 1 | Control Loop | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
75015 | 1 | Control Loop | Base | TRU-TUNE+ Band | Set the range, centered on the set point, within which TRU-TUNE+® will be in effect. | 0 to 100 | 0 | Unsigned 16-bit | R/W | 4
75016 | 1 | Control Loop | Base | TRU-TUNE+ Gain | Set the responsiveness of the TRU-TUNE+® adaptive tuning calculations. | 1 to 6 | 3 | Unsigned 8-bit | R/W | 4
75018 | 1 | Control Loop | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | Enumeration | R/W | 4
75019 | 1 | Control Loop | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
75020 | 1 | Control Loop | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | Unsigned 16-bit | R/W | 4
75021 | 1 | Control Loop | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 4
75022 | 1 | Control Loop | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | Enumeration | R | 4
75023 | 1 | Control Loop | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 4
75024 | 1 | Control Loop | Base | Peltier Delay | Set a value that will cause a delay when switching from heat PID mode to cool PID mode. | 0.0 to 5.0 | 0.0 | IEEE Float | R/W | 4
75025 | 1 | Control Loop | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 4
75026 | 1 | Control Loop | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 4
75027 | 1 | Control Loop | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | IEEE Float | R/W | 4
75028 | 1 | Control Loop | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | IEEE Float | R/W | 4
75029 | 1 | Control Loop | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | IEEE Float | R/W | 4
75030 | 1 | Control Loop | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | IEEE Float | R/W | 4
75031 | 1 | Control Loop | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | IEEE Float | R/W | 4
75032 | 1 | Control Loop | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 4
75033 | 1 | Control Loop | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 4
75034 | 1 | Control Loop | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | IEEE Float | R/W | 4
75035 | 1 | Control Loop | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 4
75036 | 1 | Control Loop | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | Enumeration | R/W | 4
75037 | 1 | Control Loop | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 4
75039 | 1 | Control Loop | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
75040 | 1 | Control Loop | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 4
75041 | 1 | Control Loop | Base | Heat Power | Monitor the PID heat power. | 0.0 to 100.0 |  | IEEE Float | R | 4
75042 | 1 | Control Loop | Base | Cool Power | Monitor the PID cool power. | -100.0 to 0.0 |  | IEEE Float | R | 4
75043 | 1 | Control Loop | Base | Control Loop Output Power | Monitor the PID total power. | -100.0 to 100.0 |  | IEEE Float | R | 4
75044 | 1 | Control Loop | Base | Closed-Loop Set Point | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 4
75045 | 1 | Control Loop | Base | Open-Loop Working Power | Monitor the set point used by the control loop while in manual mode. | -100.0 to 100.0 |  | IEEE Float | R | 4
75046 | 1 | Control Loop | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | Enumeration | R | 4
75047 | 1 | Control Loop | Base | Control Action | Set the control loop action. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | Enumeration | R/W | 4
75054 | 1 | Control Loop | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | Enumeration | R | 4
75066 | 1 | Control Loop | Base | Source Value A | Monitor the analog input value used by the control loop while in auto mode. |  |  | IEEE Float | R | 4
75070 | 1 | Control Loop | Base | Source Value B | Monitor the remote set point value. |  |  | IEEE Float | R | 4
75071 | 1 | Control Loop | Base | Source Function C | Set the source of remote set point for the control loop. | None (61), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778) | None (61) | Enumeration | R/W | 4
75074 | 1 | Control Loop | Base | Source Value C | Monitor the set point used by the control loop while a profile is active. |  |  | IEEE Float | R | 4
75107 | 1 | Control Loop | Base | Profile End Action | Set profile end action for control loop when end step is not specified in profile. | User (100), Off (62), Hold (47) | User (100) | Enumeration | R/W | 4
75113 | 1 | Control Loop | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 4
75114 | 1 | Control Loop | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | Enumeration | R/W | 4
75115 | 1 | Control Loop | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 4
75116 | 1 | Control Loop | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 4
75117 | 1 | Control Loop | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 4
75118 | 1 | Control Loop | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 4
75119 | 1 | Control Loop | Base | PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | Unsigned 8-bit | R | 4
75120 | 1 | Control Loop | Base | Heat Proportional Band 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75121 | 1 | Control Loop | Base | Cool Proportional Band 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75122 | 1 | Control Loop | Base | Integral 2 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75123 | 1 | Control Loop | Base | Derivative 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75124 | 1 | Control Loop | Base | Heat Proportional Band 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75125 | 1 | Control Loop | Base | Cool Proportional Band 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75126 | 1 | Control Loop | Base | Integral 3 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75127 | 1 | Control Loop | Base | Derivative 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75128 | 1 | Control Loop | Base | Heat Proportional Band 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75129 | 1 | Control Loop | Base | Cool Proportional Band 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75130 | 1 | Control Loop | Base | Integral 4 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75131 | 1 | Control Loop | Base | Derivative 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75132 | 1 | Control Loop | Base | Heat Proportional Band 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75133 | 1 | Control Loop | Base | Cool Proportional Band 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75134 | 1 | Control Loop | Base | Integral 5 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75135 | 1 | Control Loop | Base | Derivative 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75136 | 1 | Control Loop | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | Unsigned 8-bit | R/W | 4
75137 | 1 | Control Loop | Base | Control Loop Control Mode Is Off | Monitor the Control Loop Control Mode is Off. | On (63), Off (62) |  | Enumeration | R | 4
75138 | 1 | Control Loop | Base | Set Point | Moniotr the closed loop set point. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 4
75001 | 2 | Control Loop | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 4
75002 | 2 | Control Loop | Base | Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 4
75003 | 2 | Control Loop | Base | Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 4
75004 | 2 | Control Loop | Base | Integral 1 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75005 | 2 | Control Loop | Base | Derivative 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75006 | 2 | Control Loop | Base | Dead Band | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 4
75007 | 2 | Control Loop | Base | Heat Proportional Band 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75008 | 2 | Control Loop | Base | On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 4
75009 | 2 | Control Loop | Base | Cool Proportional Band 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75010 | 2 | Control Loop | Base | On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 4
75011 | 2 | Control Loop | Base | TRU-TUNE+ Enable | Set to enable or disable the TRU-TUNE+® adaptive tuning feature. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
75012 | 2 | Control Loop | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | Enumeration | R/W | 4
75013 | 2 | Control Loop | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | IEEE Float | R/W | 4
75014 | 2 | Control Loop | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
75015 | 2 | Control Loop | Base | TRU-TUNE+ Band | Set the range, centered on the set point, within which TRU-TUNE+® will be in effect. | 0 to 100 | 0 | Unsigned 16-bit | R/W | 4
75016 | 2 | Control Loop | Base | TRU-TUNE+ Gain | Set the responsiveness of the TRU-TUNE+® adaptive tuning calculations. | 1 to 6 | 3 | Unsigned 8-bit | R/W | 4
75018 | 2 | Control Loop | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | Enumeration | R/W | 4
75019 | 2 | Control Loop | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
75020 | 2 | Control Loop | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | Unsigned 16-bit | R/W | 4
75021 | 2 | Control Loop | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 4
75022 | 2 | Control Loop | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | Enumeration | R | 4
75023 | 2 | Control Loop | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 4
75024 | 2 | Control Loop | Base | Peltier Delay | Set a value that will cause a delay when switching from heat PID mode to cool PID mode. | 0.0 to 5.0 | 0.0 | IEEE Float | R/W | 4
75025 | 2 | Control Loop | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 4
75026 | 2 | Control Loop | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 4
75027 | 2 | Control Loop | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | IEEE Float | R/W | 4
75028 | 2 | Control Loop | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | IEEE Float | R/W | 4
75029 | 2 | Control Loop | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | IEEE Float | R/W | 4
75030 | 2 | Control Loop | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | IEEE Float | R/W | 4
75031 | 2 | Control Loop | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | IEEE Float | R/W | 4
75032 | 2 | Control Loop | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 4
75033 | 2 | Control Loop | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 4
75034 | 2 | Control Loop | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | IEEE Float | R/W | 4
75035 | 2 | Control Loop | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 4
75036 | 2 | Control Loop | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | Enumeration | R/W | 4
75037 | 2 | Control Loop | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 4
75039 | 2 | Control Loop | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
75040 | 2 | Control Loop | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 4
75041 | 2 | Control Loop | Base | Heat Power | Monitor the PID heat power. | 0.0 to 100.0 |  | IEEE Float | R | 4
75042 | 2 | Control Loop | Base | Cool Power | Monitor the PID cool power. | -100.0 to 0.0 |  | IEEE Float | R | 4
75043 | 2 | Control Loop | Base | Control Loop Output Power | Monitor the PID total power. | -100.0 to 100.0 |  | IEEE Float | R | 4
75044 | 2 | Control Loop | Base | Closed-Loop Set Point | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 4
75045 | 2 | Control Loop | Base | Open-Loop Working Power | Monitor the set point used by the control loop while in manual mode. | -100.0 to 100.0 |  | IEEE Float | R | 4
75046 | 2 | Control Loop | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | Enumeration | R | 4
75047 | 2 | Control Loop | Base | Control Action | Set the control loop action. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | Enumeration | R/W | 4
75054 | 2 | Control Loop | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | Enumeration | R | 4
75066 | 2 | Control Loop | Base | Source Value A | Monitor the analog input value used by the control loop while in auto mode. |  |  | IEEE Float | R | 4
75070 | 2 | Control Loop | Base | Source Value B | Monitor the remote set point value. |  |  | IEEE Float | R | 4
75071 | 2 | Control Loop | Base | Source Function C | Set the source of remote set point for the control loop. | None (61), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778) | None (61) | Enumeration | R/W | 4
75074 | 2 | Control Loop | Base | Source Value C | Monitor the set point used by the control loop while a profile is active. |  |  | IEEE Float | R | 4
75107 | 2 | Control Loop | Base | Profile End Action | Set profile end action for control loop when end step is not specified in profile. | User (100), Off (62), Hold (47) | User (100) | Enumeration | R/W | 4
75113 | 2 | Control Loop | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 4
75114 | 2 | Control Loop | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | Enumeration | R/W | 4
75115 | 2 | Control Loop | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 4
75116 | 2 | Control Loop | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 4
75117 | 2 | Control Loop | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 4
75118 | 2 | Control Loop | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 4
75119 | 2 | Control Loop | Base | PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | Unsigned 8-bit | R | 4
75120 | 2 | Control Loop | Base | Heat Proportional Band 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75121 | 2 | Control Loop | Base | Cool Proportional Band 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75122 | 2 | Control Loop | Base | Integral 2 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75123 | 2 | Control Loop | Base | Derivative 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75124 | 2 | Control Loop | Base | Heat Proportional Band 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75125 | 2 | Control Loop | Base | Cool Proportional Band 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75126 | 2 | Control Loop | Base | Integral 3 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75127 | 2 | Control Loop | Base | Derivative 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75128 | 2 | Control Loop | Base | Heat Proportional Band 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75129 | 2 | Control Loop | Base | Cool Proportional Band 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75130 | 2 | Control Loop | Base | Integral 4 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75131 | 2 | Control Loop | Base | Derivative 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75132 | 2 | Control Loop | Base | Heat Proportional Band 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75133 | 2 | Control Loop | Base | Cool Proportional Band 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75134 | 2 | Control Loop | Base | Integral 5 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75135 | 2 | Control Loop | Base | Derivative 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75136 | 2 | Control Loop | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | Unsigned 8-bit | R/W | 4
75137 | 2 | Control Loop | Base | Control Loop Control Mode Is Off | Monitor the Control Loop Control Mode is Off. | On (63), Off (62) |  | Enumeration | R | 4
75138 | 2 | Control Loop | Base | Set Point | Monitor the control mode is in Off state. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 4
75001 | 3 | Control Loop | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 4
75002 | 3 | Control Loop | Base | Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 4
75003 | 3 | Control Loop | Base | Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 4
75004 | 3 | Control Loop | Base | Integral 1 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75005 | 3 | Control Loop | Base | Derivative 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75006 | 3 | Control Loop | Base | Dead Band | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 4
75007 | 3 | Control Loop | Base | Heat Proportional Band 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75008 | 3 | Control Loop | Base | On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 4
75009 | 3 | Control Loop | Base | Cool Proportional Band 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75010 | 3 | Control Loop | Base | On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 4
75011 | 3 | Control Loop | Base | TRU-TUNE+ Enable | Set to enable or disable the TRU-TUNE+® adaptive tuning feature. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
75012 | 3 | Control Loop | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | Enumeration | R/W | 4
75013 | 3 | Control Loop | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | IEEE Float | R/W | 4
75014 | 3 | Control Loop | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
75015 | 3 | Control Loop | Base | TRU-TUNE+ Band | Set the range, centered on the set point, within which TRU-TUNE+® will be in effect. | 0 to 100 | 0 | Unsigned 16-bit | R/W | 4
75016 | 3 | Control Loop | Base | TRU-TUNE+ Gain | Set the responsiveness of the TRU-TUNE+® adaptive tuning calculations. | 1 to 6 | 3 | Unsigned 8-bit | R/W | 4
75018 | 3 | Control Loop | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | Enumeration | R/W | 4
75019 | 3 | Control Loop | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
75020 | 3 | Control Loop | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | Unsigned 16-bit | R/W | 4
75021 | 3 | Control Loop | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 4
75022 | 3 | Control Loop | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | Enumeration | R | 4
75023 | 3 | Control Loop | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 4
75024 | 3 | Control Loop | Base | Peltier Delay | Set a value that will cause a delay when switching from heat PID mode to cool PID mode. | 0.0 to 5.0 | 0.0 | IEEE Float | R/W | 4
75025 | 3 | Control Loop | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 4
75026 | 3 | Control Loop | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 4
75027 | 3 | Control Loop | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | IEEE Float | R/W | 4
75028 | 3 | Control Loop | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | IEEE Float | R/W | 4
75029 | 3 | Control Loop | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | IEEE Float | R/W | 4
75030 | 3 | Control Loop | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | IEEE Float | R/W | 4
75031 | 3 | Control Loop | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | IEEE Float | R/W | 4
75032 | 3 | Control Loop | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 4
75033 | 3 | Control Loop | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 4
75034 | 3 | Control Loop | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | IEEE Float | R/W | 4
75035 | 3 | Control Loop | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 4
75036 | 3 | Control Loop | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | Enumeration | R/W | 4
75037 | 3 | Control Loop | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 4
75039 | 3 | Control Loop | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
75040 | 3 | Control Loop | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 4
75041 | 3 | Control Loop | Base | Heat Power | Monitor the PID heat power. | 0.0 to 100.0 |  | IEEE Float | R | 4
75042 | 3 | Control Loop | Base | Cool Power | Monitor the PID cool power. | -100.0 to 0.0 |  | IEEE Float | R | 4
75043 | 3 | Control Loop | Base | Control Loop Output Power | Monitor the PID total power. | -100.0 to 100.0 |  | IEEE Float | R | 4
75044 | 3 | Control Loop | Base | Closed-Loop Set Point | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 4
75045 | 3 | Control Loop | Base | Open-Loop Working Power | Monitor the set point used by the control loop while in manual mode. | -100.0 to 100.0 |  | IEEE Float | R | 4
75046 | 3 | Control Loop | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | Enumeration | R | 4
75047 | 3 | Control Loop | Base | Control Action | Set the control loop action. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | Enumeration | R/W | 4
75054 | 3 | Control Loop | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | Enumeration | R | 4
75066 | 3 | Control Loop | Base | Source Value A | Monitor the analog input value used by the control loop while in auto mode. |  |  | IEEE Float | R | 4
75070 | 3 | Control Loop | Base | Source Value B | Monitor the remote set point value. |  |  | IEEE Float | R | 4
75071 | 3 | Control Loop | Base | Source Function C | Set the source of remote set point for the control loop. | None (61), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778) | None (61) | Enumeration | R/W | 4
75074 | 3 | Control Loop | Base | Source Value C | Monitor the set point used by the control loop while a profile is active. |  |  | IEEE Float | R | 4
75107 | 3 | Control Loop | Base | Profile End Action | Set profile end action for control loop when end step is not specified. | User (100), Off (62), Hold (47) | User (100) | Enumeration | R/W | 4
75113 | 3 | Control Loop | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 4
75114 | 3 | Control Loop | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | Enumeration | R/W | 4
75115 | 3 | Control Loop | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 4
75116 | 3 | Control Loop | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 4
75117 | 3 | Control Loop | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 4
75118 | 3 | Control Loop | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 4
75119 | 3 | Control Loop | Base | PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | Unsigned 8-bit | R | 4
75120 | 3 | Control Loop | Base | Heat Proportional Band 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75121 | 3 | Control Loop | Base | Cool Proportional Band 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75122 | 3 | Control Loop | Base | Integral 2 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75123 | 3 | Control Loop | Base | Derivative 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75124 | 3 | Control Loop | Base | Heat Proportional Band 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75125 | 3 | Control Loop | Base | Cool Proportional Band 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75126 | 3 | Control Loop | Base | Integral 3 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75127 | 3 | Control Loop | Base | Derivative 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75128 | 3 | Control Loop | Base | Heat Proportional Band 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75129 | 3 | Control Loop | Base | Cool Proportional Band 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75130 | 3 | Control Loop | Base | Integral 4 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75131 | 3 | Control Loop | Base | Derivative 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75132 | 3 | Control Loop | Base | Heat Proportional Band 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75133 | 3 | Control Loop | Base | Cool Proportional Band 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75134 | 3 | Control Loop | Base | Integral 5 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75135 | 3 | Control Loop | Base | Derivative 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75136 | 3 | Control Loop | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | Unsigned 8-bit | R/W | 4
75137 | 3 | Control Loop | Base | Control Loop Control Mode Is Off | Monitor the Control Loop Control Mode is Off. | On (63), Off (62) |  | Enumeration | R | 4
75138 | 3 | Control Loop | Base | Set Point | Monitor the control mode is in Off state. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 4
75001 | 4 | Control Loop | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 4
75002 | 4 | Control Loop | Base | Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 4
75003 | 4 | Control Loop | Base | Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 4
75004 | 4 | Control Loop | Base | Integral 1 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75005 | 4 | Control Loop | Base | Derivative 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75006 | 4 | Control Loop | Base | Dead Band | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 4
75007 | 4 | Control Loop | Base | Heat Proportional Band 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75008 | 4 | Control Loop | Base | On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 4
75009 | 4 | Control Loop | Base | Cool Proportional Band 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75010 | 4 | Control Loop | Base | On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 4
75011 | 4 | Control Loop | Base | TRU-TUNE+ Enable | Set to enable or disable the TRU-TUNE+® adaptive tuning feature. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
75012 | 4 | Control Loop | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | Enumeration | R/W | 4
75013 | 4 | Control Loop | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | IEEE Float | R/W | 4
75014 | 4 | Control Loop | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
75015 | 4 | Control Loop | Base | TRU-TUNE+ Band | Set the range, centered on the set point, within which TRU-TUNE+® will be in effect. | 0 to 100 | 0 | Unsigned 16-bit | R/W | 4
75016 | 4 | Control Loop | Base | TRU-TUNE+ Gain | Set the responsiveness of the TRU-TUNE+® adaptive tuning calculations. | 1 to 6 | 3 | Unsigned 8-bit | R/W | 4
75018 | 4 | Control Loop | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | Enumeration | R/W | 4
75019 | 4 | Control Loop | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
75020 | 4 | Control Loop | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | Unsigned 16-bit | R/W | 4
75021 | 4 | Control Loop | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 4
75022 | 4 | Control Loop | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | Enumeration | R | 4
75023 | 4 | Control Loop | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 4
75024 | 4 | Control Loop | Base | Peltier Delay | Set a value that will cause a delay when switching from heat PID mode to cool PID mode. | 0.0 to 5.0 | 0.0 | IEEE Float | R/W | 4
75025 | 4 | Control Loop | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 4
75026 | 4 | Control Loop | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 4
75027 | 4 | Control Loop | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | IEEE Float | R/W | 4
75028 | 4 | Control Loop | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | IEEE Float | R/W | 4
75029 | 4 | Control Loop | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | IEEE Float | R/W | 4
75030 | 4 | Control Loop | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | IEEE Float | R/W | 4
75031 | 4 | Control Loop | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | IEEE Float | R/W | 4
75032 | 4 | Control Loop | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 4
75033 | 4 | Control Loop | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 4
75034 | 4 | Control Loop | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | IEEE Float | R/W | 4
75035 | 4 | Control Loop | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 4
75036 | 4 | Control Loop | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | Enumeration | R/W | 4
75037 | 4 | Control Loop | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 4
75039 | 4 | Control Loop | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
75040 | 4 | Control Loop | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 4
75041 | 4 | Control Loop | Base | Heat Power | Monitor the PID heat power. | 0.0 to 100.0 |  | IEEE Float | R | 4
75042 | 4 | Control Loop | Base | Cool Power | Monitor the PID cool power. | -100.0 to 0.0 |  | IEEE Float | R | 4
75043 | 4 | Control Loop | Base | Control Loop Output Power | Monitor the PID total power. | -100.0 to 100.0 |  | IEEE Float | R | 4
75044 | 4 | Control Loop | Base | Closed-Loop Set Point | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 4
75045 | 4 | Control Loop | Base | Open-Loop Working Power | Monitor the set point used by the control loop while in manual mode. | -100.0 to 100.0 |  | IEEE Float | R | 4
75046 | 4 | Control Loop | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | Enumeration | R | 4
75047 | 4 | Control Loop | Base | Control Action | Set the control loop action. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | Enumeration | R/W | 4
75054 | 4 | Control Loop | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | Enumeration | R | 4
75066 | 4 | Control Loop | Base | Source Value A | Monitor the analog input value used by the control loop while in auto mode. |  |  | IEEE Float | R | 4
75070 | 4 | Control Loop | Base | Source Value B | Monitor the remote set point value. |  |  | IEEE Float | R | 4
75071 | 4 | Control Loop | Base | Source Function C | Set the source of remote set point for the control loop. | None (61), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778) | None (61) | Enumeration | R/W | 4
75074 | 4 | Control Loop | Base | Source Value C | Monitor the set point used by the control loop while a profile is active. |  |  | IEEE Float | R | 4
75107 | 4 | Control Loop | Base | Profile End Action | Set profile end action for control loop when end step is not specified. | User (100), Off (62), Hold (47) | User (100) | Enumeration | R/W | 4
75113 | 4 | Control Loop | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | String | R/W | 4
75114 | 4 | Control Loop | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | Enumeration | R/W | 4
75115 | 4 | Control Loop | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 4
75116 | 4 | Control Loop | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 4
75117 | 4 | Control Loop | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 4
75118 | 4 | Control Loop | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 4
75119 | 4 | Control Loop | Base | PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | Unsigned 8-bit | R | 4
75120 | 4 | Control Loop | Base | Heat Proportional Band 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75121 | 4 | Control Loop | Base | Cool Proportional Band 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75122 | 4 | Control Loop | Base | Integral 2 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75123 | 4 | Control Loop | Base | Derivative 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75124 | 4 | Control Loop | Base | Heat Proportional Band 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75125 | 4 | Control Loop | Base | Cool Proportional Band 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75126 | 4 | Control Loop | Base | Integral 3 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75127 | 4 | Control Loop | Base | Derivative 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75128 | 4 | Control Loop | Base | Heat Proportional Band 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75129 | 4 | Control Loop | Base | Cool Proportional Band 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75130 | 4 | Control Loop | Base | Integral 4 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75131 | 4 | Control Loop | Base | Derivative 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75132 | 4 | Control Loop | Base | Heat Proportional Band 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75133 | 4 | Control Loop | Base | Cool Proportional Band 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4
75134 | 4 | Control Loop | Base | Integral 5 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4
75135 | 4 | Control Loop | Base | Derivative 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4
75136 | 4 | Control Loop | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | Unsigned 8-bit | R/W | 4
75137 | 4 | Control Loop | Base | Control Loop Control Mode Is Off | Monitor the Control Loop Control Mode is Off. | On (63), Off (62) |  | Enumeration | R | 4
75138 | 4 | Control Loop | Base | Set Point | Monitor the control mode is in Off state. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 4
79001 | 1 | Profile | Base | Units | Monitor units applied to PV1 receiver of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | Enumeration | R | 1
79002 | 1 | Profile | Base | Units | Monitor units applied to PV2 receiver of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | Enumeration | R | 1
79003 | 1 | Profile | Base | Units | Monitor units applied to PV3 receiver of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | Enumeration | R | 1
79004 | 1 | Profile | Base | Units | Monitor units applied to PV4 receiver of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | Enumeration | R | 1
79005 | 1 | Profile | Base | Units | Monitor units applied to EVT1 receiver when analog of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | Enumeration | R | 1
79006 | 1 | Profile | Base | Units | Monitor units applied to EVT2 receiver when analog of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | Enumeration | R | 1
79007 | 1 | Profile | Base | Units | Monitor units applied to EVT3 receiver when analog of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | Enumeration | R | 1
79008 | 1 | Profile | Base | Units | Monitor units applied to EVT4 receiver when analog of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | Enumeration | R | 1
79012 | 1 | Profile | Base | Start Profile | Enter Profile number to queue for start or calendar start via Profile Action Request. | 1 to 40 | 1 | Unsigned 16-bit | R/W | 1
79013 | 1 | Profile | Base | Start Step | Enter Profile Step number to queue for start via Profile Action Request. |  | 1 | Unsigned 16-bit | R/W | 1
79014 | 1 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 1
79015 | 1 | Profile | Base | Profile Action Request | Resume a profile previously paused. | None (61), Resume (147) | None (61) | Enumeration | R/W | 1
79016 | 1 | Profile | Base | Profile Action Request | Pause running profile or terminate running profile. | None (61), Pause (146), Terminate (148) | None (61) | Enumeration | R/W | 1
79017 | 1 | Profile | Base | Profile State | Monitor state of profile. | Off (62), Running (149), Pause (146), Not Started (251), Completed Normal (252), Terminated (253), Calendar Start (1783) |  | Enumeration | R | 1
79018 | 1 | Profile | Base | Minutes | Monitor time remaining in profile (minutes portion). | 0 to 59 |  | Unsigned 8-bit | R | 1
79019 | 1 | Profile | Base | Hours | Monitor time remaining in profile (hours portion). | 0 to 9,999 |  | Unsigned 16-bit | R | 1
79020 | 1 | Profile | Base | Power Out Minutes | Set power out time (minutes portion). | 0 to 59 |  | Unsigned 8-bit | R/W | 1
79021 | 1 | Profile | Base | Power Out Hours | Set power out time (hours portion). | 0 to 99 |  | Unsigned 8-bit | R/W | 1
79023 | 1 | Profile | Base | Calendar Start Minute | Set Calendar Start time (minutes portion) for this profile. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
79024 | 1 | Profile | Base | Calendar Start Hour | Set Calendar Start time (hours portion) for this profile. | 0 to 23 | 0 | Unsigned 8-bit | R/W | 1
79025 | 1 | Profile | Base | Calendar Start Day | Set Calendar Start time (day of week portion) for this profile. | Sunday (1565), Monday (1559), Tuesday (1560), Wednesday (1561), Thursday (1562), Friday (1563), Saturday (1564) | Monday (1559) | Enumeration | R/W | 1
79027 | 1 | Profile | Base | Current Profile | Monitor current file loaded in memory. | 0 to 40 | 1 | Unsigned 16-bit | R | 1
79028 | 1 | Profile | Base | Current Step | Monitor current step loaded in memory. |  | 1 | Unsigned 16-bit | R | 1
79029 | 1 | Profile | Base | Step Type | Monitor current step type loaded in memory. | Soak (87), Wait For (1542), Instant Change (1927), Jump (116), Ramp Time (1928), Ramp Rate (81), End (27) |  | Enumeration | R | 1
79030 | 1 | Profile | Base | Event 1 | Monitor/change current step Event Output 1 transmitter (ENT1) loaded in memory. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
79031 | 1 | Profile | Base | Event 2 | Monitor/change current step Event Output 2 transmitter (ENT2) loaded in memory. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
79032 | 1 | Profile | Base | Event 3 | Monitor/change current step Event Output 3 transmitter (ENT3) loaded in memory. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
79033 | 1 | Profile | Base | Event 4 | Monitor/change current step Event Output 4 transmitter (ENT4) loaded in memory. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
79034 | 1 | Profile | Base | Target Set Point Loop 1 | Monitor/Set Target Set Point Loop 1 for current step. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 1
79035 | 1 | Profile | Base | Target Set Point Loop 2 | Monitor/Set Target Set Point Loop 2 for current step. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 1
79036 | 1 | Profile | Base | Target Set Point Loop 3 | Monitor/Set Target Set Point Loop 3 for current step. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 1
79037 | 1 | Profile | Base | Target Set Point Loop 4 | Monitor/Set Target Set Point Loop 4 for current step. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 1
79038 | 1 | Profile | Base | Produced Set Point 1 | Monitor Produced Set Point 1 for current step. (SP1) | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R | 1
79039 | 1 | Profile | Base | Produced Set Point 2 | Monitor Produced Set Point 2 for current step. (SP2) | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R | 1
79040 | 1 | Profile | Base | Produced Set Point 3 | Monitor Produced Set Point 3 for current step. (SP3) | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R | 1
79041 | 1 | Profile | Base | Produced Set Point 4 | Monitor Produced Set Point 4 for current step. (SP4) | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R | 1
79042 | 1 | Profile | Base | Status | Monitor the Wait-for Status, Returns bit values for Event 1, 2, 3 and 4. If condition is met, appropriate bit is 1. Possible returned values are 1 to 16 if all four events inputs are connected. | 0 to 65,535 | 0 | Unsigned 16-bit | R | 1
79043 | 1 | Profile | Base | Step Time Remaining | Monitor the current total Step Time remaining in seconds. | 0.0 to 3,600,000.0 | 0.0 | IEEE Float | R | 1
79044 | 1 | Profile | Base | Seconds | Monitor the current Step Time remaining (seconds portion). | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
79045 | 1 | Profile | Base | Minutes | Monitor the current total Step Time remaining (minutes portion). | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
79046 | 1 | Profile | Base | Hours | Monitor the current total Step Time remaining (hours portion). | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
79053 | 1 | Profile | Base | Source Function A | Set source to PV1 receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1
79054 | 1 | Profile | Base | Source Function B | Set source to PV2 receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1
79055 | 1 | Profile | Base | Source Function C | Set source to PV3 receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1
79056 | 1 | Profile | Base | Source Function D | Set source to PV4 receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1
79057 | 1 | Profile | Base | Source Instance A | Set source instance to PV1 receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1
79058 | 1 | Profile | Base | Source Instance B | Set source instance to PV2 receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1
79059 | 1 | Profile | Base | Source Instance C | Set source instance to PV3 receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1
79060 | 1 | Profile | Base | Source Instance D | Set source instance to PV4 receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1
79061 | 1 | Profile | Base | Source Zone A | Set source ZONE to PV1 receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1
79062 | 1 | Profile | Base | Source Zone B | Set source ZONE to PV2 receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1
79063 | 1 | Profile | Base | Source Zone C | Set source ZONE to PV3 receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1
79064 | 1 | Profile | Base | Source Zone D | Set source ZONE to PV4 receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1
79065 | 1 | Profile | Base | Source Value A | Monitor analog source value of PV1 source. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1
79066 | 1 | Profile | Base | Source Value B | Monitor analog source value of PV2 source. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1
79067 | 1 | Profile | Base | Source Value C | Monitor analog source value of PV3 source. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1
79068 | 1 | Profile | Base | Source Value D | Monitor analog source value of PV4 source. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1
79069 | 1 | Profile | Base | Source Function A | Set source to EVT1 receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1
79070 | 1 | Profile | Base | Source Function B | Set source to EVT2 receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1
79071 | 1 | Profile | Base | Source Function C | Set source to EVT3 receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1
79072 | 1 | Profile | Base | Source Function D | Set source to EVT4 receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1
79073 | 1 | Profile | Base | Source Instance A | Set source instance to ENT1 receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1
79074 | 1 | Profile | Base | Source Instance B | Set source instance to ENT2 receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1
79075 | 1 | Profile | Base | Source Instance C | Set source instance to ENT3 receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1
79076 | 1 | Profile | Base | Source Instance D | Set source instance to ENT4 receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1
79077 | 1 | Profile | Base | Source Zone A | Set source zone to ENT1 receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1
79078 | 1 | Profile | Base | Source Zone B | Set source zone to ENT2 receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1
79079 | 1 | Profile | Base | Source Zone C | Set source zone to ENT3 receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1
79080 | 1 | Profile | Base | Source Zone D | Set source zone to ENT4 receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1
79081 | 1 | Profile | Base | Source Value A | Monitor Wait-for source value applied to EVT1 receiver when digital of profile function block. | On (63), Off (62) | [n/a] | Enumeration | R | 1
79082 | 1 | Profile | Base | Source Value B | Monitor Wait-for source value applied to EVT2 receiver when digital of profile function block. | On (63), Off (62) | [n/a] | Enumeration | R | 1
79083 | 1 | Profile | Base | Source Value C | Monitor Wait-for source value applied to EVT3 receiver when digital of profile function block. | On (63), Off (62) | [n/a] | Enumeration | R | 1
79084 | 1 | Profile | Base | Source Value D | Monitor Wait-for source value applied to EVT4 receiver when digital of profile function block. | On (63), Off (62) | [n/a] | Enumeration | R | 1
79085 | 1 | Profile | Base | Source Function E | Set source to S/T receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1
79086 | 1 | Profile | Base | Source Function F | Set source to STRT receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1
79087 | 1 | Profile | Base | Source Function G | Set source to P/R receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1
79088 | 1 | Profile | Base | Source Function H | Set source to DIS receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1
79089 | 1 | Profile | Base | Source Instance E | Set source instance to S/T receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1
79090 | 1 | Profile | Base | Source Instance F | Set source instance to STRT receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1
79091 | 1 | Profile | Base | Source Instance G | Set source instance to P/R receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1
79092 | 1 | Profile | Base | Source Instance H | Set source instance to DIS receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1
79093 | 1 | Profile | Base | Source Zone E | Set source zone to S/T receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1
79094 | 1 | Profile | Base | Source Zone F | Set source zone to STRT receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1
79095 | 1 | Profile | Base | Source Zone G | Set source zone to P/R receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1
79096 | 1 | Profile | Base | Source Zone H | Set source zone to DIS receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1
79097 | 1 | Profile | Base | Source Value E | Monitor source value to S/T receiver on profile function block. | On (63), Off (62) |  | Enumeration | R | 1
79098 | 1 | Profile | Base | Source Value F | Monitor source value to STRT receiver on profile function block. | On (63), Off (62) |  | Enumeration | R | 1
79099 | 1 | Profile | Base | Source Value G | Monitor source value to P/R receiver on profile function block. | On (63), Off (62) |  | Enumeration | R | 1
79100 | 1 | Profile | Base | Source Value H | Monitor source value to DIS receiver on profile function block. | On (63), Off (62) |  | Enumeration | R | 1
79101 | 1 | Profile | Base | Start / Stop Active Level | Set Active Level for S/T receiver on profile function block. | High (37), Low (53) | High (37) | Enumeration | R/W | 1
79102 | 1 | Profile | Base | Start Active Level | Set Active Level for STRT receiver on profile function block. | High (37), Low (53) | High (37) | Enumeration | R/W | 1
79103 | 1 | Profile | Base | Pause / Resume Active Level | Set Active Level for P/R receiver on profile function block. | High (37), Low (53) | High (37) | Enumeration | R/W | 1
79104 | 1 | Profile | Base | Disable Active Level | Set Active Level for DIS receiver on profile function block. | High (37), Low (53) | High (37) | Enumeration | R/W | 1
79105 | 1 | Profile | Base | Source Function A | Set source to PRF receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1
79106 | 1 | Profile | Base | Source Function B | Set source to STP receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1
79107 | 1 | Profile | Base | Source Instance A | Set source instance to PRF receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1
79108 | 1 | Profile | Base | Source Instance B | Set source instance to STP receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1
79109 | 1 | Profile | Base | Source Zone A | Set source zone to PRF receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1
79110 | 1 | Profile | Base | Source Zone B | Set source zone to STP receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1
79111 | 1 | Profile | Base | Source Value A | Monitor profile number source value to PRF receiver on profile function block. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1
79112 | 1 | Profile | Base | Source Value B | Monitor step number source value to STP receiver on profile function block. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1
79113 | 1 | Profile | Base | Rate | If step type is rate, monitor/change ramp rate for control loop 1. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
79114 | 1 | Profile | Base | Rate | If step type is rate, monitor/change ramp rate for control loop 2. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
79115 | 1 | Profile | Base | Rate | If step type is rate, monitor/change ramp rate for control loop 3. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
79116 | 1 | Profile | Base | Rate | If step type is rate, monitor/change ramp rate for control loop 4. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
79117 | 1 | Profile | Base | Unknown | Monitor the x location of the Profile block on the canvas. | 0 to 65,535 | 0 | Unsigned 16-bit | R/W | 1
79118 | 1 | Profile | Base | Unknown | Monitor the y location of the Profile block on the canvas. | 0 to 65,535 | 0 | Unsigned 16-bit | R/W | 1
79119 | 1 | Profile | Base | Profile Running | Monitor profile running status. | On (63), Off (62) |  | Enumeration | R | 1
79120 | 1 | Profile | Base | Profile Paused | Monitor profile paused status. | On (63), Off (62) |  | Enumeration | R | 1
79125 | 1 | Profile | Base | Error | Monitor error status for produced set point 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1
79126 | 1 | Profile | Base | Error | Monitor error status for produced set point 2. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1
79127 | 1 | Profile | Base | Error | Monitor error status for produced set point 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1
79128 | 1 | Profile | Base | Error | Monitor error status for produced set point 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1
79129 | 1 | Profile | Base | Error | Monitor error status for produced event output 1 transmitter (EVT1). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1
79130 | 1 | Profile | Base | Error | Monitor error status for produced event output 2 transmitter (EVT2). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1
79131 | 1 | Profile | Base | Error | Monitor error status for produced event output 3 transmitter (EVT3). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1
79132 | 1 | Profile | Base | Error | Monitor error status for produced event output 4 transmitter (EVT4). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1
79133 | 1 | Profile | Base | Error | Monitor error status for profile running. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1
79134 | 1 | Profile | Base | Error | Monitor error status for profile paused. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1
79135 | 1 | Profile | Base | Error | Monitor error status for current profile. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1
79136 | 1 | Profile | Base | Error | Monitor error status for current profile step. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1
79137 | 1 | Profile | Base | Unknown | Monitor control loop 1 precision. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) |  | Enumeration | R | 1
79138 | 1 | Profile | Base | Unknown | Monitor control loop 2 precision. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) |  | Enumeration | R | 1
79139 | 1 | Profile | Base | Unknown | Monitor control loop 3 precision. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) |  | Enumeration | R | 1
79140 | 1 | Profile | Base | Unknown | Monitor control loop 4 precision. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) |  | Enumeration | R | 1
79141 | 1 | Profile | Base | Name | Monitor profile name. | 20 bytes (UTF-8) |  | String | R | 1
79142 | 1 | Profile | Base | Profile State | Monitor the profile status. | Off (62), Running (149), Pause (146), Not Started (251), Completed Normal (252), Terminated (253), Calendar Start (1783) | Off (62) | Enumeration | R | 1
79143 | 1 | Profile | Base |  | Monitor the number of steps for profile loaded in memory. | 0 to 50 | 0 | Unsigned 16-bit | R | 1
79144 | 1 | Profile | Base | Event 5 | Monitor/change current step Event Output 5 transmitter (EVT5) loaded in memory. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
79145 | 1 | Profile | Base | Event 6 | Monitor/change current step Event Output 6 transmitter (EVT6) loaded in memory. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
79146 | 1 | Profile | Base | Event 7 | Monitor/change current step Event Output 7 transmitter (EVT7) loaded in memory. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
79147 | 1 | Profile | Base | Event 8 | Monitor/change current step Event Output 8 transmitter (EVT8) loaded in memory. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
79152 | 1 | Profile | Base | Error | Monitor error status for produced Event Output 5 transmitter (EVT5). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1
79153 | 1 | Profile | Base | Error | Monitor error status for produced Event Output 6 transmitter (EVT6). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1
79154 | 1 | Profile | Base | Error | Monitor error status for produced Event Output 7 transmitter (EVT7). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1
79155 | 1 | Profile | Base | Error | Monitor error status for produced Event Output 8 transmitter (EVT8). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1
80000 | 0 | Profile | Base |  | Profile Active Attribute Enable. |  |  |  |  | 1
80001 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 1
80002 | 1 | Profile | Base | Profile Number | Set the profile number to work with. | 1 to 40 | 1 | Unsigned 16-bit | R/W | 1
80003 | 1 | Profile | Base | Profile Action Request | Set the profile edit action. | Edit (1770), Add (1375), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80004 | 1 | Profile | Base | Name | Set the file name. | 20 bytes (UTF-8) |  | String | R/W | 1
80005 | 1 | Profile | Base | Units | Set the units for the control loop. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) | Not Sourced (246) | Enumeration | R/W | 1
80006 | 1 | Profile | Base | Units | Set the units for the control loop. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) | Not Sourced (246) | Enumeration | R/W | 1
80007 | 1 | Profile | Base | Units | Set the units for the control loop. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) | Not Sourced (246) | Enumeration | R/W | 1
80008 | 1 | Profile | Base | Units | Set the units for the control loop. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) | Not Sourced (246) | Enumeration | R/W | 1
80009 | 1 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 1 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 1 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 1 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80014 | 1 | Profile | Base | Units | Set the unit used for the wait for steps. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) | Not Sourced (246) | Enumeration | R/W | 1
80015 | 1 | Profile | Base | Units | Set the unit used for the wait for steps. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) | Not Sourced (246) | Enumeration | R/W | 1
80016 | 1 | Profile | Base | Units | Set the unit used for the wait for steps. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) | Not Sourced (246) | Enumeration | R/W | 1
80017 | 1 | Profile | Base | Units | Set the unit used for the wait for steps. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) | Not Sourced (246) | Enumeration | R/W | 1
80018 | 1 | Profile | Base | Count | Monitor the number of steps for profile loaded in memory. | 1 to 50 | 1 | Unsigned 8-bit | R | 1
80019 | 1 | Profile | Base |  | Set the step action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80020 | 1 | Profile | Base | Current Step | Current step. |  | 1 | Unsigned 16-bit | R/W | 1
80021 | 1 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 1 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 1 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 1 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 1 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 1 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 1 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 1 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 1 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 1 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 1 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 1 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 1 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 1 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 1 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 1 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 1 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 1 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 1 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 1 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 1 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 1 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 1 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 1 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 1 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 1 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 1 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 1 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 1 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 1 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80064 | 1 | Profile | Base |  | Monitor to see if profile is available to be Setmed. | Yes (106), No (59) |  | Enumeration | R/W | 1
80065 | 1 | Profile | Base | Unknown | Set display units. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 1
80066 | 1 | Profile | Base | Unknown | Set display units. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 1
80067 | 1 | Profile | Base | Unknown | Set display units. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 1
80068 | 1 | Profile | Base | Unknown | Set display units. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 1
80069 | 1 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 1 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 1 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 1 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 1 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 1 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 1 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 1 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80077 | 1 | Profile | Base | Log Data | Set to enable data log in profile. | No (59), Yes (106) | No (59) | Enumeration | R/W | 1
80009 | 2 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 2 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 2 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 2 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 2 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 2 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 2 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 2 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 2 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 2 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 2 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 2 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 2 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 2 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 2 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 2 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 2 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 2 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 2 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 2 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 2 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 2 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 2 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 2 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 2 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 2 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 2 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 2 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 2 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 2 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 2 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 2 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 2 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 2 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 2 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 2 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 2 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 2 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 2 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 2 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 2 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 2 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 2 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 3 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 3 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 3 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 3 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 3 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 3 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 3 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 3 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 3 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 3 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 3 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 3 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 3 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 3 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 3 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 3 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 3 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 3 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 3 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 3 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 3 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 3 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 3 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 3 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 3 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 3 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 3 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 3 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 3 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 3 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 3 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 3 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 3 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 3 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 3 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 3 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 3 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 3 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 3 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 3 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 3 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 3 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 3 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 4 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 4 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 4 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 4 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 4 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 4 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 4 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 4 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 4 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 4 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 4 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 4 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 4 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 4 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 4 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 4 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 4 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 4 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 4 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 4 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 4 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 4 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 4 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 4 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 4 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 4 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 4 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 4 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 4 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 4 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 4 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 4 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 4 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 4 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 4 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 4 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 4 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 4 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 4 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 4 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 4 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 4 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 4 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 5 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 5 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 5 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 5 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 5 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 5 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 5 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 5 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 5 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 5 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 5 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 5 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 5 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 5 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 5 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 5 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 5 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 5 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 5 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 5 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 5 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 5 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 5 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 5 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 5 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 5 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 5 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 5 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 5 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 5 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 5 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 5 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 5 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 5 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 5 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 5 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 5 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 5 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 5 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 5 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 5 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 5 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 5 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 6 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 6 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 6 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 6 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 6 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 6 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 6 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 6 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 6 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 6 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 6 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 6 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 6 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 6 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 6 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 6 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 6 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 6 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 6 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 6 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 6 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 6 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 6 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 6 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 6 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 6 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 6 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 6 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 6 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 6 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 6 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 6 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 6 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 6 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 6 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 6 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 6 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 6 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 6 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 6 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 6 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 6 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 6 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 7 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 7 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 7 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 7 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 7 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 7 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 7 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 7 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 7 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 7 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 7 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 7 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 7 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 7 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 7 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 7 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 7 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 7 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 7 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 7 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 7 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 7 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 7 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 7 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 7 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 7 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 7 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 7 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 7 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 7 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 7 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 7 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 7 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 7 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 7 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 7 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 7 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 7 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 7 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 7 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 7 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 7 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 7 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 8 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 8 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 8 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 8 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 8 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 8 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 8 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 8 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 8 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 8 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 8 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 8 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 8 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 8 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 8 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 8 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 8 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 8 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 8 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 8 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 8 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 8 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 8 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 8 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 8 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 8 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 8 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 8 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 8 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 8 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 8 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 8 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 8 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 8 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 8 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 8 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 8 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 8 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 8 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 8 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 8 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 8 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 8 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 9 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 9 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 9 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 9 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 9 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 9 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 9 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 9 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 9 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 9 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 9 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 9 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 9 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 9 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 9 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 9 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 9 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 9 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 9 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 9 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 9 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 9 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 9 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 9 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 9 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 9 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 9 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 9 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 9 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 9 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 9 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 9 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 9 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 9 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 9 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 9 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 9 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 9 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 9 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 9 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 9 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 9 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 10 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 10 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 10 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 10 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 10 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 10 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 10 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 10 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 10 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 10 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 10 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 10 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 10 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 10 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 10 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 10 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 10 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 10 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 10 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 10 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 10 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 10 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 10 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 10 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 10 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 10 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 10 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 10 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 10 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 10 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 10 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 10 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 10 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 10 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 10 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 10 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 10 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 10 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 10 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 10 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 10 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 10 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 11 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 11 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 11 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 11 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 11 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 11 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 11 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 11 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 11 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 11 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 11 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 11 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 11 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 11 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 11 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 11 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 11 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 11 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 11 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 11 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 11 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 11 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 11 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 11 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 11 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 11 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 11 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 11 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 11 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 11 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 11 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 11 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 11 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 11 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 11 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 11 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 11 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 11 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 11 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 11 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 11 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 11 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 12 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 12 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 12 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 12 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 12 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 12 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 12 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 12 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 12 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 12 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 12 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 12 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 12 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 12 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 12 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 12 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 12 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 12 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 12 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 12 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 12 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 12 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 12 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 12 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 12 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 12 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 12 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 12 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 12 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 12 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 12 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 12 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 12 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 12 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 12 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 12 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 12 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 12 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 12 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 12 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 12 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 12 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 13 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 13 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 13 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 13 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 13 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 13 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 13 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 13 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 13 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 13 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 13 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 13 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 13 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 13 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 13 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 13 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 13 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 13 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 13 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 13 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 13 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 13 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 13 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 13 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 13 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 13 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 13 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 13 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 13 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 13 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 13 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 13 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 13 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 13 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 13 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 13 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 13 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 13 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 13 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 13 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 13 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 13 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 13 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 14 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 14 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 14 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 14 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 14 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 14 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 14 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 14 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 14 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 14 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 14 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 14 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 14 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 14 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 14 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 14 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 14 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 14 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 14 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 14 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 14 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 14 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 14 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 14 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 14 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 14 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 14 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 14 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 14 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 14 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 14 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 14 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 14 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 14 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 14 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 14 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 14 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 14 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 14 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 14 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 14 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 14 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 14 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 15 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 15 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 15 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 15 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 15 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 15 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 15 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 15 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 15 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 15 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 15 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 15 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 15 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 15 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 15 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 15 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 15 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 15 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 15 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 15 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 15 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 15 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 15 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 15 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 15 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 15 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 15 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 15 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 15 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 15 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 15 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 15 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 15 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 15 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 15 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 15 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 15 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 15 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 15 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 15 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 15 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 15 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 15 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 16 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 16 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 16 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 16 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 16 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 16 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 16 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 16 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 16 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 16 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 16 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 16 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 16 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 16 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 16 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 16 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 16 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 16 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 16 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 16 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 16 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 16 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 16 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 16 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 16 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 16 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 16 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 16 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 16 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 16 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 16 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 16 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 16 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 16 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 16 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 16 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 16 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 16 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 16 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 16 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 16 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 16 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 16 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 17 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 17 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 17 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 17 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 17 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 17 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 17 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 17 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 17 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 17 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 17 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 17 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 17 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 17 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 17 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 17 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 17 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 17 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 17 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 17 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 17 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 17 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 17 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 17 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 17 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 17 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 17 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 17 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 17 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 17 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 17 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 17 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 17 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 17 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 17 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 17 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 17 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 17 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 17 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 17 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 17 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 17 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 17 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 18 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 18 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 18 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 18 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 18 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 18 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 18 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 18 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 18 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 18 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 18 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 18 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 18 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 18 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 18 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 18 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 18 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 18 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 18 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 18 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 18 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 18 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 18 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 18 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 18 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 18 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 18 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 18 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 18 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 18 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 18 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 18 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 18 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 18 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 18 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 18 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 18 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 18 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 18 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 18 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 18 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 18 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 18 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 19 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 19 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 19 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 19 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 19 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 19 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 19 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 19 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 19 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 19 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 19 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 19 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 19 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 19 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 19 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 19 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 19 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 19 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 19 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 19 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 19 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 19 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 19 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 19 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 19 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 19 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 19 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 19 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 19 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 19 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 19 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 19 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 19 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 19 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 19 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 19 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 19 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 19 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 19 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 19 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 19 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 19 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 20 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 20 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 20 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 20 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 20 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 20 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 20 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 20 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 20 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 20 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 20 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 20 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 20 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 20 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 20 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 20 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 20 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 20 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 20 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 20 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 20 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 20 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 20 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 20 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 20 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 20 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 20 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 20 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 20 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 20 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 20 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 20 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 20 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 20 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 20 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 20 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 20 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 20 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 20 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 20 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 20 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 20 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 20 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 21 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 21 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 21 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 21 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 21 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 21 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 21 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 21 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 21 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 21 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 21 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 21 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 21 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 21 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 21 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 21 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 21 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 21 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 21 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 21 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 21 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 21 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 21 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 21 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 21 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 21 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 21 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 21 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 21 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 21 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 21 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 21 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 21 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 21 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 21 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 21 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 21 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 21 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 21 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 21 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 21 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 21 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 22 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 22 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 22 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 22 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 22 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 22 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 22 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 22 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 22 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 22 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 22 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 22 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 22 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 22 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 22 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 22 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 22 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 22 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 22 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 22 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 22 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 22 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 22 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 22 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 22 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 22 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 22 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 22 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 22 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 22 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 22 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 22 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 22 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 22 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 22 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 22 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 22 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 22 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 22 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 22 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 22 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 22 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 23 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 23 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 23 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 23 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 23 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 23 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 23 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 23 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 23 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 23 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 23 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 23 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 23 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 23 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 23 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 23 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 23 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 23 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 23 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 23 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 23 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 23 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 23 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 23 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 23 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 23 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 23 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 23 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 23 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 23 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 23 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 23 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 23 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 23 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 23 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 23 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 23 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 23 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 23 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 23 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 23 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 23 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 24 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 24 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 24 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 24 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 24 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 24 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 24 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 24 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 24 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 24 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 24 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 24 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 24 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 24 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 24 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 24 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 24 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 24 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 24 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 24 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 24 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 24 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 24 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 24 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 24 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 24 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 24 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 24 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 24 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 24 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 24 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 24 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 24 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 24 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 24 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 24 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 24 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 24 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 24 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 24 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 24 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 24 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 25 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 25 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 25 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 25 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 25 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 25 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 25 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 25 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 25 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 25 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 25 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 25 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 25 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 25 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 25 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 25 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 25 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 25 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 25 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 25 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 25 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 25 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 25 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 25 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 25 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 25 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 25 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 25 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 25 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 25 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 25 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 25 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 25 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 25 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 25 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 25 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 25 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 25 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 25 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 25 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 25 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 25 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 26 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 26 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 26 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 26 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 26 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 26 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 26 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 26 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 26 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 26 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 26 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 26 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 26 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 26 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 26 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 26 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 26 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 26 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 26 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 26 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 26 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 26 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 26 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 26 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 26 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 26 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 26 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 26 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 26 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 26 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 26 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 26 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 26 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 26 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 26 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 26 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 26 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 26 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 26 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 26 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 26 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 26 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 27 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 27 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 27 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 27 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 27 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 27 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 27 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 27 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 27 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 27 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 27 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 27 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 27 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 27 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 27 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 27 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 27 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 27 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 27 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 27 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 27 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 27 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 27 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 27 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 27 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 27 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 27 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 27 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 27 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 27 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 27 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 27 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 27 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 27 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 27 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 27 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 27 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 27 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 27 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 28 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 28 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 28 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 28 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 28 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 28 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 28 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 28 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 28 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 28 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 28 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 28 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 28 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 28 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 28 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 28 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 28 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 28 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 28 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 28 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 28 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 28 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 28 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 28 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 28 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 28 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 28 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 28 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 28 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 28 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 28 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 28 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 28 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 28 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 28 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 28 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 28 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 28 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 28 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 29 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 29 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 29 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 29 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 29 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 29 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 29 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 29 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 29 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 29 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 29 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 29 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 29 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 29 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 29 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 29 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 29 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 29 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 29 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 29 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 29 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 29 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 29 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 29 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 29 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 29 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 29 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 29 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 29 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 29 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 29 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 29 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 29 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 29 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 29 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 29 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 29 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 29 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 29 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 30 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 30 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 30 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 30 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 30 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 30 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 30 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 30 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 30 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 30 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 30 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 30 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 30 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 30 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 30 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 30 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 30 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 30 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 30 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 30 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 30 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 30 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 30 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 30 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 30 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 30 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 30 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 30 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 30 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 30 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 30 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 30 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 30 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 30 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 30 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 30 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 30 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 30 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 30 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 31 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 31 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 31 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 31 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 31 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 31 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 31 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 31 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 31 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 31 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 31 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 31 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 31 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 31 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 31 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 31 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 31 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 31 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 31 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 31 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 31 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 31 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 31 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 31 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 31 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 31 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 31 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 31 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 31 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 31 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 31 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 31 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 31 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 31 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 31 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 31 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 31 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 31 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 31 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 31 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 31 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 31 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 32 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 32 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 32 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 32 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 32 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 32 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 32 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 32 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 32 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 32 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 32 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 32 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 32 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 32 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 32 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 32 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 32 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 32 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 32 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 32 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 32 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 32 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 32 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 32 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 32 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 32 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 32 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 32 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 32 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 32 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 32 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 32 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 32 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 32 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 32 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 32 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 32 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 32 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 32 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 32 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 32 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 32 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 33 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 33 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 33 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 33 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 33 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 33 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 33 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 33 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 33 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 33 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 33 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 33 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 33 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 33 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 33 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 33 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 33 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 33 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 33 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 33 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 33 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 33 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 33 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 33 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 33 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 33 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 33 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 33 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 33 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 33 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 33 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 33 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 33 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 33 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 33 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 33 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 33 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 33 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 33 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 33 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 33 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 33 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 34 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 34 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 34 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 34 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 34 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 34 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 34 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 34 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 34 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 34 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 34 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 34 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 34 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 34 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 34 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 34 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 34 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 34 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 34 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 34 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 34 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 34 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 34 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 34 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 34 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 34 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 34 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 34 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 34 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 34 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 34 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 34 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 34 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 34 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 34 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 34 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 34 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 34 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 34 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 34 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 34 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 34 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 35 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 35 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 35 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 35 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 35 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 35 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 35 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 35 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 35 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 35 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 35 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 35 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 35 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 35 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 35 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 35 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 35 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 35 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 35 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 35 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 35 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 35 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 35 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 35 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 35 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 35 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 35 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 35 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 35 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 35 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 35 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 35 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 35 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 35 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 35 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 35 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 35 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 35 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 35 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 35 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 35 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 35 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 36 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 36 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 36 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 36 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 36 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 36 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 36 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 36 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 36 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 36 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 36 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 36 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 36 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 36 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 36 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 36 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 36 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 36 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 36 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 36 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 36 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 36 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 36 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 36 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 36 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 36 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 36 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 36 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 36 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 36 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 36 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 36 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 36 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 36 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 36 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 36 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 36 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 36 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 36 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 36 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 36 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 36 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 37 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 37 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 37 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 37 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 37 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 37 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 37 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 37 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 37 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 37 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 37 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 37 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 37 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 37 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 37 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 37 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 37 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 37 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 37 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 37 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 37 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 37 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 37 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 37 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 37 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 37 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 37 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 37 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 37 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 37 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 37 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 37 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 37 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 37 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 37 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 37 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 37 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 37 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 37 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 37 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 37 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 37 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 38 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 38 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 38 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 38 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 38 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 38 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 38 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 38 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 38 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 38 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 38 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 38 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 38 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 38 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 38 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 38 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 38 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 38 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 38 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 38 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 38 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 38 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 38 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 38 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 38 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 38 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 38 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 38 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 38 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 38 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 38 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 38 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 38 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 38 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 38 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 38 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 38 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 38 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 38 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 38 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 38 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 38 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 39 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 39 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 39 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 39 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 39 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 39 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 39 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 39 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 39 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 39 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 39 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 39 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 39 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 39 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 39 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 39 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 39 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 39 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 39 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 39 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 39 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 39 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 39 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 39 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 39 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 39 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 39 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 39 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 39 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 39 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 39 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 39 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 39 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 39 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 39 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 39 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 39 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 39 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 39 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 39 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 39 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 39 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 40 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 40 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 40 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 40 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 40 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 40 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 40 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 40 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 40 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 40 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 40 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 40 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 40 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 40 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 40 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 40 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 40 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 40 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 40 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 40 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 40 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 40 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 40 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 40 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 40 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 40 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 40 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 40 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 40 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 40 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 40 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 40 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 40 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 40 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 40 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 40 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 40 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 40 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 40 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 40 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 40 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 40 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 41 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 41 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 41 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 41 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 41 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 41 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 41 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 41 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 41 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 41 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 41 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 41 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 41 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 41 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 41 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 41 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 41 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 41 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 41 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 41 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 41 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 41 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 41 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 41 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 41 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 41 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 41 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 41 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 41 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 41 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 41 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 41 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 41 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 41 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 41 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 41 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 41 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 41 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 41 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 41 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 41 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 41 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 42 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 42 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 42 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 42 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 42 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 42 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 42 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 42 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 42 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 42 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 42 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 42 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 42 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 42 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 42 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 42 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 42 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 42 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 42 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 42 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 42 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 42 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 42 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 42 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 42 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 42 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 42 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 42 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 42 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 42 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 42 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 42 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 42 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 42 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 42 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 42 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 42 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 42 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 42 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 42 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 42 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 42 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 43 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 43 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 43 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 43 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 43 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 43 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 43 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 43 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 43 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 43 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 43 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 43 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 43 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 43 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 43 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 43 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 43 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 43 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 43 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 43 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 43 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 43 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 43 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 43 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 43 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 43 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 43 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 43 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 43 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 43 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 43 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 43 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 43 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 43 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 43 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 43 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 43 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 43 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 43 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 43 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 43 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 43 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 44 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 44 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 44 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 44 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 44 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 44 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 44 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 44 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 44 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 44 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 44 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 44 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 44 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 44 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 44 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 44 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 44 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 44 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 44 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 44 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 44 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 44 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 44 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 44 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 44 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 44 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 44 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 44 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 44 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 44 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 44 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 44 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 44 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 44 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 44 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 44 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 44 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 44 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 44 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 44 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 44 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 44 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 45 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 45 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 45 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 45 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 45 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 45 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 45 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 45 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 45 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 45 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 45 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 45 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 45 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 45 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 45 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 45 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 45 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 45 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 45 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 45 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 45 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 45 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 45 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 45 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 45 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 45 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 45 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 45 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 45 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 45 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 45 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 45 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 45 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 45 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 45 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 45 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 45 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 45 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 45 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 45 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 45 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 45 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 46 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 46 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 46 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 46 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 46 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 46 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 46 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 46 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 46 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 46 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 46 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 46 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 46 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 46 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 46 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 46 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 46 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 46 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 46 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 46 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 46 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 46 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 46 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 46 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 46 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 46 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 46 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 46 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 46 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 46 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 46 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 46 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 46 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 46 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 46 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 46 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 46 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 46 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 46 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 46 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 46 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 46 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 47 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 47 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 47 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 47 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 47 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 47 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 47 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 47 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 47 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 47 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 47 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 47 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 47 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 47 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 47 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 47 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 47 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 47 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 47 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 47 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 47 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 47 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 47 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 47 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 47 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 47 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 47 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 47 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 47 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 47 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 47 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 47 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 47 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 47 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 47 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 47 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 47 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 47 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 47 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 47 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 47 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 47 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 48 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 48 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 48 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 48 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 48 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 48 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 48 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 48 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 48 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 48 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 48 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 48 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 48 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 48 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 48 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 48 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 48 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 48 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 48 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 48 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 48 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 48 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 48 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 48 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 48 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 48 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 48 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 48 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 48 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 48 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 48 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 48 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 48 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 48 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 48 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 48 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 48 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 48 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 48 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 48 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 48 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 48 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 49 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 49 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 49 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 49 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 49 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 49 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 49 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 49 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 49 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 49 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 49 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 49 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 49 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 49 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 49 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 49 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 49 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 49 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 49 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 49 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 49 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 49 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 49 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 49 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 49 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 49 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 49 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 49 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 49 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 49 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 49 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 49 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 49 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 49 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 49 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 49 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 49 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 49 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 49 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 49 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 49 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 49 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80009 | 50 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80010 | 50 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80011 | 50 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80012 | 50 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 1
80019 | 50 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 1
80021 | 50 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 1
80022 | 50 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 1
80023 | 50 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80024 | 50 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 1
80025 | 50 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 1
80026 | 50 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 1
80027 | 50 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80028 | 50 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80029 | 50 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80030 | 50 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80031 | 50 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80032 | 50 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80033 | 50 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80034 | 50 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 1
80035 | 50 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80036 | 50 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80037 | 50 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80038 | 50 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80039 | 50 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80040 | 50 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80041 | 50 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 1
80042 | 50 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 1
80043 | 50 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80044 | 50 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80045 | 50 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80046 | 50 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1
80047 | 50 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80048 | 50 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80049 | 50 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80050 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80069 | 50 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80070 | 50 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80071 | 50 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80072 | 50 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 1
80073 | 50 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80074 | 50 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80075 | 50 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
80076 | 50 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 1
91001 | 1 | Message | Base | Message Enable | Set to enable message. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
91002 | 1 | Message | Base | Message | Set message to be displayed based on trigger. | 20 bytes (UTF-8) |  | String | R/W | 4
91001 | 2 | Message | Base | Message Enable | Set to enable message. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
91002 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 20 bytes (UTF-8) |  | String | R/W | 4
91001 | 3 | Message | Base | Message Enable | Set to enable message. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
91002 | 3 | Message | Base | Message | Set message to be displayed based on trigger. | 20 bytes (UTF-8) |  | String | R/W | 4
91001 | 4 | Message | Base | Message Enable | Set to enable message. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4
91002 | 4 | Message | Base | Message | Set message to be displayed based on trigger. | 20 bytes (UTF-8) |  | String | R/W | 4