## ReadMeFirst
This register list is supplied as an aid to determine the appropriate data points or tags to access desired data from the F4T or D4T using a PC/PLC/HMI. The F4T/D4T is a slave device and does not initiate any transactions; the F4T/D4T being standalone devices and (PC/PLC/HMI being a supervisor). The F4T/D4T does not have a communications watchdog feature. Do not rely on the supervisor to initiate emergency shutdown operations but incorporate other safety devices in the system such as limits as necessary. The D4T model does not contain control loops. It purpose is primarily for data acquisition/data logging/data display. The F4T/D4T supports several protocols including Standard Bus over Ethernet (accessed by Parameter ID, and Instance), Modbus RTU over serial connection (accessed by Modbus registers in relative format), Modbus TCP over Ethernet (accessed by Modbus registers in relative format), SCPI over serial connection (accessed by SCPI ASCII commands) and EtherNet/IP (accessed by Class ID, Instance ID and Attribute ID). Standard Bus is a Watlow proprietary protocol used with Watlow supplied software such as Composer, Watlow Standard Bus driver for LabVIEW or SpecVIEW by Watlow. It uses port 44819 for connection. Modbus is an open protocol - see http://www.modbus.org for more detail. It uses port 502 for Modbus TCP for connection. SCPI is an open ASCII protocol used by many instruments and supported in LabVIEW. It uses port 5025 for connection. There are multiple spreadsheet tabs supplied each providing data for different purposes: > Classes – List of the supported object types available depending on model number and ordering options. > Instances – List the instances available for quantity of objects of same type based on hardware purchased. > Modbus Map 1 – List the tags by protocol when the F4T/D4T is set use Map 1 register reservation. > Modbus Map 2 – List the tags by legacy Modbus protocol when the F4T/D4T is set to use Map 2 register reservation. Not recommended for new applications. This is intended for backwards compatibility to legacy F4S, F4D and F4P models. A limited set of registers is provided. > Modbus Map 3 – List the tags by legacy Modbus protocol when the F4T/D4T is set to use Map 3 register reservation. Not recommended for new applications. This is intended for backwards compatibility to legacy F4S, F4D and F4P models with cascade control. A limited set of registers is provided. > SCPI – List the tags for the SCPI ASCII protocol. A limited set of registers is provided. > EtherNet IP – List the tags for the EtherNet/IP protocol. This protocol is used primarily by Allen Bradley PLCs. The tags listed are identified as supporting Implicit messaging or not. Those that are not supported must be accessed via a message instruction (explicitly). Use the Class, Instance and Attribute ID to send a message instruction to a specific tag. Note the class, instance and attribute are in decimal format and may need to be converted to hexadecimal for some PLCs. > LabVIEW – List the tags for the Standard Bus protocol. A parameter id and instance is used to define each tag. Enumerations decode a read/written value from/to a register in the Standard Bus, Modbus and EtherNet/IP protocols. Registers contains either floating point values such as sensor value or an enumerated value representing a choice such as ""YES"" or ""NO"". The sheet provides a means to see what an enumerated value represents. None of the registers contain coil or bit data. These contain a 32-bit floating point analog value or an enumerated 16-bit value decoded by this sheet. In each sheet, use column filters in Class Name to quickly locate relevant parameters for a particular function. Further apply filters on other columns to reduce the choices within the class. Instance determines which of the many is being referenced and attribute references a tag within the class. Afterwards, depending on the protocol (Modbus TCP, Modbus RTU, EtherNet/IP or LabVIEW), locate the appropriate tag. The remaining columns define the parameter name, range of values, default values, and data type as well as read/write status. If you find rows or columns not displayed, check that the rows/columns have not been hidden or a filter applied. Several of the spreadsheets have filters enabled to allow quick sort to a group of tags. This is where the sheets describing the class can be beneficial as a group of tags can be displayed by class and then instance. Instead of wading through thousands of entries; just the desired few are displayed. The spreadsheet being viewed is an uncontrolled document meant to supplement the User's Guide. Although every attempt has been made to ensure accuracy of the latest available tags, errors are bound to occur with this much data. If questions arise on the accuracy or data provided, contact Watlow Technical Support at (507) 494-5656 between the hours of 7AM and 5PM CST. Note that if the F4T/D4T is in an OEM piece of equipment such as an oven or chamber, your first contact should be to the OEM who programmed and wired the controller to their system and may have applied security to prevent certain tags from being accessed. In addition, multiple tags depend on firmware revisions and options included on the F4T or D4T. There has been no attempt to identify the provided tags to a specific firmware revision. Some sheets contain a column to help the user understand what hardware or ordering option must have been installed to access those tags. When contacting Watlow Technical Support, please be prepared with the complete F4T base model number, model number of each card installed in slots 1 to 6 and data on how the controller is programmed. Record the firmware revision shown on the F4T/D4T screen under the question key and about. The software Composer is available free on the Watlow web site which may be used by an Ethernet connection to capture all settings to a WSI (Watlow System Image) file. Technical Support may request the file emailed to wintechsupport@watlow.com. You may wish to send other questions using this same email address for convenience." Note: Never write to registers that are not defined or validated to be correct to prevent unintentional change. Avoid accessing hidden registers or non-existent instances as unpredictable results may occur.

## Classes
﻿Class Name | Description
Alarm | Use an alarm block to monitor an analog signal and set an output when that signal goes above or below the user-set alarm conditions.
Analog Output | Use an analog output block to operate an external device that takes an analog or process signal such as 4 to 20 mADC or 0 to 10 VDC. Class is dependent on module type in slot.
Profile Common Editor | Use the profile common editor to define the 50 steps of each profile. Profiling is defining the sequence of set points and events over time in a recipe call a profile. The steps may change set points over time, maintain set points over time, change digital outputs at a given step and repeat a sequence of defined steps. User may name the profile with 20 characters. Class is dependent on Profiling option.
Profile Engine / Runtime | Use the profile configuration to configure the interaction of profile to control loops and events. In addition, use to monitor/mange profile activity. The profile engine links the controller’s profiling feature with the inputs, outputs and other controller functions. It provides a way to integrate the use of profiles with the application as a whole. Class is dependent on Profiling option.
Assembly Pointers | Use the assembly pointers to define a block of user assigned registers.
Assembly Status Data | Use the assembly status data to read/write the values of the assembly pointers.
Control Loop | Use a control loop block to manipulate a temperature or other process value. Class is dependent on Control Algorithm option.
Compare | Use a compare block to set an output based on comparing two analog signals. Class is dependent on Function Block option.
Cascade Loop | Use a cascade loop block to manipulate a temperature or other process value using advanced cascade control method. Cascade is two loops of control inside one block having two analog inputs controlling one load. Class is dependent on Cascade Algorithm option.
Counter | Use a counter block to set an output when a digital signal’s state changes a given number of times. Class is dependent on Function Block set option.
Current | Use a current input block to detect current flow in a load such as a heater and indicate a problem if one were to occur, such as an open or short circuit. Class is dependent on module type in slot.
Device | Use device parameters to monitor information on F4T base and modules in slots 1 to 6.
Digital Input | Use a digital input block to integrate signals from field devices in to the application. Class is dependent on module type in slot.
Digital Input/Output | Use a digital input/output block to connect a field I/O device’s signal to the application. Class is dependent on module type in slot.
Digital Output (Fast) | Use a digital output block to drive an external device. The Digital Output (Fast) is solid state in nature and may be switched very quickly. Class is dependent on module type in slot.
Digital Output (Limit) | Use a digital output block to drive an external device. The Digital Output (Limit) is mechanical in nature and dedicated to the limit contactor. Class is dependent on module type in slot.
Digital Output (Slow) | Use a digital output block to drive an external device. The Digital Output (Slow) is mechanical in nature and must be switched very slowly to prevent hardware failure. Class is dependent on module type in slot.
Display | Use display block to set units of display on touch screen. Does not affect temperature units transferred by communications.
Ethernet | Use the Ethernet block to configure the parameters for Modbus TCP and Standard Bus communications.
Key | Use a key block to configure/monitor a softkey on screen of F4T.
Logic | Use a logic block to set an output based on one or more digital signals. The logic block performs logic operations on one or more digital inputs and sets its output based on the result. Class is dependent on Function Block set option.
Limit | Use a limit block as a safety shutoff to disconnect the energy source from a system to prevent damage and/or injury in the event of a failure. This block drives the output that is used to enable or disable the energy source associated with the limit sensor. It cannot be disconnected from the Limit block or connected to any other function. Class is dependent on card type in slot.
Linearization | Use a linearize block to scale an analog signal according to a 10-point scaling curve plus an offset.
Logging | Use the logging block to configure the behavior of logged parameters and transfer of data log. Class is dependent on ordering option.
Log Point | Use the log point block to define the parameters to be data logged. Class is dependent on ordering option.
Math | Use a math block to set an output based on performing the selected math function on up to four analog inputs. A filter and offset may be applied to the calculated value. A digital input enables or disables some of the math functions. Class is dependent on Function Block set option.
Modbus (RTU) | Use the Modbus block to configure the serial connection for Modbus RTU. Class is dependent on card type in slot 6.
Message | Use the message block to activate a message displayed on touch screen via a communication's command.
Profile Start | Class is dependent on Profiling option.
Process Value | Use a process value block to produce a conditioned analog signal based on up to four analog signals and one digital signal. A filter and offset may be applied to the function’s output.
Real Time Clock | Use the real time clock to configure/monitor stored time settings. Class is dependent on Profile or Data Log options.
Special Output Function | Use special output function block to operate outputs for one of these applications: operating mechanical compressors, controlling a motorized valve or sequencing multiple output devices to switch large power loads. Class is dependent on Function Block set option.
Thermistor | Use a thermistor block to condition a temperature measurement made with a thermistor. Class us dependent on module type in slot.
Temperature | Use a temperature dedicated input card to condition a temperature measurement made with a thermocouple or RTD. Class is dependent on module type in slot.
Timer | Use a timer block when applications require timed control of a digital output or a delay to a digital output for a specific length of time. Class is dependent on Function Block set option.
User Interface Personalization | Use to personalize the home screen layout.
Universal Input | Use a universal input block to condition a measurement made with a thermocouple, RTD, potentiometer or another analog process signal. Class is dependent on module type in slot.
Variable | Use a variable block to store a digital or analog value used by other function block inputs.

## Instances
Class Name | Instance | Location | Appears if:
Device | 1 | F4T Base | Always
Device | 2 | Slot 1 | Card in slot
Device | 3 | Slot 2 | Card in slot
Device | 4 | Slot 3 | Card in slot
Device | 5 | Slot 4 | Card in slot
Device | 6 | Slot 5 | Card in slot
Device | 7 | Slot 6 | Card in slot
Assembly Status Data | 1, 25 | F4T Base | Always
Assembly Pointers | 1, 25 | F4T Base | Always
Display | 1 | F4T Base | Always
Alarm | 1 - 6 | F4T Base | Function Block Basic Set, digit 7 is A or D in F4T base
Alarm | 1 - 8 | F4T Base | Function Block Set 1, digit 7 is B or E in F4T base
Alarm | 1 - 14 | F4T Base | Function Block Set 2, digit 7 is C or F in F4T base
Profile Common Editor | 1 - 12 | F4T Base | Profile, digit 7 is D, E or F in F4T base
Analog Output | 1 | Slot 1 | FMMA-xFxx-Axxx in slot
Analog Output | 1 - 3 | Slot 1 | FMHA-FAAA-Axxx in slot
Analog Output | 11 | Slot 2 | FMMA-xFxx-Axxx in slot
Analog Output | 11 - 13 | Slot 2 | FMHA-FAAA-Axxx in slot
Analog Output | 21 | Slot 3 | FMMA-xFxx-Axxx in slot
Analog Output | 21 – 23 | Slot 3 | FMHA-FAAA-Axxx in slot
Analog Output | 31 | Slot 4 | FMMA-xFxx-Axxx in slot
Analog Output | 31 – 33 | Slot 4 | FMHA-FAAA-Axxx in slot
Analog Output | 41 | Slot 5 | FMMA-xFxx-Axxx in slot
Analog Output | 41 – 43 | Slot 5 | FMHA-FAAA-Axxx in slot
Analog Output | 51 | Slot 6 | FMMA-xFxx-Axxx in slot
Analog Output | 51 – 53 | Slot 6 | FMHA-FAAA-Axxx in slot
Profile Editor | 1 | F4T Base | Profile, digit 7 is D, E or F in F4T base
Cascade Loop | 1 | F4T Base | Control Algorithm is Cascade, digit 12 is 6, 7, 8, or 9 in F4T base
Cascade Loop | 1 - 2 | F4T Base | Control Algorithm is Cascade, digit 12 is A, B or C in F4T base
Control Loop | 1 | F4T Base | Control Algorithm is Control, digit 12 is 1, 7, or B in F4T base
Control Loop | 1 – 2 | F4T Base | Control Algorithm is Control, digit 12 is 2, 8, or C in F4T base
Control Loop | 1 – 3 | F4T Base | Control Algorithm is Control, digit 12 is 3 or 9 in F4T base
Control Loop | 1 - 4 | F4T Base | Control Algorithm is Control, digit 12 is 4 in F4T base
Compare | 1 - 4 | F4T Base | Function Block Set 1, digit 7 is B or E in F4T base
Compare | 1 - 16 | F4T Base | Function Block Set 2, digit 7 is C or F in F4T base
Counter | 1 - 4 | F4T Base | Function Block Set 1, digit 7 is B or E in F4T base
Counter | 1 - 16 | F4T Base | Function Block Set 2, digit 7 is C or F in F4T base
Current | 1 | Slot 1 | FMMA-CxxA-Axxx in slot
Current | 11 | Slot 2 | FMMA-CxxA-Axxx in slot
Current | 21 | Slot 3 | FMMA-CxxA-Axxx in slot
Current | 31 | Slot 4 | FMMA-CxxA-Axxx in slot
Current | 41 | Slot 5 | FMMA-CxxA-Axxx in slot
Current | 51 | Slot 6 | FMMA-CxxA-Axxx in slot
Digital Input | 2 | Slot 1 | FMLA-YEBA-Axxx in slot
Digital Input | 12 | Slot 2 | FMLA-YEBA-Axxx in slot
Digital Input | 22 | Slot 3 | FMLA-YEBA-Axxx in slot
Digital Input | 32 | Slot 4 | FMLA-YEBA-Axxx in slot
Digital Input | 42 | Slot 5 | FMLA-YEBA-Axxx in slot
Digital Input | 52 | Slot 6 | FMLA-YEBA-Axxx in slot
Digital Input Output | 1 - 6 | Slot 1 | FMHA-CAAA-Axxx in slot
Digital Input Output | 11 – 16 | Slot 2 | FMHA-CAAA-Axxx in slot
Digital Input Output | 21 – 26 | Slot 3 | FMHA-CAAA-Axxx in slot
Digital Input Output | 31 – 36 | Slot 4 | FMHA-CAAA-Axxx in slot
Digital Input Output | 41 – 46 | Slot 5 | FMHA-CAAA-Axxx in slot
Digital Input Output | 51 – 56 | Slot 6 | FMHA-CAAA-Axxx in slot
Digital Output Fast | 1 - 4 | Slot 1 | FMHA-[K,L]AAA-Axxx in slot
Digital Output Fast | 11 - 14 | Slot 2 | FMHA-[K,L]AAA-Axxx in slot
Digital Output Fast | 21 - 24 | Slot 3 | FMHA-[K,L]AAA-Axxx in slot
Digital Output Fast | 31 - 34 | Slot 4 | FMHA-[K,L]AAA-Axxx in slot
Digital Output Fast | 41 - 44 | Slot 5 | FMHA-[K,L]AAA-Axxx in slot
Digital Output Fast | 51 - 54 | Slot 6 | FMHA-[K,L]AAA-Axxx in slot
Digital Output Limit | 1 – 2 | Slot 1 | FMLA-xxJA-Axxx in slot
Digital Output Limit | 11 – 12 | Slot 2 | FMLA-xxJA-Axxx in slot
Digital Output Limit | 21 – 22 | Slot 3 | FMLA-xxJA-Axxx in slot
Digital Output Limit | 31 – 32 | Slot 4 | FMLA-xxJA-Axxx in slot
Digital Output Limit | 41 – 42 | Slot 5 | FMLA-xxJA-Axxx in slot
Digital Output Limit | 51 – 52 | Slot 6 | FMLA-xxJA-Axxx in slot
Digital Output Slow | 1 – 4 | Slot 1 | Mechanical Relay or NO-ARC relay in slot
Digital Output Slow | 11 – 14 | Slot 2 | Mechanical Relay or NO-ARC relay in slot
Digital Output Slow | 21 – 24 | Slot 3 | Mechanical Relay or NO-ARC relay in slot
Digital Output Slow | 31 – 34 | Slot 4 | Mechanical Relay or NO-ARC relay in slot
Digital Output Slow | 41 – 44 | Slot 5 | Mechanical Relay or NO-ARC relay in slot
Digital Output Slow | 51 – 54 | Slot 6 | Mechanical Relay or NO-ARC relay in slot
Ethernet | 1 | F4T Base | Always
Key | 1 - 4 | F4T Base | Always
Logic | 1 - 12 | F4T Base | Function Block Set 1, digit 7 is B or E in F4T base
Logic | 1 - 24 | F4T Base | Function Block Set 2, digit 7 is C or F in F4T base
Limit | 1 | Slot 1 | Limit card in slot
Limit | 11 | Slot 2 | Limit card in slot
Limit | 21 | Slot 3 | Limit card in slot
Limit | 31 | Slot 4 | Limit card in slot
Limit | 41 | Slot 5 | Limit card in slot
Limit | 51 | Slot 6 | Limit card in slot
Linearization | 1 - 4 | F4T Base | Function Block Basic Set or Set 1, digit 7 is A, B, D, or E in F4T base
Linearization | 1 - 8 | F4T Base | Function Block Set 2, digit 7 is C or F in F4T base
Log Setup | 1 | F4T Base | Data Logging digit 5 is J, L or M in F4T base
Log Point | 1 – 128 | F4T Base | Data Logging digit 5 is J, L or M in F4T base
Math | 1 - 12 | F4T Base | Function Block Set 1, digit 7 is B or E in F4T base
Math | 1 - 24 | F4T Base | Function Block Set 2, digit 7 is C or F in F4T base
Modbus RTU | 1 | Slot 6 | FMMA-CAAA-Axxx in slot
Message | 1 - 4 | F4T Base | Always
Profile Start | 1 | F4T Base | Profile, digit 7 is D, E, or F in F4T base
Process Value | 1 - 4 | F4T Base | Function Block Basic or Set 1, digit 7 is A, B, D, or E in F4T base
Process Value | 1 - 8 | F4T Base | Function Block Set 2, digit 7 is C or F in F4T base
Real Time Clock | 1 | F4T Base | Data Logging, digit 5 is J, K, L, M or Profile, digit 7 is D, E or F in F4T base
Special Output Function | 1 - 2 | F4T Base | Function Block Set 1, digit 7 is B or E in F4T base
Special Output Function | 1 - 4 | F4T Base | Function Block Set 2, digit 7 is C or F in F4T base
Thermistor | 1 | Slot 1 | FMMA-TxxA-Axxx in slot
Thermistor | 11 | Slot 2 | FMMA-TxxA-Axxx in slot
Thermistor | 21 | Slot 3 | FMMA-TxxA-Axxx in slot
Thermistor | 31 | Slot 4 | FMMA-TxxA-Axxx in slot
Thermistor | 41 | Slot 5 | FMMA-TxxA-Axxx in slot
Thermistor | 51 | Slot 6 | FMMA-TxxA-Axxx in slot
Thermistor | 1 - 4 | Slot 1 | FMHA-PAAA-Axxx in slot
Thermistor | 11 – 14 | Slot 2 | FMHA-PAAA-Axxx in slot
Thermistor | 21 – 24 | Slot 3 | FMHA-PAAA-Axxx in slot
Thermistor | 31 – 34 | Slot 4 | FMHA-PAAA-Axxx in slot
Thermistor | 41 – 44 | Slot 5 | FMHA-PAAA-Axxx in slot
Thermistor | 51 – 54 | Slot 6 | FMHA-PAAA-Axxx in slot
Temperature Input | 1 | Slot 1 | FMLA-YEB-Axxx in slot
Temperature Input | 11 | Slot 2 | FMLA-YEB-Axxx in slot
Temperature Input | 21 | Slot 3 | FMLA-YEB-Axxx in slot
Temperature Input | 31 | Slot 4 | FMLA-YEB-Axxx in slot
Temperature Input | 41 | Slot 5 | FMLA-YEB-Axxx in slot
Temperature Input | 51 | Slot 6 | FMLA-YEB-Axxx in slot
Timer | 1 - 6 | F4T Base | Function Block Set 1, digit 7 is B or E in F4T base
Timer | 1 - 16 | F4T Base | Function Block Set 2, digit 7 is C or F in F4T base
User Interface | 1 | F4T Base | Always
Universal Input | 1 | Slot 1 | FMMA-UxxA-Axxx in slot
Universal Input | 11 | Slot 2 | FMMA-UxxA-Axxx in slot
Universal Input | 21 | Slot 3 | FMMA-UxxA-Axxx in slot
Universal Input | 31 | Slot 4 | FMMA-UxxA-Axxx in slot
Universal Input | 41 | Slot 5 | FMMA-UxxA-Axxx in slot
Universal Input | 51 | Slot 6 | FMMA-UxxA-Axxx in slot
Universal Input | 1 - 4 | Slot 1 | FMHA-RAAA-Axxx in slot
Universal Input | 11 – 14 | Slot 2 | FMHA-RAAA-Axxx in slot
Universal Input | 21 – 24 | Slot 3 | FMHA-RAAA-Axxx in slot
Universal Input | 31 – 34 | Slot 4 | FMHA-RAAA-Axxx in slot
Universal Input | 41 – 44 | Slot 5 | FMHA-RAAA-Axxx in slot
Universal Input | 51 – 54 | Slot 6 | FMHA-RAAA-Axxx in slot
Variable | 1 - 4 | F4T Base | Function Block Basic Set, digit 7 is A or D in F4T base
Variable | 1 - 12 | F4T Base | Function Block Set 1, digit 7 is B or E in F4T base
Variable | 1 - 24 | F4T Base | Function Block Set 2, digit 7 is C or F in F4T base

## Modbus Map 1
Standard Bus Class ID | Standard Bus Instance ID | Standard Bus Member ID | Class Name | Module | Member Name | Description | Range/Enumerations | Default Value | Data Type | Access | Relative Address | Absolute Address
1 | 1 | 1 | Device | Base | Hardware ID | Monitor the hardware ID. | 0 to 65,535 | 124 | Signed 32-bit | R | 0 | 400,001
1 | 1 | 2 | Device | Base | Software ID | Monitor the software ID. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 2 | 400,003
1 | 1 | 3 | Device | Base | Software Release Version | Monitor the software release version. For example, if the About screen is showing 04:06:0008, 4 will be returned. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 4 | 400,005
1 | 1 | 4 | Device | Base | Software Prototype Version | Monitor the prototype version if prototype. For example, if the About screen is showing 04:06:0008, 6 will be returned. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 6 | 400,007
1 | 1 | 5 | Device | Base | Software Build Number | Monitor the software build number. For example, if the About screen is showing 04:06:0008, 8 will be returned. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 8 | 400,009
1 | 1 | 6 | Device | Base | Firmware Branch Number | Monitor the firmware branch number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 10 | 400,011
1 | 1 | 7 | Device | Base | Serial Number | Monitor the serial number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 12 | 400,013
1 | 1 | 8 | Device | Base | Date of Manufacture | Monitor the date the hardware was manufactured. Serial number in format YYDDD | 0 to 2,147,483,647 |  | Signed 32-bit | R | 14 | 400,015
1 | 1 | 9 | Device | Base | Part Number | Monitor the model number of the base. | 1 byte (UTF-8) | F (70) | String | R | 16 | 400,017
1 | 1 | 9 | Device | Base | Part Number | Monitor the model number of the base. | 1 byte (UTF-8) | 4 (52) | String | R | 17 | 400,018
1 | 1 | 9 | Device | Base | Part Number | Monitor the model number of the base. | 1 byte (UTF-8) | T (84) | String | R | 18 | 400,019
1 | 1 | 9 | Device | Base | Part Number | Monitor the model number of the base. | 1 byte (UTF-8) | 1 (49) | String | R | 19 | 400,020
1 | 1 | 9 | Device | Base | Part Number | Monitor the model number of the base. | 1 byte (UTF-8) | A (65) | String | R | 20 | 400,021
1 | 1 | 9 | Device | Base | Part Number | Monitor the model number of the base. | 1 byte (UTF-8) | 1 (49) | String | R | 21 | 400,022
1 | 1 | 9 | Device | Base | Part Number | Monitor the model number of the base. | 1 byte (UTF-8) | A (65) | String | R | 22 | 400,023
1 | 1 | 9 | Device | Base | Part Number | Monitor the model number of the base. | 1 byte (UTF-8) | 1 (49) | String | R | 23 | 400,024
1 | 1 | 9 | Device | Base | Part Number | Monitor the model number of the base. | 1 byte (UTF-8) | A (65) | String | R | 24 | 400,025
1 | 1 | 9 | Device | Base | Part Number | Monitor the model number of the base. | 1 byte (UTF-8) | 1 (49) | String | R | 25 | 400,026
1 | 1 | 9 | Device | Base | Part Number | Monitor the model number of the base. | 1 byte (UTF-8) | A (65) | String | R | 26 | 400,027
1 | 1 | 9 | Device | Base | Part Number | Monitor the model number of the base. | 1 byte (UTF-8) | 5 (53) | String | R | 27 | 400,028
1 | 1 | 9 | Device | Base | Part Number | Monitor the model number of the base. | 1 byte (UTF-8) | 0 (48) | String | R | 28 | 400,029
1 | 1 | 9 | Device | Base | Part Number | Monitor the model number of the base. | 1 byte (UTF-8) | 0 (48) | String | R | 29 | 400,030
1 | 1 | 9 | Device | Base | Part Number | Monitor the model number of the base. | 1 byte (UTF-8) | 0 (48) | String | R | 30 | 400,031
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) | F (70) | String | R/W | 46 | 400,047
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) | 4 (52) | String | R/W | 47 | 400,048
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) | T (84) | String | R/W | 48 | 400,049
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 49 | 400,050
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 50 | 400,051
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 51 | 400,052
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 52 | 400,053
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 53 | 400,054
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 54 | 400,055
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 55 | 400,056
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 56 | 400,057
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 57 | 400,058
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 58 | 400,059
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 59 | 400,060
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 60 | 400,061
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 61 | 400,062
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 62 | 400,063
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 63 | 400,064
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 64 | 400,065
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 65 | 400,066
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 66 | 400,067
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 67 | 400,068
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 68 | 400,069
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 69 | 400,070
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 70 | 400,071
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 71 | 400,072
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 72 | 400,073
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 73 | 400,074
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 74 | 400,075
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 75 | 400,076
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 76 | 400,077
1 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 1 byte (UTF-8) |  | String | R/W | 77 | 400,078
1 | 1 | 13 | Device | Base | Restore Settings From | Set to restore factory settings. | None (61), Factory (31) | None (61) | Enumeration | R/W | 86 | 400,087
1 | 1 | 16 | Device | Base | Device Status | Monitor the base for failure. | OK (138), Fail (32) |  | Enumeration | R | 90 | 400,091
1 | 1 | 34 | Device | Base | AC Line Frequency | Set the frequency used for variable time base control. | 50 Hz (3), 60 Hz (4) | 60 Hz (4) | Enumeration | R/W | 94 | 400,095
1 | 2 | 1 | Device | 1 | Hardware ID | Monitor the hardware card ID populated in slot 1. | 0 to 65,535 |  | Signed 32-bit | R | 120 | 400,121
1 | 2 | 2 | Device | 1 | Software ID | Monitor the hardware ID. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 122 | 400,123
1 | 2 | 3 | Device | 1 | Software Release Version | Monitor the software release version. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 124 | 400,125
1 | 2 | 4 | Device | 1 | Software Prototype Version | Monitor the prototype version if prototype. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 126 | 400,127
1 | 2 | 5 | Device | 1 | Software Build Number | Monitor the software build number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 128 | 400,129
1 | 2 | 6 | Device | 1 | Firmware Branch Number | Monitor the firmware branch number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 130 | 400,131
1 | 2 | 7 | Device | 1 | Serial Number | Monitor the serial number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 132 | 400,133
1 | 2 | 8 | Device | 1 | Date of Manufacture | Monitor the date the hardware was manufactured. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 134 | 400,135
1 | 2 | 9 | Device | 1 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 136 | 400,137
1 | 2 | 9 | Device | 1 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 137 | 400,138
1 | 2 | 9 | Device | 1 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 138 | 400,139
1 | 2 | 9 | Device | 1 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 139 | 400,140
1 | 2 | 9 | Device | 1 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 140 | 400,141
1 | 2 | 9 | Device | 1 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 141 | 400,142
1 | 2 | 9 | Device | 1 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 142 | 400,143
1 | 2 | 9 | Device | 1 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 143 | 400,144
1 | 2 | 9 | Device | 1 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 144 | 400,145
1 | 2 | 9 | Device | 1 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 145 | 400,146
1 | 2 | 9 | Device | 1 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 146 | 400,147
1 | 2 | 9 | Device | 1 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 147 | 400,148
1 | 2 | 9 | Device | 1 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 148 | 400,149
1 | 2 | 9 | Device | 1 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 149 | 400,150
1 | 2 | 9 | Device | 1 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 150 | 400,151
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 166 | 400,167
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 167 | 400,168
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 168 | 400,169
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 169 | 400,170
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 170 | 400,171
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 171 | 400,172
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 172 | 400,173
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 173 | 400,174
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 174 | 400,175
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 175 | 400,176
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 176 | 400,177
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 177 | 400,178
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 178 | 400,179
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 179 | 400,180
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 180 | 400,181
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 181 | 400,182
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 182 | 400,183
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 183 | 400,184
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 184 | 400,185
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 185 | 400,186
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 186 | 400,187
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 187 | 400,188
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 188 | 400,189
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 189 | 400,190
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 190 | 400,191
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 191 | 400,192
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 192 | 400,193
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 193 | 400,194
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 194 | 400,195
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 195 | 400,196
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 196 | 400,197
1 | 2 | 11 | Device | 1 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 197 | 400,198
1 | 2 | 13 | Device | 1 | Restore Settings From | Set to restore factory settings. | None (61), Factory (31) | None (61) | Enumeration | R/W | 206 | 400,207
1 | 2 | 16 | Device | 1 | Device Status | Monitor the base for failure. | OK (138), Fail (32) |  | Enumeration | R | 210 | 400,211
1 | 2 | 34 | Device | 1 | AC Line Frequency | Set the frequency used for variable time base control. | 50 Hz (3), 60 Hz (4) | 60 Hz (4) | Enumeration | R/W | 214 | 400,215
1 | 3 | 1 | Device | 2 | Hardware ID | Monitor the hardware card ID populated in slot 2. | 0 to 65,535 |  | Signed 32-bit | R | 240 | 400,241
1 | 3 | 2 | Device | 2 | Software ID | Monitor the hardware ID. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 242 | 400,243
1 | 3 | 3 | Device | 2 | Software Release Version | Monitor the software release version. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 244 | 400,245
1 | 3 | 4 | Device | 2 | Software Prototype Version | Monitor the prototype version if prototype. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 246 | 400,247
1 | 3 | 5 | Device | 2 | Software Build Number | Monitor the software build number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 248 | 400,249
1 | 3 | 6 | Device | 2 | Firmware Branch Number | Monitor the firmware branch number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 250 | 400,251
1 | 3 | 7 | Device | 2 | Serial Number | Monitor the serial number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 252 | 400,253
1 | 3 | 8 | Device | 2 | Date of Manufacture | Monitor the date the hardware was manufactured. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 254 | 400,255
1 | 3 | 9 | Device | 2 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 256 | 400,257
1 | 3 | 9 | Device | 2 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 257 | 400,258
1 | 3 | 9 | Device | 2 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 258 | 400,259
1 | 3 | 9 | Device | 2 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 259 | 400,260
1 | 3 | 9 | Device | 2 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 260 | 400,261
1 | 3 | 9 | Device | 2 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 261 | 400,262
1 | 3 | 9 | Device | 2 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 262 | 400,263
1 | 3 | 9 | Device | 2 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 263 | 400,264
1 | 3 | 9 | Device | 2 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 264 | 400,265
1 | 3 | 9 | Device | 2 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 265 | 400,266
1 | 3 | 9 | Device | 2 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 266 | 400,267
1 | 3 | 9 | Device | 2 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 267 | 400,268
1 | 3 | 9 | Device | 2 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 268 | 400,269
1 | 3 | 9 | Device | 2 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 269 | 400,270
1 | 3 | 9 | Device | 2 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 270 | 400,271
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 286 | 400,287
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 287 | 400,288
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 288 | 400,289
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 289 | 400,290
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 290 | 400,291
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 291 | 400,292
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 292 | 400,293
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 293 | 400,294
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 294 | 400,295
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 295 | 400,296
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 296 | 400,297
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 297 | 400,298
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 298 | 400,299
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 299 | 400,300
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 300 | 400,301
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 301 | 400,302
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 302 | 400,303
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 303 | 400,304
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 304 | 400,305
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 305 | 400,306
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 306 | 400,307
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 307 | 400,308
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 308 | 400,309
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 309 | 400,310
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 310 | 400,311
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 311 | 400,312
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 312 | 400,313
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 313 | 400,314
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 314 | 400,315
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 315 | 400,316
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 316 | 400,317
1 | 3 | 11 | Device | 2 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 317 | 400,318
1 | 3 | 13 | Device | 2 | Restore Settings From | Set to restore factory settings. | None (61), Factory (31) | None (61) | Enumeration | R/W | 326 | 400,327
1 | 3 | 16 | Device | 2 | Device Status | Monitor the base for failure. | OK (138), Fail (32) |  | Enumeration | R | 330 | 400,331
1 | 3 | 34 | Device | 2 | AC Line Frequency | Set the frequency used for variable time base control. | 50 Hz (3), 60 Hz (4) | 60 Hz (4) | Enumeration | R/W | 334 | 400,335
1 | 4 | 1 | Device | 3 | Hardware ID | Monitor the hardware card ID populated in slot 3. | 0 to 65,535 |  | Signed 32-bit | R | 360 | 400,361
1 | 4 | 2 | Device | 3 | Software ID | Monitor the hardware ID. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 362 | 400,363
1 | 4 | 3 | Device | 3 | Software Release Version | Monitor the software release version. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 364 | 400,365
1 | 4 | 4 | Device | 3 | Software Prototype Version | Monitor the prototype version if prototype. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 366 | 400,367
1 | 4 | 5 | Device | 3 | Software Build Number | Monitor the software build number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 368 | 400,369
1 | 4 | 6 | Device | 3 | Firmware Branch Number | Monitor the firmware branch number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 370 | 400,371
1 | 4 | 7 | Device | 3 | Serial Number | Monitor the serial number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 372 | 400,373
1 | 4 | 8 | Device | 3 | Date of Manufacture | Monitor the date the hardware was manufactured. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 374 | 400,375
1 | 4 | 9 | Device | 3 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 376 | 400,377
1 | 4 | 9 | Device | 3 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 377 | 400,378
1 | 4 | 9 | Device | 3 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 378 | 400,379
1 | 4 | 9 | Device | 3 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 379 | 400,380
1 | 4 | 9 | Device | 3 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 380 | 400,381
1 | 4 | 9 | Device | 3 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 381 | 400,382
1 | 4 | 9 | Device | 3 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 382 | 400,383
1 | 4 | 9 | Device | 3 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 383 | 400,384
1 | 4 | 9 | Device | 3 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 384 | 400,385
1 | 4 | 9 | Device | 3 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 385 | 400,386
1 | 4 | 9 | Device | 3 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 386 | 400,387
1 | 4 | 9 | Device | 3 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 387 | 400,388
1 | 4 | 9 | Device | 3 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 388 | 400,389
1 | 4 | 9 | Device | 3 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 389 | 400,390
1 | 4 | 9 | Device | 3 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 390 | 400,391
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 406 | 400,407
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 407 | 400,408
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 408 | 400,409
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 409 | 400,410
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 410 | 400,411
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 411 | 400,412
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 412 | 400,413
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 413 | 400,414
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 414 | 400,415
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 415 | 400,416
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 416 | 400,417
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 417 | 400,418
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 418 | 400,419
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 419 | 400,420
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 420 | 400,421
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 421 | 400,422
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 422 | 400,423
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 423 | 400,424
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 424 | 400,425
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 425 | 400,426
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 426 | 400,427
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 427 | 400,428
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 428 | 400,429
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 429 | 400,430
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 430 | 400,431
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 431 | 400,432
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 432 | 400,433
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 433 | 400,434
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 434 | 400,435
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 435 | 400,436
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 436 | 400,437
1 | 4 | 11 | Device | 3 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 437 | 400,438
1 | 4 | 13 | Device | 3 | Restore Settings From | Set to restore factory settings. | None (61), Factory (31) | None (61) | Enumeration | R/W | 446 | 400,447
1 | 4 | 16 | Device | 3 | Device Status | Monitor the base for failure. | OK (138), Fail (32) |  | Enumeration | R | 450 | 400,451
1 | 4 | 34 | Device | 3 | AC Line Frequency | Set the frequency used for variable time base control. | 50 Hz (3), 60 Hz (4) | 60 Hz (4) | Enumeration | R/W | 454 | 400,455
1 | 5 | 1 | Device | 4 | Hardware ID | Monitor the hardware card ID populated in slot 4. | 0 to 65,535 |  | Signed 32-bit | R | 480 | 400,481
1 | 5 | 2 | Device | 4 | Software ID | Monitor the hardware ID. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 482 | 400,483
1 | 5 | 3 | Device | 4 | Software Release Version | Monitor the software release version. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 484 | 400,485
1 | 5 | 4 | Device | 4 | Software Prototype Version | Monitor the prototype version if prototype. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 486 | 400,487
1 | 5 | 5 | Device | 4 | Software Build Number | Monitor the software build number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 488 | 400,489
1 | 5 | 6 | Device | 4 | Firmware Branch Number | Monitor the firmware branch number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 490 | 400,491
1 | 5 | 7 | Device | 4 | Serial Number | Monitor the serial number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 492 | 400,493
1 | 5 | 8 | Device | 4 | Date of Manufacture | Monitor the date the hardware was manufactured. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 494 | 400,495
1 | 5 | 9 | Device | 4 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 496 | 400,497
1 | 5 | 9 | Device | 4 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 497 | 400,498
1 | 5 | 9 | Device | 4 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 498 | 400,499
1 | 5 | 9 | Device | 4 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 499 | 400,500
1 | 5 | 9 | Device | 4 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 500 | 400,501
1 | 5 | 9 | Device | 4 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 501 | 400,502
1 | 5 | 9 | Device | 4 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 502 | 400,503
1 | 5 | 9 | Device | 4 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 503 | 400,504
1 | 5 | 9 | Device | 4 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 504 | 400,505
1 | 5 | 9 | Device | 4 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 505 | 400,506
1 | 5 | 9 | Device | 4 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 506 | 400,507
1 | 5 | 9 | Device | 4 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 507 | 400,508
1 | 5 | 9 | Device | 4 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 508 | 400,509
1 | 5 | 9 | Device | 4 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 509 | 400,510
1 | 5 | 9 | Device | 4 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 510 | 400,511
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 526 | 400,527
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 527 | 400,528
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 528 | 400,529
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 529 | 400,530
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 530 | 400,531
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 531 | 400,532
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 532 | 400,533
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 533 | 400,534
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 534 | 400,535
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 535 | 400,536
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 536 | 400,537
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 537 | 400,538
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 538 | 400,539
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 539 | 400,540
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 540 | 400,541
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 541 | 400,542
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 542 | 400,543
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 543 | 400,544
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 544 | 400,545
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 545 | 400,546
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 546 | 400,547
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 547 | 400,548
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 548 | 400,549
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 549 | 400,550
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 550 | 400,551
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 551 | 400,552
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 552 | 400,553
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 553 | 400,554
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 554 | 400,555
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 555 | 400,556
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 556 | 400,557
1 | 5 | 11 | Device | 4 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 557 | 400,558
1 | 5 | 13 | Device | 4 | Restore Settings From | Set to restore factory settings. | None (61), Factory (31) | None (61) | Enumeration | R/W | 566 | 400,567
1 | 5 | 16 | Device | 4 | Device Status | Monitor the base for failure. | OK (138), Fail (32) |  | Enumeration | R | 570 | 400,571
1 | 5 | 34 | Device | 4 | AC Line Frequency | Set the frequency used for variable time base control. | 50 Hz (3), 60 Hz (4) | 60 Hz (4) | Enumeration | R/W | 574 | 400,575
1 | 6 | 1 | Device | 5 | Hardware ID | Monitor the hardware card ID populated in slot 5. | 0 to 65,535 |  | Signed 32-bit | R | 600 | 400,601
1 | 6 | 2 | Device | 5 | Software ID | Monitor the hardware ID. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 602 | 400,603
1 | 6 | 3 | Device | 5 | Software Release Version | Monitor the software release version. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 604 | 400,605
1 | 6 | 4 | Device | 5 | Software Prototype Version | Monitor the prototype version if prototype. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 606 | 400,607
1 | 6 | 5 | Device | 5 | Software Build Number | Monitor the software build number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 608 | 400,609
1 | 6 | 6 | Device | 5 | Firmware Branch Number | Monitor the firmware branch number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 610 | 400,611
1 | 6 | 7 | Device | 5 | Serial Number | Monitor the serial number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 612 | 400,613
1 | 6 | 8 | Device | 5 | Date of Manufacture | Monitor the date the hardware was manufactured. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 614 | 400,615
1 | 6 | 9 | Device | 5 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 616 | 400,617
1 | 6 | 9 | Device | 5 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 617 | 400,618
1 | 6 | 9 | Device | 5 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 618 | 400,619
1 | 6 | 9 | Device | 5 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 619 | 400,620
1 | 6 | 9 | Device | 5 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 620 | 400,621
1 | 6 | 9 | Device | 5 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 621 | 400,622
1 | 6 | 9 | Device | 5 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 622 | 400,623
1 | 6 | 9 | Device | 5 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 623 | 400,624
1 | 6 | 9 | Device | 5 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 624 | 400,625
1 | 6 | 9 | Device | 5 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 625 | 400,626
1 | 6 | 9 | Device | 5 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 626 | 400,627
1 | 6 | 9 | Device | 5 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 627 | 400,628
1 | 6 | 9 | Device | 5 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 628 | 400,629
1 | 6 | 9 | Device | 5 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 629 | 400,630
1 | 6 | 9 | Device | 5 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 630 | 400,631
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 646 | 400,647
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 647 | 400,648
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 648 | 400,649
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 649 | 400,650
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 650 | 400,651
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 651 | 400,652
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 652 | 400,653
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 653 | 400,654
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 654 | 400,655
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 655 | 400,656
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 656 | 400,657
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 657 | 400,658
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 658 | 400,659
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 659 | 400,660
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 660 | 400,661
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 661 | 400,662
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 662 | 400,663
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 663 | 400,664
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 664 | 400,665
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 665 | 400,666
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 666 | 400,667
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 667 | 400,668
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 668 | 400,669
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 669 | 400,670
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 670 | 400,671
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 671 | 400,672
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 672 | 400,673
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 673 | 400,674
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 674 | 400,675
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 675 | 400,676
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 676 | 400,677
1 | 6 | 11 | Device | 5 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 677 | 400,678
1 | 6 | 13 | Device | 5 | Restore Settings From | Set to restore factory settings. | None (61), Factory (31) | None (61) | Enumeration | R/W | 686 | 400,687
1 | 6 | 16 | Device | 5 | Device Status | Monitor the base for failure. | OK (138), Fail (32) |  | Enumeration | R | 690 | 400,691
1 | 6 | 34 | Device | 5 | AC Line Frequency | Set the frequency used for variable time base control. | 50 Hz (3), 60 Hz (4) | 60 Hz (4) | Enumeration | R/W | 694 | 400,695
1 | 7 | 1 | Device | 6 | Hardware ID | Monitor the hardware card ID populated in slot 6. | 0 to 65,535 |  | Signed 32-bit | R | 720 | 400,721
1 | 7 | 2 | Device | 6 | Software ID | Monitor the hardware ID. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 722 | 400,723
1 | 7 | 3 | Device | 6 | Software Release Version | Monitor the software release version. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 724 | 400,725
1 | 7 | 4 | Device | 6 | Software Prototype Version | Monitor the prototype version if prototype. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 726 | 400,727
1 | 7 | 5 | Device | 6 | Software Build Number | Monitor the software build number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 728 | 400,729
1 | 7 | 6 | Device | 6 | Firmware Branch Number | Monitor the firmware branch number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 730 | 400,731
1 | 7 | 7 | Device | 6 | Serial Number | Monitor the serial number. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 732 | 400,733
1 | 7 | 8 | Device | 6 | Date of Manufacture | Monitor the date the hardware was manufactured. | 0 to 2,147,483,647 |  | Signed 32-bit | R | 734 | 400,735
1 | 7 | 9 | Device | 6 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 736 | 400,737
1 | 7 | 9 | Device | 6 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 737 | 400,738
1 | 7 | 9 | Device | 6 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 738 | 400,739
1 | 7 | 9 | Device | 6 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 739 | 400,740
1 | 7 | 9 | Device | 6 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 740 | 400,741
1 | 7 | 9 | Device | 6 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 741 | 400,742
1 | 7 | 9 | Device | 6 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 742 | 400,743
1 | 7 | 9 | Device | 6 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 743 | 400,744
1 | 7 | 9 | Device | 6 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 744 | 400,745
1 | 7 | 9 | Device | 6 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 745 | 400,746
1 | 7 | 9 | Device | 6 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 746 | 400,747
1 | 7 | 9 | Device | 6 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 747 | 400,748
1 | 7 | 9 | Device | 6 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 748 | 400,749
1 | 7 | 9 | Device | 6 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 749 | 400,750
1 | 7 | 9 | Device | 6 | Part Number | Monitor the model number of the card. | 1 byte (UTF-8) |  | String | R | 750 | 400,751
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 766 | 400,767
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 767 | 400,768
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 768 | 400,769
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 769 | 400,770
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 770 | 400,771
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 771 | 400,772
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 772 | 400,773
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 773 | 400,774
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 774 | 400,775
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 775 | 400,776
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 776 | 400,777
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 777 | 400,778
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 778 | 400,779
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 779 | 400,780
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 780 | 400,781
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 781 | 400,782
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 782 | 400,783
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 783 | 400,784
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 784 | 400,785
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 785 | 400,786
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 786 | 400,787
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 787 | 400,788
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 788 | 400,789
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 789 | 400,790
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 790 | 400,791
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 791 | 400,792
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 792 | 400,793
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 793 | 400,794
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 794 | 400,795
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 795 | 400,796
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 796 | 400,797
1 | 7 | 11 | Device | 6 | Device Name | Set the name to assign the card. | 1 byte (UTF-8) |  | String | R/W | 797 | 400,798
1 | 7 | 13 | Device | 6 | Restore Settings From | Set to restore factory settings. | None (61), Factory (31) | None (61) | Enumeration | R/W | 806 | 400,807
1 | 7 | 16 | Device | 6 | Device Status | Monitor the base for failure. | OK (138), Fail (32) |  | Enumeration | R | 810 | 400,811
1 | 7 | 34 | Device | 6 | AC Line Frequency | Set the frequency used for variable time base control. | 50 Hz (3), 60 Hz (4) | 60 Hz (4) | Enumeration | R/W | 814 | 400,815
2 | 1 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 15816 | 415,817
2 | 1 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 15818 | 415,819
2 | 1 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 15820 | 415,821
2 | 1 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 15822 | 415,823
2 | 1 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 15828 | 415,829
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48100 | 448,101
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48101 | 448,102
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48102 | 448,103
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48103 | 448,104
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48104 | 448,105
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48105 | 448,106
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48106 | 448,107
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48107 | 448,108
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48108 | 448,109
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48109 | 448,110
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48110 | 448,111
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48111 | 448,112
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48112 | 448,113
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48113 | 448,114
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48114 | 448,115
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48115 | 448,116
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48116 | 448,117
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48117 | 448,118
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48118 | 448,119
2 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48119 | 448,120
2 | 2 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 15846 | 415,847
2 | 2 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 15848 | 415,849
2 | 2 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 15850 | 415,851
2 | 2 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 15852 | 415,853
2 | 2 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 15858 | 415,859
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48120 | 448,121
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48121 | 448,122
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48122 | 448,123
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48123 | 448,124
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48124 | 448,125
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48125 | 448,126
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48126 | 448,127
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48127 | 448,128
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48128 | 448,129
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48129 | 448,130
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48130 | 448,131
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48131 | 448,132
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48132 | 448,133
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48133 | 448,134
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48134 | 448,135
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48135 | 448,136
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48136 | 448,137
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48137 | 448,138
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48138 | 448,139
2 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48139 | 448,140
2 | 3 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 15876 | 415,877
2 | 3 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 15878 | 415,879
2 | 3 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 15880 | 415,881
2 | 3 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 15882 | 415,883
2 | 3 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 15888 | 415,889
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48140 | 448,141
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48141 | 448,142
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48142 | 448,143
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48143 | 448,144
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48144 | 448,145
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48145 | 448,146
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48146 | 448,147
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48147 | 448,148
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48148 | 448,149
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48149 | 448,150
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48150 | 448,151
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48151 | 448,152
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48152 | 448,153
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48153 | 448,154
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48154 | 448,155
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48155 | 448,156
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48156 | 448,157
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48157 | 448,158
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48158 | 448,159
2 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48159 | 448,160
2 | 4 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 15906 | 415,907
2 | 4 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 15908 | 415,909
2 | 4 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 15910 | 415,911
2 | 4 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 15912 | 415,913
2 | 4 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 15918 | 415,919
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48160 | 448,161
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48161 | 448,162
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48162 | 448,163
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48163 | 448,164
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48164 | 448,165
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48165 | 448,166
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48166 | 448,167
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48167 | 448,168
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48168 | 448,169
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48169 | 448,170
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48170 | 448,171
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48171 | 448,172
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48172 | 448,173
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48173 | 448,174
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48174 | 448,175
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48175 | 448,176
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48176 | 448,177
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48177 | 448,178
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48178 | 448,179
2 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48179 | 448,180
2 | 5 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 15936 | 415,937
2 | 5 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 15938 | 415,939
2 | 5 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 15940 | 415,941
2 | 5 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 15942 | 415,943
2 | 5 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 15948 | 415,949
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48180 | 448,181
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48181 | 448,182
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48182 | 448,183
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48183 | 448,184
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48184 | 448,185
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48185 | 448,186
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48186 | 448,187
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48187 | 448,188
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48188 | 448,189
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48189 | 448,190
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48190 | 448,191
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48191 | 448,192
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48192 | 448,193
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48193 | 448,194
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48194 | 448,195
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48195 | 448,196
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48196 | 448,197
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48197 | 448,198
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48198 | 448,199
2 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48199 | 448,200
2 | 6 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 15966 | 415,967
2 | 6 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 15968 | 415,969
2 | 6 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 15970 | 415,971
2 | 6 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 15972 | 415,973
2 | 6 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 15978 | 415,979
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48200 | 448,201
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48201 | 448,202
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48202 | 448,203
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48203 | 448,204
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48204 | 448,205
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48205 | 448,206
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48206 | 448,207
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48207 | 448,208
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48208 | 448,209
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48209 | 448,210
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48210 | 448,211
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48211 | 448,212
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48212 | 448,213
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48213 | 448,214
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48214 | 448,215
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48215 | 448,216
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48216 | 448,217
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48217 | 448,218
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48218 | 448,219
2 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48219 | 448,220
2 | 7 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 15996 | 415,997
2 | 7 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 15998 | 415,999
2 | 7 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16000 | 416,001
2 | 7 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16002 | 416,003
2 | 7 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16008 | 416,009
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48220 | 448,221
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48221 | 448,222
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48222 | 448,223
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48223 | 448,224
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48224 | 448,225
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48225 | 448,226
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48226 | 448,227
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48227 | 448,228
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48228 | 448,229
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48229 | 448,230
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48230 | 448,231
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48231 | 448,232
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48232 | 448,233
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48233 | 448,234
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48234 | 448,235
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48235 | 448,236
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48236 | 448,237
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48237 | 448,238
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48238 | 448,239
2 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48239 | 448,240
2 | 8 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16026 | 416,027
2 | 8 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16028 | 416,029
2 | 8 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16030 | 416,031
2 | 8 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16032 | 416,033
2 | 8 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16038 | 416,039
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48240 | 448,241
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48241 | 448,242
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48242 | 448,243
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48243 | 448,244
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48244 | 448,245
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48245 | 448,246
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48246 | 448,247
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48247 | 448,248
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48248 | 448,249
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48249 | 448,250
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48250 | 448,251
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48251 | 448,252
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48252 | 448,253
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48253 | 448,254
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48254 | 448,255
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48255 | 448,256
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48256 | 448,257
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48257 | 448,258
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48258 | 448,259
2 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48259 | 448,260
2 | 9 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16056 | 416,057
2 | 9 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16058 | 416,059
2 | 9 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16060 | 416,061
2 | 9 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16062 | 416,063
2 | 9 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16068 | 416,069
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48260 | 448,261
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48261 | 448,262
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48262 | 448,263
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48263 | 448,264
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48264 | 448,265
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48265 | 448,266
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48266 | 448,267
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48267 | 448,268
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48268 | 448,269
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48269 | 448,270
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48270 | 448,271
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48271 | 448,272
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48272 | 448,273
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48273 | 448,274
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48274 | 448,275
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48275 | 448,276
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48276 | 448,277
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48277 | 448,278
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48278 | 448,279
2 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48279 | 448,280
2 | 10 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16086 | 416,087
2 | 10 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16088 | 416,089
2 | 10 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16090 | 416,091
2 | 10 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16092 | 416,093
2 | 10 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16098 | 416,099
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48280 | 448,281
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48281 | 448,282
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48282 | 448,283
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48283 | 448,284
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48284 | 448,285
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48285 | 448,286
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48286 | 448,287
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48287 | 448,288
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48288 | 448,289
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48289 | 448,290
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48290 | 448,291
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48291 | 448,292
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48292 | 448,293
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48293 | 448,294
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48294 | 448,295
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48295 | 448,296
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48296 | 448,297
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48297 | 448,298
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48298 | 448,299
2 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48299 | 448,300
2 | 11 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16116 | 416,117
2 | 11 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16118 | 416,119
2 | 11 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16120 | 416,121
2 | 11 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16122 | 416,123
2 | 11 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16128 | 416,129
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48300 | 448,301
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48301 | 448,302
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48302 | 448,303
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48303 | 448,304
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48304 | 448,305
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48305 | 448,306
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48306 | 448,307
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48307 | 448,308
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48308 | 448,309
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48309 | 448,310
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48310 | 448,311
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48311 | 448,312
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48312 | 448,313
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48313 | 448,314
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48314 | 448,315
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48315 | 448,316
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48316 | 448,317
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48317 | 448,318
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48318 | 448,319
2 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48319 | 448,320
2 | 12 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16146 | 416,147
2 | 12 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16148 | 416,149
2 | 12 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16150 | 416,151
2 | 12 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16152 | 416,153
2 | 12 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16158 | 416,159
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48320 | 448,321
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48321 | 448,322
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48322 | 448,323
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48323 | 448,324
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48324 | 448,325
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48325 | 448,326
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48326 | 448,327
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48327 | 448,328
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48328 | 448,329
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48329 | 448,330
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48330 | 448,331
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48331 | 448,332
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48332 | 448,333
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48333 | 448,334
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48334 | 448,335
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48335 | 448,336
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48336 | 448,337
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48337 | 448,338
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48338 | 448,339
2 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48339 | 448,340
2 | 13 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16176 | 416,177
2 | 13 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16178 | 416,179
2 | 13 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16180 | 416,181
2 | 13 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16182 | 416,183
2 | 13 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16188 | 416,189
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48340 | 448,341
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48341 | 448,342
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48342 | 448,343
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48343 | 448,344
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48344 | 448,345
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48345 | 448,346
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48346 | 448,347
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48347 | 448,348
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48348 | 448,349
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48349 | 448,350
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48350 | 448,351
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48351 | 448,352
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48352 | 448,353
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48353 | 448,354
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48354 | 448,355
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48355 | 448,356
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48356 | 448,357
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48357 | 448,358
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48358 | 448,359
2 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48359 | 448,360
2 | 14 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16206 | 416,207
2 | 14 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16208 | 416,209
2 | 14 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16210 | 416,211
2 | 14 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16212 | 416,213
2 | 14 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16218 | 416,219
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48360 | 448,361
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48361 | 448,362
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48362 | 448,363
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48363 | 448,364
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48364 | 448,365
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48365 | 448,366
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48366 | 448,367
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48367 | 448,368
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48368 | 448,369
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48369 | 448,370
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48370 | 448,371
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48371 | 448,372
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48372 | 448,373
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48373 | 448,374
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48374 | 448,375
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48375 | 448,376
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48376 | 448,377
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48377 | 448,378
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48378 | 448,379
2 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48379 | 448,380
2 | 15 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16236 | 416,237
2 | 15 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16238 | 416,239
2 | 15 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16240 | 416,241
2 | 15 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16242 | 416,243
2 | 15 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16248 | 416,249
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48380 | 448,381
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48381 | 448,382
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48382 | 448,383
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48383 | 448,384
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48384 | 448,385
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48385 | 448,386
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48386 | 448,387
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48387 | 448,388
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48388 | 448,389
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48389 | 448,390
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48390 | 448,391
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48391 | 448,392
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48392 | 448,393
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48393 | 448,394
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48394 | 448,395
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48395 | 448,396
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48396 | 448,397
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48397 | 448,398
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48398 | 448,399
2 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48399 | 448,400
2 | 16 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16266 | 416,267
2 | 16 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16268 | 416,269
2 | 16 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16270 | 416,271
2 | 16 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16272 | 416,273
2 | 16 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16278 | 416,279
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48400 | 448,401
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48401 | 448,402
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48402 | 448,403
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48403 | 448,404
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48404 | 448,405
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48405 | 448,406
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48406 | 448,407
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48407 | 448,408
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48408 | 448,409
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48409 | 448,410
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48410 | 448,411
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48411 | 448,412
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48412 | 448,413
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48413 | 448,414
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48414 | 448,415
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48415 | 448,416
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48416 | 448,417
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48417 | 448,418
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48418 | 448,419
2 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48419 | 448,420
2 | 17 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16296 | 416,297
2 | 17 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16298 | 416,299
2 | 17 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16300 | 416,301
2 | 17 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16302 | 416,303
2 | 17 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16308 | 416,309
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48420 | 448,421
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48421 | 448,422
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48422 | 448,423
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48423 | 448,424
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48424 | 448,425
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48425 | 448,426
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48426 | 448,427
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48427 | 448,428
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48428 | 448,429
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48429 | 448,430
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48430 | 448,431
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48431 | 448,432
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48432 | 448,433
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48433 | 448,434
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48434 | 448,435
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48435 | 448,436
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48436 | 448,437
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48437 | 448,438
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48438 | 448,439
2 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48439 | 448,440
2 | 18 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16326 | 416,327
2 | 18 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16328 | 416,329
2 | 18 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16330 | 416,331
2 | 18 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16332 | 416,333
2 | 18 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16338 | 416,339
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48440 | 448,441
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48441 | 448,442
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48442 | 448,443
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48443 | 448,444
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48444 | 448,445
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48445 | 448,446
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48446 | 448,447
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48447 | 448,448
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48448 | 448,449
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48449 | 448,450
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48450 | 448,451
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48451 | 448,452
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48452 | 448,453
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48453 | 448,454
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48454 | 448,455
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48455 | 448,456
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48456 | 448,457
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48457 | 448,458
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48458 | 448,459
2 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48459 | 448,460
2 | 19 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16356 | 416,357
2 | 19 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16358 | 416,359
2 | 19 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16360 | 416,361
2 | 19 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16362 | 416,363
2 | 19 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16368 | 416,369
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48460 | 448,461
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48461 | 448,462
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48462 | 448,463
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48463 | 448,464
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48464 | 448,465
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48465 | 448,466
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48466 | 448,467
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48467 | 448,468
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48468 | 448,469
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48469 | 448,470
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48470 | 448,471
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48471 | 448,472
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48472 | 448,473
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48473 | 448,474
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48474 | 448,475
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48475 | 448,476
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48476 | 448,477
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48477 | 448,478
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48478 | 448,479
2 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48479 | 448,480
2 | 20 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16386 | 416,387
2 | 20 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16388 | 416,389
2 | 20 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16390 | 416,391
2 | 20 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16392 | 416,393
2 | 20 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16398 | 416,399
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48480 | 448,481
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48481 | 448,482
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48482 | 448,483
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48483 | 448,484
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48484 | 448,485
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48485 | 448,486
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48486 | 448,487
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48487 | 448,488
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48488 | 448,489
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48489 | 448,490
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48490 | 448,491
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48491 | 448,492
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48492 | 448,493
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48493 | 448,494
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48494 | 448,495
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48495 | 448,496
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48496 | 448,497
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48497 | 448,498
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48498 | 448,499
2 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48499 | 448,500
2 | 21 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16416 | 416,417
2 | 21 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16418 | 416,419
2 | 21 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16420 | 416,421
2 | 21 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16422 | 416,423
2 | 21 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16428 | 416,429
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48500 | 448,501
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48501 | 448,502
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48502 | 448,503
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48503 | 448,504
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48504 | 448,505
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48505 | 448,506
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48506 | 448,507
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48507 | 448,508
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48508 | 448,509
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48509 | 448,510
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48510 | 448,511
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48511 | 448,512
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48512 | 448,513
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48513 | 448,514
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48514 | 448,515
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48515 | 448,516
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48516 | 448,517
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48517 | 448,518
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48518 | 448,519
2 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48519 | 448,520
2 | 22 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16446 | 416,447
2 | 22 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16448 | 416,449
2 | 22 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16450 | 416,451
2 | 22 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16452 | 416,453
2 | 22 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16458 | 416,459
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48520 | 448,521
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48521 | 448,522
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48522 | 448,523
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48523 | 448,524
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48524 | 448,525
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48525 | 448,526
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48526 | 448,527
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48527 | 448,528
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48528 | 448,529
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48529 | 448,530
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48530 | 448,531
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48531 | 448,532
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48532 | 448,533
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48533 | 448,534
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48534 | 448,535
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48535 | 448,536
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48536 | 448,537
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48537 | 448,538
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48538 | 448,539
2 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48539 | 448,540
2 | 23 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16476 | 416,477
2 | 23 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16478 | 416,479
2 | 23 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16480 | 416,481
2 | 23 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16482 | 416,483
2 | 23 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16488 | 416,489
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48540 | 448,541
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48541 | 448,542
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48542 | 448,543
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48543 | 448,544
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48544 | 448,545
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48545 | 448,546
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48546 | 448,547
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48547 | 448,548
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48548 | 448,549
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48549 | 448,550
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48550 | 448,551
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48551 | 448,552
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48552 | 448,553
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48553 | 448,554
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48554 | 448,555
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48555 | 448,556
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48556 | 448,557
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48557 | 448,558
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48558 | 448,559
2 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48559 | 448,560
2 | 24 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | Enumeration | R/W | 16506 | 416,507
2 | 24 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | Enumeration | R/W | 16508 | 416,509
2 | 24 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 16510 | 416,511
2 | 24 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | IEEE Float | R | 16512 | 416,513
2 | 24 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | Enumeration | R/W | 16518 | 416,519
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48560 | 448,561
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48561 | 448,562
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48562 | 448,563
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48563 | 448,564
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48564 | 448,565
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48565 | 448,566
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48566 | 448,567
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48567 | 448,568
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48568 | 448,569
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48569 | 448,570
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48570 | 448,571
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48571 | 448,572
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48572 | 448,573
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48573 | 448,574
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48574 | 448,575
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48575 | 448,576
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48576 | 448,577
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48577 | 448,578
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48578 | 448,579
2 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48579 | 448,580
3 | 1 | 5 | Display | Base | Display Units | Set display units for touchscreen. | F (30), C (15) | F (30) | Enumeration | R/W | 1328 | 401,329
12 | 1 | 2 | Limit | 1 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | IEEE Float | R/W | 11242 | 411,243
12 | 1 | 3 | Limit | 1 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 11244 | 411,245
12 | 1 | 4 | Limit | 1 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 11246 | 411,247
12 | 1 | 5 | Limit | 1 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 11248 | 411,249
12 | 1 | 6 | Limit | 1 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | Enumeration | R | 11250 | 411,251
12 | 1 | 7 | Limit | 1 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | Enumeration | R | 11252 | 411,253
12 | 1 | 9 | Limit | 1 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 11256 | 411,257
12 | 1 | 10 | Limit | 1 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 11258 | 411,259
12 | 1 | 13 | Limit | 1 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | Enumeration | R | 11264 | 411,265
12 | 1 | 14 | Limit | 1 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 11266 | 411,267
12 | 1 | 15 | Limit | 1 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | Enumeration | R/W | 11268 | 411,269
12 | 1 | 16 | Limit | 1 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 11270 | 411,271
12 | 1 | 17 | Limit | 1 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 11272 | 411,273
12 | 1 | 18 | Limit | 1 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | Enumeration | R | 11274 | 411,275
12 | 1 | 19 | Limit | 1 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | Enumeration | R/W | 11276 | 411,277
12 | 1 | 20 | Limit | 1 | Source Instance B | Set the source Instance for the Limit sensor. | 1 to 1 | 1 | Unsigned 8-bit | R/W | 11278 | 411,279
12 | 1 | 21 | Limit | 1 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 11280 | 411,281
12 | 1 | 22 | Limit | 1 | Source Value B | Monitor the IN receiver source value. |  |  | IEEE Float | R | 11282 | 411,283
12 | 1 | 25 | Limit | 1 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 11288 | 411,289
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48580 | 448,581
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48581 | 448,582
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48582 | 448,583
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48583 | 448,584
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48584 | 448,585
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48585 | 448,586
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48586 | 448,587
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48587 | 448,588
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48588 | 448,589
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48589 | 448,590
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48590 | 448,591
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48591 | 448,592
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48592 | 448,593
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48593 | 448,594
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48594 | 448,595
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48595 | 448,596
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48596 | 448,597
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48597 | 448,598
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48598 | 448,599
12 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48599 | 448,600
12 | 11 | 2 | Limit | 2 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | IEEE Float | R/W | 11302 | 411,303
12 | 11 | 3 | Limit | 2 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 11304 | 411,305
12 | 11 | 4 | Limit | 2 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 11306 | 411,307
12 | 11 | 5 | Limit | 2 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 11308 | 411,309
12 | 11 | 6 | Limit | 2 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | Enumeration | R | 11310 | 411,311
12 | 11 | 7 | Limit | 2 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | Enumeration | R | 11312 | 411,313
12 | 11 | 9 | Limit | 2 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 11316 | 411,317
12 | 11 | 10 | Limit | 2 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 11318 | 411,319
12 | 11 | 13 | Limit | 2 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | Enumeration | R | 11324 | 411,325
12 | 11 | 14 | Limit | 2 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 11326 | 411,327
12 | 11 | 15 | Limit | 2 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | Enumeration | R/W | 11328 | 411,329
12 | 11 | 16 | Limit | 2 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 11330 | 411,331
12 | 11 | 17 | Limit | 2 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 11332 | 411,333
12 | 11 | 18 | Limit | 2 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | Enumeration | R | 11334 | 411,335
12 | 11 | 19 | Limit | 2 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | Enumeration | R/W | 11336 | 411,337
12 | 11 | 20 | Limit | 2 | Source Instance B | Set the source Instance for the Limit sensor. | 11 to 11 | 11 | Unsigned 8-bit | R/W | 11338 | 411,339
12 | 11 | 21 | Limit | 2 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 11340 | 411,341
12 | 11 | 22 | Limit | 2 | Source Value B | Monitor the IN receiver source value. |  |  | IEEE Float | R | 11342 | 411,343
12 | 11 | 25 | Limit | 2 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 11348 | 411,349
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48600 | 448,601
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48601 | 448,602
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48602 | 448,603
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48603 | 448,604
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48604 | 448,605
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48605 | 448,606
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48606 | 448,607
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48607 | 448,608
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48608 | 448,609
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48609 | 448,610
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48610 | 448,611
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48611 | 448,612
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48612 | 448,613
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48613 | 448,614
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48614 | 448,615
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48615 | 448,616
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48616 | 448,617
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48617 | 448,618
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48618 | 448,619
12 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48619 | 448,620
12 | 21 | 2 | Limit | 3 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | IEEE Float | R/W | 11362 | 411,363
12 | 21 | 3 | Limit | 3 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 11364 | 411,365
12 | 21 | 4 | Limit | 3 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 11366 | 411,367
12 | 21 | 5 | Limit | 3 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 11368 | 411,369
12 | 21 | 6 | Limit | 3 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | Enumeration | R | 11370 | 411,371
12 | 21 | 7 | Limit | 3 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | Enumeration | R | 11372 | 411,373
12 | 21 | 9 | Limit | 3 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 11376 | 411,377
12 | 21 | 10 | Limit | 3 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 11378 | 411,379
12 | 21 | 13 | Limit | 3 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | Enumeration | R | 11384 | 411,385
12 | 21 | 14 | Limit | 3 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 11386 | 411,387
12 | 21 | 15 | Limit | 3 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | Enumeration | R/W | 11388 | 411,389
12 | 21 | 16 | Limit | 3 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 11390 | 411,391
12 | 21 | 17 | Limit | 3 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 11392 | 411,393
12 | 21 | 18 | Limit | 3 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | Enumeration | R | 11394 | 411,395
12 | 21 | 19 | Limit | 3 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | Enumeration | R/W | 11396 | 411,397
12 | 21 | 20 | Limit | 3 | Source Instance B | Set the source Instance for the Limit sensor. | 21 to 21 | 21 | Unsigned 8-bit | R/W | 11398 | 411,399
12 | 21 | 21 | Limit | 3 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 11400 | 411,401
12 | 21 | 22 | Limit | 3 | Source Value B | Monitor the IN receiver source value. |  |  | IEEE Float | R | 11402 | 411,403
12 | 21 | 25 | Limit | 3 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 11408 | 411,409
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48620 | 448,621
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48621 | 448,622
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48622 | 448,623
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48623 | 448,624
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48624 | 448,625
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48625 | 448,626
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48626 | 448,627
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48627 | 448,628
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48628 | 448,629
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48629 | 448,630
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48630 | 448,631
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48631 | 448,632
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48632 | 448,633
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48633 | 448,634
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48634 | 448,635
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48635 | 448,636
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48636 | 448,637
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48637 | 448,638
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48638 | 448,639
12 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48639 | 448,640
12 | 31 | 2 | Limit | 4 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | IEEE Float | R/W | 11422 | 411,423
12 | 31 | 3 | Limit | 4 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 11424 | 411,425
12 | 31 | 4 | Limit | 4 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 11426 | 411,427
12 | 31 | 5 | Limit | 4 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 11428 | 411,429
12 | 31 | 6 | Limit | 4 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | Enumeration | R | 11430 | 411,431
12 | 31 | 7 | Limit | 4 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | Enumeration | R | 11432 | 411,433
12 | 31 | 9 | Limit | 4 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 11436 | 411,437
12 | 31 | 10 | Limit | 4 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 11438 | 411,439
12 | 31 | 13 | Limit | 4 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | Enumeration | R | 11444 | 411,445
12 | 31 | 14 | Limit | 4 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 11446 | 411,447
12 | 31 | 15 | Limit | 4 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | Enumeration | R/W | 11448 | 411,449
12 | 31 | 16 | Limit | 4 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 11450 | 411,451
12 | 31 | 17 | Limit | 4 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 11452 | 411,453
12 | 31 | 18 | Limit | 4 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | Enumeration | R | 11454 | 411,455
12 | 31 | 19 | Limit | 4 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | Enumeration | R/W | 11456 | 411,457
12 | 31 | 20 | Limit | 4 | Source Instance B | Set the source Instance for the Limit sensor. | 31 to 31 | 31 | Unsigned 8-bit | R/W | 11458 | 411,459
12 | 31 | 21 | Limit | 4 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 11460 | 411,461
12 | 31 | 22 | Limit | 4 | Source Value B | Monitor the IN receiver source value. |  |  | IEEE Float | R | 11462 | 411,463
12 | 31 | 25 | Limit | 4 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 11468 | 411,469
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48640 | 448,641
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48641 | 448,642
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48642 | 448,643
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48643 | 448,644
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48644 | 448,645
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48645 | 448,646
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48646 | 448,647
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48647 | 448,648
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48648 | 448,649
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48649 | 448,650
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48650 | 448,651
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48651 | 448,652
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48652 | 448,653
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48653 | 448,654
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48654 | 448,655
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48655 | 448,656
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48656 | 448,657
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48657 | 448,658
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48658 | 448,659
12 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48659 | 448,660
12 | 41 | 2 | Limit | 5 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | IEEE Float | R/W | 11482 | 411,483
12 | 41 | 3 | Limit | 5 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 11484 | 411,485
12 | 41 | 4 | Limit | 5 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 11486 | 411,487
12 | 41 | 5 | Limit | 5 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 11488 | 411,489
12 | 41 | 6 | Limit | 5 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | Enumeration | R | 11490 | 411,491
12 | 41 | 7 | Limit | 5 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | Enumeration | R | 11492 | 411,493
12 | 41 | 9 | Limit | 5 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 11496 | 411,497
12 | 41 | 10 | Limit | 5 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 11498 | 411,499
12 | 41 | 13 | Limit | 5 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | Enumeration | R | 11504 | 411,505
12 | 41 | 14 | Limit | 5 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 11506 | 411,507
12 | 41 | 15 | Limit | 5 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | Enumeration | R/W | 11508 | 411,509
12 | 41 | 16 | Limit | 5 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 11510 | 411,511
12 | 41 | 17 | Limit | 5 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 11512 | 411,513
12 | 41 | 18 | Limit | 5 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | Enumeration | R | 11514 | 411,515
12 | 41 | 19 | Limit | 5 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | Enumeration | R/W | 11516 | 411,517
12 | 41 | 20 | Limit | 5 | Source Instance B | Set the source Instance for the Limit sensor. | 41 to 41 | 41 | Unsigned 8-bit | R/W | 11518 | 411,519
12 | 41 | 21 | Limit | 5 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 11520 | 411,521
12 | 41 | 22 | Limit | 5 | Source Value B | Monitor the IN receiver source value. |  |  | IEEE Float | R | 11522 | 411,523
12 | 41 | 25 | Limit | 5 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 11528 | 411,529
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48660 | 448,661
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48661 | 448,662
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48662 | 448,663
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48663 | 448,664
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48664 | 448,665
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48665 | 448,666
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48666 | 448,667
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48667 | 448,668
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48668 | 448,669
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48669 | 448,670
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48670 | 448,671
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48671 | 448,672
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48672 | 448,673
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48673 | 448,674
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48674 | 448,675
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48675 | 448,676
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48676 | 448,677
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48677 | 448,678
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48678 | 448,679
12 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48679 | 448,680
12 | 51 | 2 | Limit | 6 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | IEEE Float | R/W | 11542 | 411,543
12 | 51 | 3 | Limit | 6 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 11544 | 411,545
12 | 51 | 4 | Limit | 6 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | IEEE Float | R/W | 11546 | 411,547
12 | 51 | 5 | Limit | 6 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 11548 | 411,549
12 | 51 | 6 | Limit | 6 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | Enumeration | R | 11550 | 411,551
12 | 51 | 7 | Limit | 6 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | Enumeration | R | 11552 | 411,553
12 | 51 | 9 | Limit | 6 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 11556 | 411,557
12 | 51 | 10 | Limit | 6 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 11558 | 411,559
12 | 51 | 13 | Limit | 6 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | Enumeration | R | 11564 | 411,565
12 | 51 | 14 | Limit | 6 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 11566 | 411,567
12 | 51 | 15 | Limit | 6 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | Enumeration | R/W | 11568 | 411,569
12 | 51 | 16 | Limit | 6 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 11570 | 411,571
12 | 51 | 17 | Limit | 6 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 11572 | 411,573
12 | 51 | 18 | Limit | 6 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | Enumeration | R | 11574 | 411,575
12 | 51 | 19 | Limit | 6 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | Enumeration | R/W | 11576 | 411,577
12 | 51 | 20 | Limit | 6 | Source Instance B | Set the source Instance for the Limit sensor. | 51 to 51 | 51 | Unsigned 8-bit | R/W | 11578 | 411,579
12 | 51 | 21 | Limit | 6 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 11580 | 411,581
12 | 51 | 22 | Limit | 6 | Source Value B | Monitor the IN receiver source value. |  |  | IEEE Float | R | 11582 | 411,583
12 | 51 | 25 | Limit | 6 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 11588 | 411,589
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48680 | 448,681
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48681 | 448,682
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48682 | 448,683
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48683 | 448,684
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48684 | 448,685
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48685 | 448,686
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48686 | 448,687
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48687 | 448,688
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48688 | 448,689
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48689 | 448,690
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48690 | 448,691
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48691 | 448,692
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48692 | 448,693
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48693 | 448,694
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48694 | 448,695
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48695 | 448,696
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48696 | 448,697
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48697 | 448,698
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48698 | 448,699
12 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48699 | 448,700
15 | 1 | 1 | Current | 1 | Current Read | Monitor current of S&H transmitter. |  |  | IEEE Float | R | 6250 | 406,251
15 | 1 | 2 | Current | 1 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | Enumeration | R | 6252 | 406,253
15 | 1 | 3 | Current | 1 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | Enumeration | R | 6254 | 406,255
15 | 1 | 4 | Current | 1 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | Enumeration | R/W | 6256 | 406,257
15 | 1 | 5 | Current | 1 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | Enumeration | R/W | 6258 | 406,259
15 | 1 | 7 | Current | 1 | Load Current RMS | Monitor current of CUR transmitter. |  |  | IEEE Float | R | 6262 | 406,263
15 | 1 | 8 | Current | 1 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | IEEE Float | R/W | 6264 | 406,265
15 | 1 | 9 | Current | 1 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 6266 | 406,267
15 | 1 | 10 | Current | 1 | Current Gain | Monitor the Gain setting. |  | 0.17 | IEEE Float | R | 6268 | 406,269
15 | 1 | 11 | Current | 1 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 6270 | 406,271
15 | 1 | 12 | Current | 1 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | Unsigned 16-bit | R/W | 6272 | 406,273
15 | 1 | 19 | Current | 1 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6286 | 406,287
15 | 1 | 20 | Current | 1 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | IEEE Float | R | 6288 | 406,289
15 | 1 | 21 | Current | 1 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | Enumeration | R | 6290 | 406,291
15 | 1 | 22 | Current | 1 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | IEEE Float | R/W | 6292 | 406,293
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48700 | 448,701
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48701 | 448,702
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48702 | 448,703
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48703 | 448,704
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48704 | 448,705
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48705 | 448,706
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48706 | 448,707
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48707 | 448,708
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48708 | 448,709
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48709 | 448,710
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48710 | 448,711
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48711 | 448,712
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48712 | 448,713
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48713 | 448,714
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48714 | 448,715
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48715 | 448,716
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48716 | 448,717
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48717 | 448,718
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48718 | 448,719
15 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48719 | 448,720
15 | 11 | 1 | Current | 2 | Current Read | Monitor current of S&H transmitter. |  |  | IEEE Float | R | 6330 | 406,331
15 | 11 | 2 | Current | 2 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | Enumeration | R | 6332 | 406,333
15 | 11 | 3 | Current | 2 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | Enumeration | R | 6334 | 406,335
15 | 11 | 4 | Current | 2 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | Enumeration | R/W | 6336 | 406,337
15 | 11 | 5 | Current | 2 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | Enumeration | R/W | 6338 | 406,339
15 | 11 | 7 | Current | 2 | Load Current RMS | Monitor current of CUR transmitter. |  |  | IEEE Float | R | 6342 | 406,343
15 | 11 | 8 | Current | 2 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | IEEE Float | R/W | 6344 | 406,345
15 | 11 | 9 | Current | 2 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 6346 | 406,347
15 | 11 | 10 | Current | 2 | Current Gain | Monitor the Gain setting. |  | 0.17 | IEEE Float | R | 6348 | 406,349
15 | 11 | 11 | Current | 2 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 6350 | 406,351
15 | 11 | 12 | Current | 2 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | Unsigned 16-bit | R/W | 6352 | 406,353
15 | 11 | 19 | Current | 2 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6366 | 406,367
15 | 11 | 20 | Current | 2 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | IEEE Float | R | 6368 | 406,369
15 | 11 | 21 | Current | 2 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | Enumeration | R | 6370 | 406,371
15 | 11 | 22 | Current | 2 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | IEEE Float | R/W | 6372 | 406,373
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48720 | 448,721
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48721 | 448,722
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48722 | 448,723
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48723 | 448,724
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48724 | 448,725
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48725 | 448,726
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48726 | 448,727
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48727 | 448,728
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48728 | 448,729
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48729 | 448,730
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48730 | 448,731
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48731 | 448,732
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48732 | 448,733
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48733 | 448,734
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48734 | 448,735
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48735 | 448,736
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48736 | 448,737
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48737 | 448,738
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48738 | 448,739
15 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48739 | 448,740
15 | 21 | 1 | Current | 3 | Current Read | Monitor current of S&H transmitter. |  |  | IEEE Float | R | 6410 | 406,411
15 | 21 | 2 | Current | 3 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | Enumeration | R | 6412 | 406,413
15 | 21 | 3 | Current | 3 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | Enumeration | R | 6414 | 406,415
15 | 21 | 4 | Current | 3 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | Enumeration | R/W | 6416 | 406,417
15 | 21 | 5 | Current | 3 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | Enumeration | R/W | 6418 | 406,419
15 | 21 | 7 | Current | 3 | Load Current RMS | Monitor current of CUR transmitter. |  |  | IEEE Float | R | 6422 | 406,423
15 | 21 | 8 | Current | 3 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | IEEE Float | R/W | 6424 | 406,425
15 | 21 | 9 | Current | 3 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 6426 | 406,427
15 | 21 | 10 | Current | 3 | Current Gain | Monitor the Gain setting. |  | 0.17 | IEEE Float | R | 6428 | 406,429
15 | 21 | 11 | Current | 3 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 6430 | 406,431
15 | 21 | 12 | Current | 3 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | Unsigned 16-bit | R/W | 6432 | 406,433
15 | 21 | 19 | Current | 3 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6446 | 406,447
15 | 21 | 20 | Current | 3 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | IEEE Float | R | 6448 | 406,449
15 | 21 | 21 | Current | 3 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | Enumeration | R | 6450 | 406,451
15 | 21 | 22 | Current | 3 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | IEEE Float | R/W | 6452 | 406,453
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48740 | 448,741
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48741 | 448,742
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48742 | 448,743
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48743 | 448,744
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48744 | 448,745
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48745 | 448,746
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48746 | 448,747
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48747 | 448,748
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48748 | 448,749
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48749 | 448,750
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48750 | 448,751
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48751 | 448,752
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48752 | 448,753
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48753 | 448,754
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48754 | 448,755
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48755 | 448,756
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48756 | 448,757
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48757 | 448,758
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48758 | 448,759
15 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48759 | 448,760
15 | 31 | 1 | Current | 4 | Current Read | Monitor current of S&H transmitter. |  |  | IEEE Float | R | 6490 | 406,491
15 | 31 | 2 | Current | 4 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | Enumeration | R | 6492 | 406,493
15 | 31 | 3 | Current | 4 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | Enumeration | R | 6494 | 406,495
15 | 31 | 4 | Current | 4 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | Enumeration | R/W | 6496 | 406,497
15 | 31 | 5 | Current | 4 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | Enumeration | R/W | 6498 | 406,499
15 | 31 | 7 | Current | 4 | Load Current RMS | Monitor current of CUR transmitter. |  |  | IEEE Float | R | 6502 | 406,503
15 | 31 | 8 | Current | 4 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | IEEE Float | R/W | 6504 | 406,505
15 | 31 | 9 | Current | 4 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 6506 | 406,507
15 | 31 | 10 | Current | 4 | Current Gain | Monitor the Gain setting. |  | 0.17 | IEEE Float | R | 6508 | 406,509
15 | 31 | 11 | Current | 4 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 6510 | 406,511
15 | 31 | 12 | Current | 4 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | Unsigned 16-bit | R/W | 6512 | 406,513
15 | 31 | 19 | Current | 4 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6526 | 406,527
15 | 31 | 20 | Current | 4 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | IEEE Float | R | 6528 | 406,529
15 | 31 | 21 | Current | 4 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | Enumeration | R | 6530 | 406,531
15 | 31 | 22 | Current | 4 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | IEEE Float | R/W | 6532 | 406,533
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48760 | 448,761
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48761 | 448,762
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48762 | 448,763
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48763 | 448,764
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48764 | 448,765
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48765 | 448,766
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48766 | 448,767
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48767 | 448,768
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48768 | 448,769
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48769 | 448,770
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48770 | 448,771
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48771 | 448,772
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48772 | 448,773
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48773 | 448,774
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48774 | 448,775
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48775 | 448,776
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48776 | 448,777
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48777 | 448,778
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48778 | 448,779
15 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48779 | 448,780
15 | 41 | 1 | Current | 5 | Current Read | Monitor current of S&H transmitter. |  |  | IEEE Float | R | 6570 | 406,571
15 | 41 | 2 | Current | 5 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | Enumeration | R | 6572 | 406,573
15 | 41 | 3 | Current | 5 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | Enumeration | R | 6574 | 406,575
15 | 41 | 4 | Current | 5 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | Enumeration | R/W | 6576 | 406,577
15 | 41 | 5 | Current | 5 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | Enumeration | R/W | 6578 | 406,579
15 | 41 | 7 | Current | 5 | Load Current RMS | Monitor current of CUR transmitter. |  |  | IEEE Float | R | 6582 | 406,583
15 | 41 | 8 | Current | 5 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | IEEE Float | R/W | 6584 | 406,585
15 | 41 | 9 | Current | 5 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 6586 | 406,587
15 | 41 | 10 | Current | 5 | Current Gain | Monitor the Gain setting. |  | 0.17 | IEEE Float | R | 6588 | 406,589
15 | 41 | 11 | Current | 5 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 6590 | 406,591
15 | 41 | 12 | Current | 5 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | Unsigned 16-bit | R/W | 6592 | 406,593
15 | 41 | 19 | Current | 5 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6606 | 406,607
15 | 41 | 20 | Current | 5 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | IEEE Float | R | 6608 | 406,609
15 | 41 | 21 | Current | 5 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | Enumeration | R | 6610 | 406,611
15 | 41 | 22 | Current | 5 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | IEEE Float | R/W | 6612 | 406,613
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48780 | 448,781
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48781 | 448,782
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48782 | 448,783
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48783 | 448,784
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48784 | 448,785
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48785 | 448,786
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48786 | 448,787
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48787 | 448,788
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48788 | 448,789
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48789 | 448,790
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48790 | 448,791
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48791 | 448,792
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48792 | 448,793
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48793 | 448,794
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48794 | 448,795
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48795 | 448,796
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48796 | 448,797
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48797 | 448,798
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48798 | 448,799
15 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48799 | 448,800
15 | 51 | 1 | Current | 6 | Current Read | Monitor current of S&H transmitter. |  |  | IEEE Float | R | 6650 | 406,651
15 | 51 | 2 | Current | 6 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | Enumeration | R | 6652 | 406,653
15 | 51 | 3 | Current | 6 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | Enumeration | R | 6654 | 406,655
15 | 51 | 4 | Current | 6 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | Enumeration | R/W | 6656 | 406,657
15 | 51 | 5 | Current | 6 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | Enumeration | R/W | 6658 | 406,659
15 | 51 | 7 | Current | 6 | Load Current RMS | Monitor current of CUR transmitter. |  |  | IEEE Float | R | 6662 | 406,663
15 | 51 | 8 | Current | 6 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | IEEE Float | R/W | 6664 | 406,665
15 | 51 | 9 | Current | 6 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 6666 | 406,667
15 | 51 | 10 | Current | 6 | Current Gain | Monitor the Gain setting. |  | 0.17 | IEEE Float | R | 6668 | 406,669
15 | 51 | 11 | Current | 6 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 6670 | 406,671
15 | 51 | 12 | Current | 6 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | Unsigned 16-bit | R/W | 6672 | 406,673
15 | 51 | 19 | Current | 6 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6686 | 406,687
15 | 51 | 20 | Current | 6 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | IEEE Float | R | 6688 | 406,689
15 | 51 | 21 | Current | 6 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | Enumeration | R | 6690 | 406,691
15 | 51 | 22 | Current | 6 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | IEEE Float | R/W | 6692 | 406,693
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48800 | 448,801
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48801 | 448,802
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48802 | 448,803
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48803 | 448,804
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48804 | 448,805
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48805 | 448,806
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48806 | 448,807
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48807 | 448,808
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48808 | 448,809
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48809 | 448,810
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48810 | 448,811
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48811 | 448,812
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48812 | 448,813
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48813 | 448,814
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48814 | 448,815
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48815 | 448,816
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48816 | 448,817
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48817 | 448,818
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48818 | 448,819
15 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48819 | 448,820
18 | 1 | 1 | Analog Output | 1 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 32566 | 432,567
18 | 1 | 2 | Analog Output | 1 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 32568 | 432,569
18 | 1 | 4 | Analog Output | 1 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 32572 | 432,573
18 | 1 | 5 | Analog Output | 1 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32574 | 432,575
18 | 1 | 6 | Analog Output | 1 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32576 | 432,577
18 | 1 | 7 | Analog Output | 1 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32578 | 432,579
18 | 1 | 8 | Analog Output | 1 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32580 | 432,581
18 | 1 | 9 | Analog Output | 1 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 32582 | 432,583
18 | 1 | 10 | Analog Output | 1 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 32584 | 432,585
18 | 1 | 11 | Analog Output | 1 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32586 | 432,587
18 | 1 | 12 | Analog Output | 1 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 32588 | 432,589
18 | 1 | 16 | Analog Output | 1 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 32596 | 432,597
18 | 1 | 17 | Analog Output | 1 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 32598 | 432,599
18 | 1 | 18 | Analog Output | 1 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 32600 | 432,601
18 | 1 | 19 | Analog Output | 1 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 32602 | 432,603
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48820 | 448,821
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48821 | 448,822
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48822 | 448,823
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48823 | 448,824
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48824 | 448,825
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48825 | 448,826
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48826 | 448,827
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48827 | 448,828
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48828 | 448,829
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48829 | 448,830
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48830 | 448,831
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48831 | 448,832
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48832 | 448,833
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48833 | 448,834
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48834 | 448,835
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48835 | 448,836
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48836 | 448,837
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48837 | 448,838
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48838 | 448,839
18 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48839 | 448,840
18 | 1 | 25 | Analog Output | 1 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 32614 | 432,615
18 | 2 | 1 | Analog Output | 1 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 32616 | 432,617
18 | 2 | 2 | Analog Output | 1 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 32618 | 432,619
18 | 2 | 4 | Analog Output | 1 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 32622 | 432,623
18 | 2 | 5 | Analog Output | 1 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32624 | 432,625
18 | 2 | 6 | Analog Output | 1 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32626 | 432,627
18 | 2 | 7 | Analog Output | 1 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32628 | 432,629
18 | 2 | 8 | Analog Output | 1 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32630 | 432,631
18 | 2 | 9 | Analog Output | 1 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 32632 | 432,633
18 | 2 | 10 | Analog Output | 1 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 32634 | 432,635
18 | 2 | 11 | Analog Output | 1 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32636 | 432,637
18 | 2 | 12 | Analog Output | 1 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 32638 | 432,639
18 | 2 | 16 | Analog Output | 1 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 32646 | 432,647
18 | 2 | 17 | Analog Output | 1 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 32648 | 432,649
18 | 2 | 18 | Analog Output | 1 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 32650 | 432,651
18 | 2 | 19 | Analog Output | 1 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 32652 | 432,653
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48840 | 448,841
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48841 | 448,842
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48842 | 448,843
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48843 | 448,844
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48844 | 448,845
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48845 | 448,846
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48846 | 448,847
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48847 | 448,848
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48848 | 448,849
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48849 | 448,850
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48850 | 448,851
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48851 | 448,852
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48852 | 448,853
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48853 | 448,854
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48854 | 448,855
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48855 | 448,856
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48856 | 448,857
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48857 | 448,858
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48858 | 448,859
18 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48859 | 448,860
18 | 2 | 25 | Analog Output | 1 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 32664 | 432,665
18 | 3 | 1 | Analog Output | 1 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 32666 | 432,667
18 | 3 | 2 | Analog Output | 1 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 32668 | 432,669
18 | 3 | 4 | Analog Output | 1 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 32672 | 432,673
18 | 3 | 5 | Analog Output | 1 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32674 | 432,675
18 | 3 | 6 | Analog Output | 1 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32676 | 432,677
18 | 3 | 7 | Analog Output | 1 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32678 | 432,679
18 | 3 | 8 | Analog Output | 1 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32680 | 432,681
18 | 3 | 9 | Analog Output | 1 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 32682 | 432,683
18 | 3 | 10 | Analog Output | 1 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 32684 | 432,685
18 | 3 | 11 | Analog Output | 1 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32686 | 432,687
18 | 3 | 12 | Analog Output | 1 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 32688 | 432,689
18 | 3 | 16 | Analog Output | 1 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 32696 | 432,697
18 | 3 | 17 | Analog Output | 1 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 32698 | 432,699
18 | 3 | 18 | Analog Output | 1 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 32700 | 432,701
18 | 3 | 19 | Analog Output | 1 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 32702 | 432,703
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48860 | 448,861
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48861 | 448,862
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48862 | 448,863
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48863 | 448,864
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48864 | 448,865
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48865 | 448,866
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48866 | 448,867
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48867 | 448,868
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48868 | 448,869
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48869 | 448,870
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48870 | 448,871
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48871 | 448,872
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48872 | 448,873
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48873 | 448,874
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48874 | 448,875
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48875 | 448,876
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48876 | 448,877
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48877 | 448,878
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48878 | 448,879
18 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48879 | 448,880
18 | 3 | 25 | Analog Output | 1 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 32714 | 432,715
18 | 11 | 1 | Analog Output | 2 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 32716 | 432,717
18 | 11 | 2 | Analog Output | 2 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 32718 | 432,719
18 | 11 | 4 | Analog Output | 2 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 32722 | 432,723
18 | 11 | 5 | Analog Output | 2 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32724 | 432,725
18 | 11 | 6 | Analog Output | 2 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32726 | 432,727
18 | 11 | 7 | Analog Output | 2 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32728 | 432,729
18 | 11 | 8 | Analog Output | 2 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32730 | 432,731
18 | 11 | 9 | Analog Output | 2 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 32732 | 432,733
18 | 11 | 10 | Analog Output | 2 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 32734 | 432,735
18 | 11 | 11 | Analog Output | 2 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32736 | 432,737
18 | 11 | 12 | Analog Output | 2 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 32738 | 432,739
18 | 11 | 16 | Analog Output | 2 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 32746 | 432,747
18 | 11 | 17 | Analog Output | 2 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 32748 | 432,749
18 | 11 | 18 | Analog Output | 2 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 32750 | 432,751
18 | 11 | 19 | Analog Output | 2 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 32752 | 432,753
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48880 | 448,881
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48881 | 448,882
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48882 | 448,883
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48883 | 448,884
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48884 | 448,885
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48885 | 448,886
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48886 | 448,887
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48887 | 448,888
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48888 | 448,889
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48889 | 448,890
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48890 | 448,891
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48891 | 448,892
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48892 | 448,893
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48893 | 448,894
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48894 | 448,895
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48895 | 448,896
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48896 | 448,897
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48897 | 448,898
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48898 | 448,899
18 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48899 | 448,900
18 | 11 | 25 | Analog Output | 2 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 32764 | 432,765
18 | 12 | 1 | Analog Output | 2 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 32766 | 432,767
18 | 12 | 2 | Analog Output | 2 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 32768 | 432,769
18 | 12 | 4 | Analog Output | 2 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 32772 | 432,773
18 | 12 | 5 | Analog Output | 2 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32774 | 432,775
18 | 12 | 6 | Analog Output | 2 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32776 | 432,777
18 | 12 | 7 | Analog Output | 2 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32778 | 432,779
18 | 12 | 8 | Analog Output | 2 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32780 | 432,781
18 | 12 | 9 | Analog Output | 2 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 32782 | 432,783
18 | 12 | 10 | Analog Output | 2 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 32784 | 432,785
18 | 12 | 11 | Analog Output | 2 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32786 | 432,787
18 | 12 | 12 | Analog Output | 2 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 32788 | 432,789
18 | 12 | 16 | Analog Output | 2 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 32796 | 432,797
18 | 12 | 17 | Analog Output | 2 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 32798 | 432,799
18 | 12 | 18 | Analog Output | 2 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 32800 | 432,801
18 | 12 | 19 | Analog Output | 2 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 32802 | 432,803
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48900 | 448,901
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48901 | 448,902
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48902 | 448,903
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48903 | 448,904
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48904 | 448,905
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48905 | 448,906
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48906 | 448,907
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48907 | 448,908
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48908 | 448,909
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48909 | 448,910
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48910 | 448,911
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48911 | 448,912
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48912 | 448,913
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48913 | 448,914
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48914 | 448,915
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48915 | 448,916
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48916 | 448,917
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48917 | 448,918
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48918 | 448,919
18 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48919 | 448,920
18 | 12 | 25 | Analog Output | 2 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 32814 | 432,815
18 | 13 | 1 | Analog Output | 2 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 32816 | 432,817
18 | 13 | 2 | Analog Output | 2 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 32818 | 432,819
18 | 13 | 4 | Analog Output | 2 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 32822 | 432,823
18 | 13 | 5 | Analog Output | 2 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32824 | 432,825
18 | 13 | 6 | Analog Output | 2 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32826 | 432,827
18 | 13 | 7 | Analog Output | 2 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32828 | 432,829
18 | 13 | 8 | Analog Output | 2 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32830 | 432,831
18 | 13 | 9 | Analog Output | 2 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 32832 | 432,833
18 | 13 | 10 | Analog Output | 2 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 32834 | 432,835
18 | 13 | 11 | Analog Output | 2 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32836 | 432,837
18 | 13 | 12 | Analog Output | 2 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 32838 | 432,839
18 | 13 | 16 | Analog Output | 2 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 32846 | 432,847
18 | 13 | 17 | Analog Output | 2 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 32848 | 432,849
18 | 13 | 18 | Analog Output | 2 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 32850 | 432,851
18 | 13 | 19 | Analog Output | 2 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 32852 | 432,853
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48920 | 448,921
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48921 | 448,922
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48922 | 448,923
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48923 | 448,924
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48924 | 448,925
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48925 | 448,926
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48926 | 448,927
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48927 | 448,928
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48928 | 448,929
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48929 | 448,930
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48930 | 448,931
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48931 | 448,932
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48932 | 448,933
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48933 | 448,934
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48934 | 448,935
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48935 | 448,936
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48936 | 448,937
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48937 | 448,938
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48938 | 448,939
18 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48939 | 448,940
18 | 13 | 25 | Analog Output | 2 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 32864 | 432,865
18 | 21 | 1 | Analog Output | 3 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 32866 | 432,867
18 | 21 | 2 | Analog Output | 3 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 32868 | 432,869
18 | 21 | 4 | Analog Output | 3 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 32872 | 432,873
18 | 21 | 5 | Analog Output | 3 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32874 | 432,875
18 | 21 | 6 | Analog Output | 3 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32876 | 432,877
18 | 21 | 7 | Analog Output | 3 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32878 | 432,879
18 | 21 | 8 | Analog Output | 3 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32880 | 432,881
18 | 21 | 9 | Analog Output | 3 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 32882 | 432,883
18 | 21 | 10 | Analog Output | 3 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 32884 | 432,885
18 | 21 | 11 | Analog Output | 3 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32886 | 432,887
18 | 21 | 12 | Analog Output | 3 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 32888 | 432,889
18 | 21 | 16 | Analog Output | 3 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 32896 | 432,897
18 | 21 | 17 | Analog Output | 3 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 32898 | 432,899
18 | 21 | 18 | Analog Output | 3 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 32900 | 432,901
18 | 21 | 19 | Analog Output | 3 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 32902 | 432,903
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48940 | 448,941
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48941 | 448,942
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48942 | 448,943
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48943 | 448,944
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48944 | 448,945
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48945 | 448,946
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48946 | 448,947
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48947 | 448,948
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48948 | 448,949
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48949 | 448,950
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48950 | 448,951
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48951 | 448,952
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48952 | 448,953
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48953 | 448,954
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48954 | 448,955
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48955 | 448,956
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48956 | 448,957
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48957 | 448,958
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48958 | 448,959
18 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48959 | 448,960
18 | 21 | 25 | Analog Output | 3 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 32914 | 432,915
18 | 22 | 1 | Analog Output | 3 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 32916 | 432,917
18 | 22 | 2 | Analog Output | 3 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 32918 | 432,919
18 | 22 | 4 | Analog Output | 3 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 32922 | 432,923
18 | 22 | 5 | Analog Output | 3 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32924 | 432,925
18 | 22 | 6 | Analog Output | 3 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32926 | 432,927
18 | 22 | 7 | Analog Output | 3 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32928 | 432,929
18 | 22 | 8 | Analog Output | 3 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32930 | 432,931
18 | 22 | 9 | Analog Output | 3 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 32932 | 432,933
18 | 22 | 10 | Analog Output | 3 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 32934 | 432,935
18 | 22 | 11 | Analog Output | 3 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32936 | 432,937
18 | 22 | 12 | Analog Output | 3 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 32938 | 432,939
18 | 22 | 16 | Analog Output | 3 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 32946 | 432,947
18 | 22 | 17 | Analog Output | 3 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 32948 | 432,949
18 | 22 | 18 | Analog Output | 3 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 32950 | 432,951
18 | 22 | 19 | Analog Output | 3 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 32952 | 432,953
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48960 | 448,961
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48961 | 448,962
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48962 | 448,963
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48963 | 448,964
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48964 | 448,965
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48965 | 448,966
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48966 | 448,967
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48967 | 448,968
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48968 | 448,969
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48969 | 448,970
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48970 | 448,971
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48971 | 448,972
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48972 | 448,973
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48973 | 448,974
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48974 | 448,975
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48975 | 448,976
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48976 | 448,977
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48977 | 448,978
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48978 | 448,979
18 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48979 | 448,980
18 | 22 | 25 | Analog Output | 3 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 32964 | 432,965
18 | 23 | 1 | Analog Output | 3 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 32966 | 432,967
18 | 23 | 2 | Analog Output | 3 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 32968 | 432,969
18 | 23 | 4 | Analog Output | 3 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 32972 | 432,973
18 | 23 | 5 | Analog Output | 3 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32974 | 432,975
18 | 23 | 6 | Analog Output | 3 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32976 | 432,977
18 | 23 | 7 | Analog Output | 3 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32978 | 432,979
18 | 23 | 8 | Analog Output | 3 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32980 | 432,981
18 | 23 | 9 | Analog Output | 3 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 32982 | 432,983
18 | 23 | 10 | Analog Output | 3 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 32984 | 432,985
18 | 23 | 11 | Analog Output | 3 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32986 | 432,987
18 | 23 | 12 | Analog Output | 3 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 32988 | 432,989
18 | 23 | 16 | Analog Output | 3 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 32996 | 432,997
18 | 23 | 17 | Analog Output | 3 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 32998 | 432,999
18 | 23 | 18 | Analog Output | 3 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 33000 | 433,001
18 | 23 | 19 | Analog Output | 3 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33002 | 433,003
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48980 | 448,981
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48981 | 448,982
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48982 | 448,983
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48983 | 448,984
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48984 | 448,985
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48985 | 448,986
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48986 | 448,987
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48987 | 448,988
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48988 | 448,989
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48989 | 448,990
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48990 | 448,991
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48991 | 448,992
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48992 | 448,993
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48993 | 448,994
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48994 | 448,995
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48995 | 448,996
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48996 | 448,997
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48997 | 448,998
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48998 | 448,999
18 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 48999 | 449,000
18 | 23 | 25 | Analog Output | 3 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 33014 | 433,015
18 | 31 | 1 | Analog Output | 4 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 33016 | 433,017
18 | 31 | 2 | Analog Output | 4 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 33018 | 433,019
18 | 31 | 4 | Analog Output | 4 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33022 | 433,023
18 | 31 | 5 | Analog Output | 4 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33024 | 433,025
18 | 31 | 6 | Analog Output | 4 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33026 | 433,027
18 | 31 | 7 | Analog Output | 4 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33028 | 433,029
18 | 31 | 8 | Analog Output | 4 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33030 | 433,031
18 | 31 | 9 | Analog Output | 4 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 33032 | 433,033
18 | 31 | 10 | Analog Output | 4 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 33034 | 433,035
18 | 31 | 11 | Analog Output | 4 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33036 | 433,037
18 | 31 | 12 | Analog Output | 4 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 33038 | 433,039
18 | 31 | 16 | Analog Output | 4 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 33046 | 433,047
18 | 31 | 17 | Analog Output | 4 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 33048 | 433,049
18 | 31 | 18 | Analog Output | 4 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 33050 | 433,051
18 | 31 | 19 | Analog Output | 4 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33052 | 433,053
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49000 | 449,001
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49001 | 449,002
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49002 | 449,003
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49003 | 449,004
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49004 | 449,005
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49005 | 449,006
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49006 | 449,007
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49007 | 449,008
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49008 | 449,009
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49009 | 449,010
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49010 | 449,011
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49011 | 449,012
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49012 | 449,013
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49013 | 449,014
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49014 | 449,015
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49015 | 449,016
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49016 | 449,017
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49017 | 449,018
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49018 | 449,019
18 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49019 | 449,020
18 | 31 | 25 | Analog Output | 4 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 33064 | 433,065
18 | 32 | 1 | Analog Output | 4 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 33066 | 433,067
18 | 32 | 2 | Analog Output | 4 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 33068 | 433,069
18 | 32 | 4 | Analog Output | 4 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33072 | 433,073
18 | 32 | 5 | Analog Output | 4 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33074 | 433,075
18 | 32 | 6 | Analog Output | 4 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33076 | 433,077
18 | 32 | 7 | Analog Output | 4 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33078 | 433,079
18 | 32 | 8 | Analog Output | 4 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33080 | 433,081
18 | 32 | 9 | Analog Output | 4 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 33082 | 433,083
18 | 32 | 10 | Analog Output | 4 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 33084 | 433,085
18 | 32 | 11 | Analog Output | 4 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33086 | 433,087
18 | 32 | 12 | Analog Output | 4 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 33088 | 433,089
18 | 32 | 16 | Analog Output | 4 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 33096 | 433,097
18 | 32 | 17 | Analog Output | 4 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 33098 | 433,099
18 | 32 | 18 | Analog Output | 4 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 33100 | 433,101
18 | 32 | 19 | Analog Output | 4 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33102 | 433,103
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49020 | 449,021
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49021 | 449,022
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49022 | 449,023
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49023 | 449,024
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49024 | 449,025
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49025 | 449,026
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49026 | 449,027
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49027 | 449,028
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49028 | 449,029
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49029 | 449,030
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49030 | 449,031
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49031 | 449,032
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49032 | 449,033
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49033 | 449,034
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49034 | 449,035
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49035 | 449,036
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49036 | 449,037
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49037 | 449,038
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49038 | 449,039
18 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49039 | 449,040
18 | 32 | 25 | Analog Output | 4 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 33114 | 433,115
18 | 33 | 1 | Analog Output | 4 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 33116 | 433,117
18 | 33 | 2 | Analog Output | 4 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 33118 | 433,119
18 | 33 | 4 | Analog Output | 4 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33122 | 433,123
18 | 33 | 5 | Analog Output | 4 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33124 | 433,125
18 | 33 | 6 | Analog Output | 4 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33126 | 433,127
18 | 33 | 7 | Analog Output | 4 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33128 | 433,129
18 | 33 | 8 | Analog Output | 4 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33130 | 433,131
18 | 33 | 9 | Analog Output | 4 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 33132 | 433,133
18 | 33 | 10 | Analog Output | 4 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 33134 | 433,135
18 | 33 | 11 | Analog Output | 4 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33136 | 433,137
18 | 33 | 12 | Analog Output | 4 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 33138 | 433,139
18 | 33 | 16 | Analog Output | 4 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 33146 | 433,147
18 | 33 | 17 | Analog Output | 4 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 33148 | 433,149
18 | 33 | 18 | Analog Output | 4 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 33150 | 433,151
18 | 33 | 19 | Analog Output | 4 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33152 | 433,153
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49040 | 449,041
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49041 | 449,042
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49042 | 449,043
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49043 | 449,044
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49044 | 449,045
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49045 | 449,046
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49046 | 449,047
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49047 | 449,048
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49048 | 449,049
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49049 | 449,050
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49050 | 449,051
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49051 | 449,052
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49052 | 449,053
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49053 | 449,054
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49054 | 449,055
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49055 | 449,056
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49056 | 449,057
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49057 | 449,058
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49058 | 449,059
18 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49059 | 449,060
18 | 33 | 25 | Analog Output | 4 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 33164 | 433,165
18 | 41 | 1 | Analog Output | 5 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 33166 | 433,167
18 | 41 | 2 | Analog Output | 5 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 33168 | 433,169
18 | 41 | 4 | Analog Output | 5 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33172 | 433,173
18 | 41 | 5 | Analog Output | 5 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33174 | 433,175
18 | 41 | 6 | Analog Output | 5 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33176 | 433,177
18 | 41 | 7 | Analog Output | 5 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33178 | 433,179
18 | 41 | 8 | Analog Output | 5 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33180 | 433,181
18 | 41 | 9 | Analog Output | 5 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 33182 | 433,183
18 | 41 | 10 | Analog Output | 5 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 33184 | 433,185
18 | 41 | 11 | Analog Output | 5 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33186 | 433,187
18 | 41 | 12 | Analog Output | 5 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 33188 | 433,189
18 | 41 | 16 | Analog Output | 5 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 33196 | 433,197
18 | 41 | 17 | Analog Output | 5 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 33198 | 433,199
18 | 41 | 18 | Analog Output | 5 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 33200 | 433,201
18 | 41 | 19 | Analog Output | 5 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33202 | 433,203
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49060 | 449,061
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49061 | 449,062
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49062 | 449,063
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49063 | 449,064
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49064 | 449,065
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49065 | 449,066
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49066 | 449,067
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49067 | 449,068
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49068 | 449,069
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49069 | 449,070
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49070 | 449,071
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49071 | 449,072
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49072 | 449,073
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49073 | 449,074
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49074 | 449,075
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49075 | 449,076
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49076 | 449,077
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49077 | 449,078
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49078 | 449,079
18 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49079 | 449,080
18 | 41 | 25 | Analog Output | 5 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 33214 | 433,215
18 | 42 | 1 | Analog Output | 5 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 33216 | 433,217
18 | 42 | 2 | Analog Output | 5 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 33218 | 433,219
18 | 42 | 4 | Analog Output | 5 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33222 | 433,223
18 | 42 | 5 | Analog Output | 5 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33224 | 433,225
18 | 42 | 6 | Analog Output | 5 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33226 | 433,227
18 | 42 | 7 | Analog Output | 5 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33228 | 433,229
18 | 42 | 8 | Analog Output | 5 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33230 | 433,231
18 | 42 | 9 | Analog Output | 5 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 33232 | 433,233
18 | 42 | 10 | Analog Output | 5 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 33234 | 433,235
18 | 42 | 11 | Analog Output | 5 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33236 | 433,237
18 | 42 | 12 | Analog Output | 5 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 33238 | 433,239
18 | 42 | 16 | Analog Output | 5 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 33246 | 433,247
18 | 42 | 17 | Analog Output | 5 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 33248 | 433,249
18 | 42 | 18 | Analog Output | 5 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 33250 | 433,251
18 | 42 | 19 | Analog Output | 5 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33252 | 433,253
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49080 | 449,081
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49081 | 449,082
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49082 | 449,083
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49083 | 449,084
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49084 | 449,085
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49085 | 449,086
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49086 | 449,087
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49087 | 449,088
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49088 | 449,089
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49089 | 449,090
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49090 | 449,091
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49091 | 449,092
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49092 | 449,093
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49093 | 449,094
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49094 | 449,095
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49095 | 449,096
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49096 | 449,097
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49097 | 449,098
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49098 | 449,099
18 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49099 | 449,100
18 | 42 | 25 | Analog Output | 5 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 33264 | 433,265
18 | 43 | 1 | Analog Output | 5 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 33266 | 433,267
18 | 43 | 2 | Analog Output | 5 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 33268 | 433,269
18 | 43 | 4 | Analog Output | 5 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33272 | 433,273
18 | 43 | 5 | Analog Output | 5 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33274 | 433,275
18 | 43 | 6 | Analog Output | 5 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33276 | 433,277
18 | 43 | 7 | Analog Output | 5 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33278 | 433,279
18 | 43 | 8 | Analog Output | 5 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33280 | 433,281
18 | 43 | 9 | Analog Output | 5 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 33282 | 433,283
18 | 43 | 10 | Analog Output | 5 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 33284 | 433,285
18 | 43 | 11 | Analog Output | 5 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33286 | 433,287
18 | 43 | 12 | Analog Output | 5 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 33288 | 433,289
18 | 43 | 16 | Analog Output | 5 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 33296 | 433,297
18 | 43 | 17 | Analog Output | 5 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 33298 | 433,299
18 | 43 | 18 | Analog Output | 5 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 33300 | 433,301
18 | 43 | 19 | Analog Output | 5 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33302 | 433,303
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49100 | 449,101
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49101 | 449,102
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49102 | 449,103
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49103 | 449,104
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49104 | 449,105
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49105 | 449,106
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49106 | 449,107
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49107 | 449,108
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49108 | 449,109
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49109 | 449,110
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49110 | 449,111
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49111 | 449,112
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49112 | 449,113
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49113 | 449,114
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49114 | 449,115
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49115 | 449,116
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49116 | 449,117
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49117 | 449,118
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49118 | 449,119
18 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49119 | 449,120
18 | 43 | 25 | Analog Output | 5 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 33314 | 433,315
18 | 51 | 1 | Analog Output | 6 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 33316 | 433,317
18 | 51 | 2 | Analog Output | 6 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 33318 | 433,319
18 | 51 | 4 | Analog Output | 6 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33322 | 433,323
18 | 51 | 5 | Analog Output | 6 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33324 | 433,325
18 | 51 | 6 | Analog Output | 6 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33326 | 433,327
18 | 51 | 7 | Analog Output | 6 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33328 | 433,329
18 | 51 | 8 | Analog Output | 6 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33330 | 433,331
18 | 51 | 9 | Analog Output | 6 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 33332 | 433,333
18 | 51 | 10 | Analog Output | 6 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 33334 | 433,335
18 | 51 | 11 | Analog Output | 6 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33336 | 433,337
18 | 51 | 12 | Analog Output | 6 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 33338 | 433,339
18 | 51 | 16 | Analog Output | 6 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 33346 | 433,347
18 | 51 | 17 | Analog Output | 6 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 33348 | 433,349
18 | 51 | 18 | Analog Output | 6 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 33350 | 433,351
18 | 51 | 19 | Analog Output | 6 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33352 | 433,353
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49120 | 449,121
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49121 | 449,122
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49122 | 449,123
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49123 | 449,124
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49124 | 449,125
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49125 | 449,126
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49126 | 449,127
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49127 | 449,128
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49128 | 449,129
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49129 | 449,130
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49130 | 449,131
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49131 | 449,132
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49132 | 449,133
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49133 | 449,134
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49134 | 449,135
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49135 | 449,136
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49136 | 449,137
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49137 | 449,138
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49138 | 449,139
18 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49139 | 449,140
18 | 51 | 25 | Analog Output | 6 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 33364 | 433,365
18 | 52 | 1 | Analog Output | 6 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 33366 | 433,367
18 | 52 | 2 | Analog Output | 6 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 33368 | 433,369
18 | 52 | 4 | Analog Output | 6 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33372 | 433,373
18 | 52 | 5 | Analog Output | 6 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33374 | 433,375
18 | 52 | 6 | Analog Output | 6 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33376 | 433,377
18 | 52 | 7 | Analog Output | 6 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33378 | 433,379
18 | 52 | 8 | Analog Output | 6 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33380 | 433,381
18 | 52 | 9 | Analog Output | 6 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 33382 | 433,383
18 | 52 | 10 | Analog Output | 6 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 33384 | 433,385
18 | 52 | 11 | Analog Output | 6 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33386 | 433,387
18 | 52 | 12 | Analog Output | 6 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 33388 | 433,389
18 | 52 | 16 | Analog Output | 6 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 33396 | 433,397
18 | 52 | 17 | Analog Output | 6 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 33398 | 433,399
18 | 52 | 18 | Analog Output | 6 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 33400 | 433,401
18 | 52 | 19 | Analog Output | 6 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33402 | 433,403
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49140 | 449,141
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49141 | 449,142
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49142 | 449,143
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49143 | 449,144
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49144 | 449,145
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49145 | 449,146
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49146 | 449,147
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49147 | 449,148
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49148 | 449,149
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49149 | 449,150
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49150 | 449,151
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49151 | 449,152
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49152 | 449,153
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49153 | 449,154
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49154 | 449,155
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49155 | 449,156
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49156 | 449,157
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49157 | 449,158
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49158 | 449,159
18 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49159 | 449,160
18 | 52 | 25 | Analog Output | 6 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 33414 | 433,415
18 | 53 | 1 | Analog Output | 6 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | Enumeration | R/W | 33416 | 433,417
18 | 53 | 2 | Analog Output | 6 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | Enumeration | R/W | 33418 | 433,419
18 | 53 | 4 | Analog Output | 6 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33422 | 433,423
18 | 53 | 5 | Analog Output | 6 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33424 | 433,425
18 | 53 | 6 | Analog Output | 6 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33426 | 433,427
18 | 53 | 7 | Analog Output | 6 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33428 | 433,429
18 | 53 | 8 | Analog Output | 6 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 33430 | 433,431
18 | 53 | 9 | Analog Output | 6 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | IEEE Float | R/W | 33432 | 433,433
18 | 53 | 10 | Analog Output | 6 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | IEEE Float | R/W | 33434 | 433,435
18 | 53 | 11 | Analog Output | 6 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 33436 | 433,437
18 | 53 | 12 | Analog Output | 6 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 33438 | 433,439
18 | 53 | 16 | Analog Output | 6 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | IEEE Float | R | 33446 | 433,447
18 | 53 | 17 | Analog Output | 6 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | Enumeration | R/W | 33448 | 433,449
18 | 53 | 18 | Analog Output | 6 | Source Value A | Monitor the source value driving the output. |  |  | IEEE Float | R | 33450 | 433,451
18 | 53 | 19 | Analog Output | 6 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33452 | 433,453
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49160 | 449,161
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49161 | 449,162
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49162 | 449,163
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49163 | 449,164
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49164 | 449,165
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49165 | 449,166
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49166 | 449,167
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49167 | 449,168
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49168 | 449,169
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49169 | 449,170
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49170 | 449,171
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49171 | 449,172
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49172 | 449,173
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49173 | 449,174
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49174 | 449,175
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49175 | 449,176
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49176 | 449,177
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49177 | 449,178
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49178 | 449,179
18 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49179 | 449,180
18 | 53 | 25 | Analog Output | 6 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | Enumeration | R | 33464 | 433,465
19 | 1 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 840 | 400,841
19 | 1 | 2 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 842 | 400,843
19 | 1 | 3 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 844 | 400,845
19 | 1 | 4 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 846 | 400,847
19 | 1 | 5 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 848 | 400,849
19 | 1 | 6 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 850 | 400,851
19 | 1 | 7 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 852 | 400,853
19 | 1 | 8 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 854 | 400,855
19 | 1 | 9 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 856 | 400,857
19 | 1 | 10 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 858 | 400,859
19 | 1 | 11 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 860 | 400,861
19 | 1 | 12 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 862 | 400,863
19 | 1 | 13 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 864 | 400,865
19 | 1 | 14 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 866 | 400,867
19 | 1 | 15 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 868 | 400,869
19 | 1 | 16 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 870 | 400,871
19 | 1 | 17 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 872 | 400,873
19 | 1 | 18 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 874 | 400,875
19 | 1 | 19 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 876 | 400,877
19 | 1 | 20 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 878 | 400,879
19 | 1 | 21 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 880 | 400,881
19 | 1 | 22 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 882 | 400,883
19 | 1 | 23 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 884 | 400,885
19 | 1 | 24 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 886 | 400,887
19 | 1 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 888 | 400,889
19 | 1 | 26 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 890 | 400,891
19 | 1 | 27 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 892 | 400,893
19 | 1 | 28 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 894 | 400,895
19 | 1 | 29 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 896 | 400,897
19 | 1 | 30 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 898 | 400,899
19 | 1 | 31 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 900 | 400,901
19 | 1 | 32 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 902 | 400,903
19 | 1 | 33 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 904 | 400,905
19 | 1 | 34 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 906 | 400,907
19 | 1 | 35 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 908 | 400,909
19 | 1 | 36 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 910 | 400,911
19 | 1 | 37 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 912 | 400,913
19 | 1 | 38 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 914 | 400,915
19 | 1 | 39 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 916 | 400,917
19 | 1 | 40 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 918 | 400,919
19 | 1 | 41 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 920 | 400,921
19 | 1 | 42 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 922 | 400,923
19 | 1 | 43 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 924 | 400,925
19 | 1 | 44 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 926 | 400,927
19 | 1 | 45 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 928 | 400,929
19 | 1 | 46 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 930 | 400,931
19 | 1 | 47 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 932 | 400,933
19 | 1 | 48 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 934 | 400,935
19 | 1 | 49 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 936 | 400,937
19 | 1 | 50 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 938 | 400,939
19 | 1 | 51 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 940 | 400,941
19 | 1 | 52 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 942 | 400,943
19 | 1 | 53 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 944 | 400,945
19 | 1 | 54 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 946 | 400,947
19 | 1 | 55 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 948 | 400,949
19 | 1 | 56 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 950 | 400,951
19 | 1 | 57 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 952 | 400,953
19 | 1 | 58 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 954 | 400,955
19 | 1 | 59 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 956 | 400,957
19 | 1 | 60 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 958 | 400,959
19 | 25 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 960 | 400,961
19 | 25 | 2 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 962 | 400,963
19 | 25 | 3 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 964 | 400,965
19 | 25 | 4 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 966 | 400,967
19 | 25 | 5 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 968 | 400,969
19 | 25 | 6 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 970 | 400,971
19 | 25 | 7 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 972 | 400,973
19 | 25 | 8 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 974 | 400,975
19 | 25 | 9 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 976 | 400,977
19 | 25 | 10 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 978 | 400,979
19 | 25 | 11 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 980 | 400,981
19 | 25 | 12 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 982 | 400,983
19 | 25 | 13 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 984 | 400,985
19 | 25 | 14 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 986 | 400,987
19 | 25 | 15 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 988 | 400,989
19 | 25 | 16 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 990 | 400,991
19 | 25 | 17 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 992 | 400,993
19 | 25 | 18 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 994 | 400,995
19 | 25 | 19 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 996 | 400,997
19 | 25 | 20 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 998 | 400,999
19 | 25 | 21 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1000 | 401,001
19 | 25 | 22 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1002 | 401,003
19 | 25 | 23 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1004 | 401,005
19 | 25 | 24 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1006 | 401,007
19 | 25 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1008 | 401,009
19 | 25 | 26 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1010 | 401,011
19 | 25 | 27 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1012 | 401,013
19 | 25 | 28 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1014 | 401,015
19 | 25 | 29 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1016 | 401,017
19 | 25 | 30 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1018 | 401,019
19 | 25 | 31 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1020 | 401,021
19 | 25 | 32 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1022 | 401,023
19 | 25 | 33 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1024 | 401,025
19 | 25 | 34 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1026 | 401,027
19 | 25 | 35 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1028 | 401,029
19 | 25 | 36 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1030 | 401,031
19 | 25 | 37 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1032 | 401,033
19 | 25 | 38 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1034 | 401,035
19 | 25 | 39 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1036 | 401,037
19 | 25 | 40 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1038 | 401,039
19 | 25 | 41 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1040 | 401,041
19 | 25 | 42 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1042 | 401,043
19 | 25 | 43 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1044 | 401,045
19 | 25 | 44 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1046 | 401,047
19 | 25 | 45 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1048 | 401,049
19 | 25 | 46 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1050 | 401,051
19 | 25 | 47 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1052 | 401,053
19 | 25 | 48 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1054 | 401,055
19 | 25 | 49 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1056 | 401,057
19 | 25 | 50 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1058 | 401,059
19 | 25 | 51 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1060 | 401,061
19 | 25 | 52 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1062 | 401,063
19 | 25 | 53 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1064 | 401,065
19 | 25 | 54 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1066 | 401,067
19 | 25 | 55 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1068 | 401,069
19 | 25 | 56 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1070 | 401,071
19 | 25 | 57 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1072 | 401,073
19 | 25 | 58 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1074 | 401,075
19 | 25 | 59 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1076 | 401,077
19 | 25 | 60 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Parameter | R/W | 1078 | 401,079
20 | 1 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1080 | 401,081
20 | 1 | 2 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1082 | 401,083
20 | 1 | 3 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1084 | 401,085
20 | 1 | 4 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1086 | 401,087
20 | 1 | 5 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1088 | 401,089
20 | 1 | 6 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1090 | 401,091
20 | 1 | 7 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1092 | 401,093
20 | 1 | 8 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1094 | 401,095
20 | 1 | 9 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1096 | 401,097
20 | 1 | 10 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1098 | 401,099
20 | 1 | 11 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1100 | 401,101
20 | 1 | 12 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1102 | 401,103
20 | 1 | 13 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1104 | 401,105
20 | 1 | 14 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1106 | 401,107
20 | 1 | 15 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1108 | 401,109
20 | 1 | 16 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1110 | 401,111
20 | 1 | 17 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1112 | 401,113
20 | 1 | 18 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1114 | 401,115
20 | 1 | 19 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1116 | 401,117
20 | 1 | 20 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1118 | 401,119
20 | 1 | 21 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1120 | 401,121
20 | 1 | 22 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1122 | 401,123
20 | 1 | 23 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1124 | 401,125
20 | 1 | 24 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1126 | 401,127
20 | 1 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1128 | 401,129
20 | 1 | 26 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1130 | 401,131
20 | 1 | 27 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1132 | 401,133
20 | 1 | 28 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1134 | 401,135
20 | 1 | 29 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1136 | 401,137
20 | 1 | 30 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1138 | 401,139
20 | 1 | 31 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1140 | 401,141
20 | 1 | 32 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1142 | 401,143
20 | 1 | 33 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1144 | 401,145
20 | 1 | 34 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1146 | 401,147
20 | 1 | 35 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1148 | 401,149
20 | 1 | 36 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1150 | 401,151
20 | 1 | 37 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1152 | 401,153
20 | 1 | 38 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1154 | 401,155
20 | 1 | 39 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1156 | 401,157
20 | 1 | 40 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1158 | 401,159
20 | 1 | 41 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1160 | 401,161
20 | 1 | 42 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1162 | 401,163
20 | 1 | 43 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1164 | 401,165
20 | 1 | 44 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1166 | 401,167
20 | 1 | 45 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1168 | 401,169
20 | 1 | 46 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1170 | 401,171
20 | 1 | 47 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1172 | 401,173
20 | 1 | 48 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1174 | 401,175
20 | 1 | 49 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1176 | 401,177
20 | 1 | 50 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1178 | 401,179
20 | 1 | 51 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1180 | 401,181
20 | 1 | 52 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1182 | 401,183
20 | 1 | 53 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1184 | 401,185
20 | 1 | 54 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1186 | 401,187
20 | 1 | 55 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1188 | 401,189
20 | 1 | 56 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1190 | 401,191
20 | 1 | 57 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1192 | 401,193
20 | 1 | 58 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1194 | 401,195
20 | 1 | 59 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1196 | 401,197
20 | 1 | 60 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1198 | 401,199
20 | 25 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1200 | 401,201
20 | 25 | 2 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1202 | 401,203
20 | 25 | 3 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1204 | 401,205
20 | 25 | 4 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1206 | 401,207
20 | 25 | 5 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1208 | 401,209
20 | 25 | 6 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1210 | 401,211
20 | 25 | 7 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1212 | 401,213
20 | 25 | 8 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1214 | 401,215
20 | 25 | 9 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1216 | 401,217
20 | 25 | 10 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1218 | 401,219
20 | 25 | 11 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1220 | 401,221
20 | 25 | 12 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1222 | 401,223
20 | 25 | 13 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1224 | 401,225
20 | 25 | 14 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1226 | 401,227
20 | 25 | 15 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1228 | 401,229
20 | 25 | 16 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1230 | 401,231
20 | 25 | 17 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1232 | 401,233
20 | 25 | 18 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1234 | 401,235
20 | 25 | 19 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1236 | 401,237
20 | 25 | 20 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1238 | 401,239
20 | 25 | 21 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1240 | 401,241
20 | 25 | 22 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1242 | 401,243
20 | 25 | 23 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1244 | 401,245
20 | 25 | 24 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1246 | 401,247
20 | 25 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1248 | 401,249
20 | 25 | 26 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1250 | 401,251
20 | 25 | 27 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1252 | 401,253
20 | 25 | 28 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1254 | 401,255
20 | 25 | 29 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1256 | 401,257
20 | 25 | 30 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1258 | 401,259
20 | 25 | 31 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1260 | 401,261
20 | 25 | 32 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1262 | 401,263
20 | 25 | 33 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1264 | 401,265
20 | 25 | 34 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1266 | 401,267
20 | 25 | 35 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1268 | 401,269
20 | 25 | 36 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1270 | 401,271
20 | 25 | 37 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1272 | 401,273
20 | 25 | 38 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1274 | 401,275
20 | 25 | 39 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1276 | 401,277
20 | 25 | 40 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1278 | 401,279
20 | 25 | 41 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1280 | 401,281
20 | 25 | 42 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1282 | 401,283
20 | 25 | 43 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1284 | 401,285
20 | 25 | 44 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1286 | 401,287
20 | 25 | 45 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1288 | 401,289
20 | 25 | 46 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1290 | 401,291
20 | 25 | 47 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1292 | 401,293
20 | 25 | 48 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1294 | 401,295
20 | 25 | 49 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1296 | 401,297
20 | 25 | 50 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1298 | 401,299
20 | 25 | 51 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1300 | 401,301
20 | 25 | 52 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1302 | 401,303
20 | 25 | 53 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1304 | 401,305
20 | 25 | 54 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1306 | 401,307
20 | 25 | 55 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1308 | 401,309
20 | 25 | 56 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1310 | 401,311
20 | 25 | 57 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1312 | 401,313
20 | 25 | 58 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1314 | 401,315
20 | 25 | 59 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1316 | 401,317
20 | 25 | 60 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 1318 | 401,319
25 | 1 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12160 | 412,161
25 | 1 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12162 | 412,163
25 | 1 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12164 | 412,165
25 | 1 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12166 | 412,167
25 | 1 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 12168 | 412,169
25 | 1 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12170 | 412,171
25 | 1 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12172 | 412,173
25 | 1 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12174 | 412,175
25 | 1 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12176 | 412,177
25 | 1 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12178 | 412,179
25 | 1 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12180 | 412,181
25 | 1 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12182 | 412,183
25 | 1 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12184 | 412,185
25 | 1 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12186 | 412,187
25 | 1 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12188 | 412,189
25 | 1 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 12190 | 412,191
25 | 1 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 12192 | 412,193
25 | 1 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 12194 | 412,195
25 | 1 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 12196 | 412,197
25 | 1 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 12198 | 412,199
25 | 1 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 12200 | 412,201
25 | 1 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 12202 | 412,203
25 | 1 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12204 | 412,205
25 | 1 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12206 | 412,207
25 | 1 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12208 | 412,209
25 | 1 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12210 | 412,211
25 | 1 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12212 | 412,213
25 | 1 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 12214 | 412,215
25 | 1 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 12216 | 412,217
25 | 1 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 12218 | 412,219
25 | 1 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 12220 | 412,221
25 | 1 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 12222 | 412,223
25 | 2 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12240 | 412,241
25 | 2 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12242 | 412,243
25 | 2 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12244 | 412,245
25 | 2 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12246 | 412,247
25 | 2 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 12248 | 412,249
25 | 2 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12250 | 412,251
25 | 2 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12252 | 412,253
25 | 2 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12254 | 412,255
25 | 2 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12256 | 412,257
25 | 2 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12258 | 412,259
25 | 2 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12260 | 412,261
25 | 2 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12262 | 412,263
25 | 2 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12264 | 412,265
25 | 2 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12266 | 412,267
25 | 2 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12268 | 412,269
25 | 2 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 12270 | 412,271
25 | 2 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 12272 | 412,273
25 | 2 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 12274 | 412,275
25 | 2 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 12276 | 412,277
25 | 2 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 12278 | 412,279
25 | 2 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 12280 | 412,281
25 | 2 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 12282 | 412,283
25 | 2 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12284 | 412,285
25 | 2 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12286 | 412,287
25 | 2 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12288 | 412,289
25 | 2 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12290 | 412,291
25 | 2 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12292 | 412,293
25 | 2 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 12294 | 412,295
25 | 2 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 12296 | 412,297
25 | 2 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 12298 | 412,299
25 | 2 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 12300 | 412,301
25 | 2 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 12302 | 412,303
25 | 3 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12320 | 412,321
25 | 3 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12322 | 412,323
25 | 3 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12324 | 412,325
25 | 3 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12326 | 412,327
25 | 3 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 12328 | 412,329
25 | 3 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12330 | 412,331
25 | 3 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12332 | 412,333
25 | 3 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12334 | 412,335
25 | 3 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12336 | 412,337
25 | 3 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12338 | 412,339
25 | 3 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12340 | 412,341
25 | 3 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12342 | 412,343
25 | 3 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12344 | 412,345
25 | 3 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12346 | 412,347
25 | 3 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12348 | 412,349
25 | 3 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 12350 | 412,351
25 | 3 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 12352 | 412,353
25 | 3 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 12354 | 412,355
25 | 3 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 12356 | 412,357
25 | 3 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 12358 | 412,359
25 | 3 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 12360 | 412,361
25 | 3 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 12362 | 412,363
25 | 3 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12364 | 412,365
25 | 3 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12366 | 412,367
25 | 3 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12368 | 412,369
25 | 3 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12370 | 412,371
25 | 3 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12372 | 412,373
25 | 3 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 12374 | 412,375
25 | 3 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 12376 | 412,377
25 | 3 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 12378 | 412,379
25 | 3 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 12380 | 412,381
25 | 3 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 12382 | 412,383
25 | 4 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12400 | 412,401
25 | 4 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12402 | 412,403
25 | 4 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12404 | 412,405
25 | 4 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12406 | 412,407
25 | 4 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 12408 | 412,409
25 | 4 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12410 | 412,411
25 | 4 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12412 | 412,413
25 | 4 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12414 | 412,415
25 | 4 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12416 | 412,417
25 | 4 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12418 | 412,419
25 | 4 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12420 | 412,421
25 | 4 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12422 | 412,423
25 | 4 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12424 | 412,425
25 | 4 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12426 | 412,427
25 | 4 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12428 | 412,429
25 | 4 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 12430 | 412,431
25 | 4 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 12432 | 412,433
25 | 4 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 12434 | 412,435
25 | 4 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 12436 | 412,437
25 | 4 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 12438 | 412,439
25 | 4 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 12440 | 412,441
25 | 4 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 12442 | 412,443
25 | 4 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12444 | 412,445
25 | 4 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12446 | 412,447
25 | 4 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12448 | 412,449
25 | 4 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12450 | 412,451
25 | 4 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12452 | 412,453
25 | 4 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 12454 | 412,455
25 | 4 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 12456 | 412,457
25 | 4 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 12458 | 412,459
25 | 4 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 12460 | 412,461
25 | 4 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 12462 | 412,463
25 | 5 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12480 | 412,481
25 | 5 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12482 | 412,483
25 | 5 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12484 | 412,485
25 | 5 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12486 | 412,487
25 | 5 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 12488 | 412,489
25 | 5 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12490 | 412,491
25 | 5 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12492 | 412,493
25 | 5 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12494 | 412,495
25 | 5 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12496 | 412,497
25 | 5 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12498 | 412,499
25 | 5 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12500 | 412,501
25 | 5 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12502 | 412,503
25 | 5 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12504 | 412,505
25 | 5 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12506 | 412,507
25 | 5 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12508 | 412,509
25 | 5 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 12510 | 412,511
25 | 5 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 12512 | 412,513
25 | 5 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 12514 | 412,515
25 | 5 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 12516 | 412,517
25 | 5 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 12518 | 412,519
25 | 5 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 12520 | 412,521
25 | 5 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 12522 | 412,523
25 | 5 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12524 | 412,525
25 | 5 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12526 | 412,527
25 | 5 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12528 | 412,529
25 | 5 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12530 | 412,531
25 | 5 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12532 | 412,533
25 | 5 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 12534 | 412,535
25 | 5 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 12536 | 412,537
25 | 5 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 12538 | 412,539
25 | 5 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 12540 | 412,541
25 | 5 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 12542 | 412,543
25 | 6 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12560 | 412,561
25 | 6 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12562 | 412,563
25 | 6 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12564 | 412,565
25 | 6 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12566 | 412,567
25 | 6 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 12568 | 412,569
25 | 6 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12570 | 412,571
25 | 6 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12572 | 412,573
25 | 6 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12574 | 412,575
25 | 6 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12576 | 412,577
25 | 6 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12578 | 412,579
25 | 6 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12580 | 412,581
25 | 6 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12582 | 412,583
25 | 6 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12584 | 412,585
25 | 6 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12586 | 412,587
25 | 6 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12588 | 412,589
25 | 6 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 12590 | 412,591
25 | 6 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 12592 | 412,593
25 | 6 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 12594 | 412,595
25 | 6 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 12596 | 412,597
25 | 6 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 12598 | 412,599
25 | 6 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 12600 | 412,601
25 | 6 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 12602 | 412,603
25 | 6 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12604 | 412,605
25 | 6 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12606 | 412,607
25 | 6 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12608 | 412,609
25 | 6 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12610 | 412,611
25 | 6 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12612 | 412,613
25 | 6 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 12614 | 412,615
25 | 6 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 12616 | 412,617
25 | 6 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 12618 | 412,619
25 | 6 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 12620 | 412,621
25 | 6 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 12622 | 412,623
25 | 7 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12640 | 412,641
25 | 7 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12642 | 412,643
25 | 7 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12644 | 412,645
25 | 7 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12646 | 412,647
25 | 7 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 12648 | 412,649
25 | 7 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12650 | 412,651
25 | 7 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12652 | 412,653
25 | 7 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12654 | 412,655
25 | 7 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12656 | 412,657
25 | 7 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12658 | 412,659
25 | 7 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12660 | 412,661
25 | 7 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12662 | 412,663
25 | 7 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12664 | 412,665
25 | 7 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12666 | 412,667
25 | 7 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12668 | 412,669
25 | 7 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 12670 | 412,671
25 | 7 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 12672 | 412,673
25 | 7 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 12674 | 412,675
25 | 7 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 12676 | 412,677
25 | 7 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 12678 | 412,679
25 | 7 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 12680 | 412,681
25 | 7 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 12682 | 412,683
25 | 7 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12684 | 412,685
25 | 7 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12686 | 412,687
25 | 7 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12688 | 412,689
25 | 7 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12690 | 412,691
25 | 7 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12692 | 412,693
25 | 7 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 12694 | 412,695
25 | 7 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 12696 | 412,697
25 | 7 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 12698 | 412,699
25 | 7 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 12700 | 412,701
25 | 7 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 12702 | 412,703
25 | 8 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12720 | 412,721
25 | 8 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12722 | 412,723
25 | 8 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12724 | 412,725
25 | 8 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12726 | 412,727
25 | 8 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 12728 | 412,729
25 | 8 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12730 | 412,731
25 | 8 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12732 | 412,733
25 | 8 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12734 | 412,735
25 | 8 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12736 | 412,737
25 | 8 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12738 | 412,739
25 | 8 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12740 | 412,741
25 | 8 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12742 | 412,743
25 | 8 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12744 | 412,745
25 | 8 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12746 | 412,747
25 | 8 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12748 | 412,749
25 | 8 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 12750 | 412,751
25 | 8 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 12752 | 412,753
25 | 8 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 12754 | 412,755
25 | 8 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 12756 | 412,757
25 | 8 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 12758 | 412,759
25 | 8 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 12760 | 412,761
25 | 8 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 12762 | 412,763
25 | 8 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12764 | 412,765
25 | 8 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12766 | 412,767
25 | 8 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12768 | 412,769
25 | 8 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12770 | 412,771
25 | 8 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12772 | 412,773
25 | 8 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 12774 | 412,775
25 | 8 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 12776 | 412,777
25 | 8 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 12778 | 412,779
25 | 8 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 12780 | 412,781
25 | 8 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 12782 | 412,783
25 | 9 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12800 | 412,801
25 | 9 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12802 | 412,803
25 | 9 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12804 | 412,805
25 | 9 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12806 | 412,807
25 | 9 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 12808 | 412,809
25 | 9 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12810 | 412,811
25 | 9 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12812 | 412,813
25 | 9 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12814 | 412,815
25 | 9 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12816 | 412,817
25 | 9 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12818 | 412,819
25 | 9 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12820 | 412,821
25 | 9 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12822 | 412,823
25 | 9 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12824 | 412,825
25 | 9 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12826 | 412,827
25 | 9 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12828 | 412,829
25 | 9 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 12830 | 412,831
25 | 9 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 12832 | 412,833
25 | 9 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 12834 | 412,835
25 | 9 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 12836 | 412,837
25 | 9 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 12838 | 412,839
25 | 9 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 12840 | 412,841
25 | 9 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 12842 | 412,843
25 | 9 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12844 | 412,845
25 | 9 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12846 | 412,847
25 | 9 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12848 | 412,849
25 | 9 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12850 | 412,851
25 | 9 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12852 | 412,853
25 | 9 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 12854 | 412,855
25 | 9 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 12856 | 412,857
25 | 9 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 12858 | 412,859
25 | 9 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 12860 | 412,861
25 | 9 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 12862 | 412,863
25 | 10 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12880 | 412,881
25 | 10 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12882 | 412,883
25 | 10 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12884 | 412,885
25 | 10 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12886 | 412,887
25 | 10 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 12888 | 412,889
25 | 10 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12890 | 412,891
25 | 10 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12892 | 412,893
25 | 10 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12894 | 412,895
25 | 10 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12896 | 412,897
25 | 10 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12898 | 412,899
25 | 10 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12900 | 412,901
25 | 10 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12902 | 412,903
25 | 10 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12904 | 412,905
25 | 10 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12906 | 412,907
25 | 10 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12908 | 412,909
25 | 10 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 12910 | 412,911
25 | 10 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 12912 | 412,913
25 | 10 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 12914 | 412,915
25 | 10 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 12916 | 412,917
25 | 10 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 12918 | 412,919
25 | 10 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 12920 | 412,921
25 | 10 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 12922 | 412,923
25 | 10 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12924 | 412,925
25 | 10 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12926 | 412,927
25 | 10 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12928 | 412,929
25 | 10 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12930 | 412,931
25 | 10 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12932 | 412,933
25 | 10 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 12934 | 412,935
25 | 10 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 12936 | 412,937
25 | 10 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 12938 | 412,939
25 | 10 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 12940 | 412,941
25 | 10 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 12942 | 412,943
25 | 11 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12960 | 412,961
25 | 11 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12962 | 412,963
25 | 11 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12964 | 412,965
25 | 11 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12966 | 412,967
25 | 11 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 12968 | 412,969
25 | 11 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12970 | 412,971
25 | 11 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12972 | 412,973
25 | 11 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12974 | 412,975
25 | 11 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12976 | 412,977
25 | 11 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12978 | 412,979
25 | 11 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12980 | 412,981
25 | 11 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12982 | 412,983
25 | 11 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12984 | 412,985
25 | 11 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12986 | 412,987
25 | 11 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12988 | 412,989
25 | 11 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 12990 | 412,991
25 | 11 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 12992 | 412,993
25 | 11 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 12994 | 412,995
25 | 11 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 12996 | 412,997
25 | 11 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 12998 | 412,999
25 | 11 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 13000 | 413,001
25 | 11 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 13002 | 413,003
25 | 11 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13004 | 413,005
25 | 11 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13006 | 413,007
25 | 11 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13008 | 413,009
25 | 11 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13010 | 413,011
25 | 11 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13012 | 413,013
25 | 11 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 13014 | 413,015
25 | 11 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 13016 | 413,017
25 | 11 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 13018 | 413,019
25 | 11 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 13020 | 413,021
25 | 11 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 13022 | 413,023
25 | 12 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13040 | 413,041
25 | 12 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13042 | 413,043
25 | 12 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13044 | 413,045
25 | 12 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13046 | 413,047
25 | 12 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 13048 | 413,049
25 | 12 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13050 | 413,051
25 | 12 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13052 | 413,053
25 | 12 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13054 | 413,055
25 | 12 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13056 | 413,057
25 | 12 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13058 | 413,059
25 | 12 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13060 | 413,061
25 | 12 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13062 | 413,063
25 | 12 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13064 | 413,065
25 | 12 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13066 | 413,067
25 | 12 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13068 | 413,069
25 | 12 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 13070 | 413,071
25 | 12 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 13072 | 413,073
25 | 12 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 13074 | 413,075
25 | 12 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 13076 | 413,077
25 | 12 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 13078 | 413,079
25 | 12 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 13080 | 413,081
25 | 12 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 13082 | 413,083
25 | 12 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13084 | 413,085
25 | 12 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13086 | 413,087
25 | 12 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13088 | 413,089
25 | 12 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13090 | 413,091
25 | 12 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13092 | 413,093
25 | 12 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 13094 | 413,095
25 | 12 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 13096 | 413,097
25 | 12 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 13098 | 413,099
25 | 12 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 13100 | 413,101
25 | 12 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 13102 | 413,103
25 | 13 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13120 | 413,121
25 | 13 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13122 | 413,123
25 | 13 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13124 | 413,125
25 | 13 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13126 | 413,127
25 | 13 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 13128 | 413,129
25 | 13 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13130 | 413,131
25 | 13 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13132 | 413,133
25 | 13 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13134 | 413,135
25 | 13 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13136 | 413,137
25 | 13 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13138 | 413,139
25 | 13 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13140 | 413,141
25 | 13 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13142 | 413,143
25 | 13 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13144 | 413,145
25 | 13 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13146 | 413,147
25 | 13 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13148 | 413,149
25 | 13 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 13150 | 413,151
25 | 13 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 13152 | 413,153
25 | 13 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 13154 | 413,155
25 | 13 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 13156 | 413,157
25 | 13 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 13158 | 413,159
25 | 13 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 13160 | 413,161
25 | 13 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 13162 | 413,163
25 | 13 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13164 | 413,165
25 | 13 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13166 | 413,167
25 | 13 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13168 | 413,169
25 | 13 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13170 | 413,171
25 | 13 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13172 | 413,173
25 | 13 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 13174 | 413,175
25 | 13 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 13176 | 413,177
25 | 13 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 13178 | 413,179
25 | 13 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 13180 | 413,181
25 | 13 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 13182 | 413,183
25 | 14 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13200 | 413,201
25 | 14 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13202 | 413,203
25 | 14 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13204 | 413,205
25 | 14 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13206 | 413,207
25 | 14 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 13208 | 413,209
25 | 14 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13210 | 413,211
25 | 14 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13212 | 413,213
25 | 14 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13214 | 413,215
25 | 14 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13216 | 413,217
25 | 14 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13218 | 413,219
25 | 14 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13220 | 413,221
25 | 14 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13222 | 413,223
25 | 14 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13224 | 413,225
25 | 14 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13226 | 413,227
25 | 14 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13228 | 413,229
25 | 14 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 13230 | 413,231
25 | 14 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 13232 | 413,233
25 | 14 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 13234 | 413,235
25 | 14 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 13236 | 413,237
25 | 14 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 13238 | 413,239
25 | 14 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 13240 | 413,241
25 | 14 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 13242 | 413,243
25 | 14 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13244 | 413,245
25 | 14 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13246 | 413,247
25 | 14 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13248 | 413,249
25 | 14 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13250 | 413,251
25 | 14 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13252 | 413,253
25 | 14 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 13254 | 413,255
25 | 14 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 13256 | 413,257
25 | 14 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 13258 | 413,259
25 | 14 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 13260 | 413,261
25 | 14 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 13262 | 413,263
25 | 15 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13280 | 413,281
25 | 15 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13282 | 413,283
25 | 15 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13284 | 413,285
25 | 15 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13286 | 413,287
25 | 15 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 13288 | 413,289
25 | 15 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13290 | 413,291
25 | 15 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13292 | 413,293
25 | 15 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13294 | 413,295
25 | 15 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13296 | 413,297
25 | 15 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13298 | 413,299
25 | 15 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13300 | 413,301
25 | 15 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13302 | 413,303
25 | 15 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13304 | 413,305
25 | 15 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13306 | 413,307
25 | 15 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13308 | 413,309
25 | 15 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 13310 | 413,311
25 | 15 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 13312 | 413,313
25 | 15 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 13314 | 413,315
25 | 15 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 13316 | 413,317
25 | 15 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 13318 | 413,319
25 | 15 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 13320 | 413,321
25 | 15 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 13322 | 413,323
25 | 15 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13324 | 413,325
25 | 15 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13326 | 413,327
25 | 15 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13328 | 413,329
25 | 15 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13330 | 413,331
25 | 15 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13332 | 413,333
25 | 15 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 13334 | 413,335
25 | 15 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 13336 | 413,337
25 | 15 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 13338 | 413,339
25 | 15 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 13340 | 413,341
25 | 15 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 13342 | 413,343
25 | 16 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13360 | 413,361
25 | 16 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13362 | 413,363
25 | 16 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13364 | 413,365
25 | 16 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13366 | 413,367
25 | 16 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 13368 | 413,369
25 | 16 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13370 | 413,371
25 | 16 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13372 | 413,373
25 | 16 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13374 | 413,375
25 | 16 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13376 | 413,377
25 | 16 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13378 | 413,379
25 | 16 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13380 | 413,381
25 | 16 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13382 | 413,383
25 | 16 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13384 | 413,385
25 | 16 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13386 | 413,387
25 | 16 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13388 | 413,389
25 | 16 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 13390 | 413,391
25 | 16 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 13392 | 413,393
25 | 16 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 13394 | 413,395
25 | 16 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 13396 | 413,397
25 | 16 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 13398 | 413,399
25 | 16 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 13400 | 413,401
25 | 16 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 13402 | 413,403
25 | 16 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13404 | 413,405
25 | 16 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13406 | 413,407
25 | 16 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13408 | 413,409
25 | 16 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13410 | 413,411
25 | 16 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13412 | 413,413
25 | 16 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 13414 | 413,415
25 | 16 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 13416 | 413,417
25 | 16 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 13418 | 413,419
25 | 16 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 13420 | 413,421
25 | 16 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 13422 | 413,423
25 | 17 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13440 | 413,441
25 | 17 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13442 | 413,443
25 | 17 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13444 | 413,445
25 | 17 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13446 | 413,447
25 | 17 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 13448 | 413,449
25 | 17 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13450 | 413,451
25 | 17 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13452 | 413,453
25 | 17 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13454 | 413,455
25 | 17 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13456 | 413,457
25 | 17 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13458 | 413,459
25 | 17 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13460 | 413,461
25 | 17 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13462 | 413,463
25 | 17 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13464 | 413,465
25 | 17 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13466 | 413,467
25 | 17 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13468 | 413,469
25 | 17 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 13470 | 413,471
25 | 17 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 13472 | 413,473
25 | 17 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 13474 | 413,475
25 | 17 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 13476 | 413,477
25 | 17 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 13478 | 413,479
25 | 17 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 13480 | 413,481
25 | 17 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 13482 | 413,483
25 | 17 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13484 | 413,485
25 | 17 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13486 | 413,487
25 | 17 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13488 | 413,489
25 | 17 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13490 | 413,491
25 | 17 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13492 | 413,493
25 | 17 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 13494 | 413,495
25 | 17 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 13496 | 413,497
25 | 17 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 13498 | 413,499
25 | 17 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 13500 | 413,501
25 | 17 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 13502 | 413,503
25 | 18 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13520 | 413,521
25 | 18 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13522 | 413,523
25 | 18 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13524 | 413,525
25 | 18 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13526 | 413,527
25 | 18 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 13528 | 413,529
25 | 18 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13530 | 413,531
25 | 18 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13532 | 413,533
25 | 18 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13534 | 413,535
25 | 18 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13536 | 413,537
25 | 18 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13538 | 413,539
25 | 18 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13540 | 413,541
25 | 18 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13542 | 413,543
25 | 18 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13544 | 413,545
25 | 18 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13546 | 413,547
25 | 18 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13548 | 413,549
25 | 18 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 13550 | 413,551
25 | 18 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 13552 | 413,553
25 | 18 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 13554 | 413,555
25 | 18 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 13556 | 413,557
25 | 18 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 13558 | 413,559
25 | 18 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 13560 | 413,561
25 | 18 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 13562 | 413,563
25 | 18 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13564 | 413,565
25 | 18 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13566 | 413,567
25 | 18 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13568 | 413,569
25 | 18 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13570 | 413,571
25 | 18 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13572 | 413,573
25 | 18 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 13574 | 413,575
25 | 18 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 13576 | 413,577
25 | 18 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 13578 | 413,579
25 | 18 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 13580 | 413,581
25 | 18 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 13582 | 413,583
25 | 19 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13600 | 413,601
25 | 19 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13602 | 413,603
25 | 19 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13604 | 413,605
25 | 19 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13606 | 413,607
25 | 19 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 13608 | 413,609
25 | 19 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13610 | 413,611
25 | 19 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13612 | 413,613
25 | 19 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13614 | 413,615
25 | 19 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13616 | 413,617
25 | 19 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13618 | 413,619
25 | 19 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13620 | 413,621
25 | 19 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13622 | 413,623
25 | 19 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13624 | 413,625
25 | 19 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13626 | 413,627
25 | 19 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13628 | 413,629
25 | 19 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 13630 | 413,631
25 | 19 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 13632 | 413,633
25 | 19 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 13634 | 413,635
25 | 19 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 13636 | 413,637
25 | 19 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 13638 | 413,639
25 | 19 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 13640 | 413,641
25 | 19 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 13642 | 413,643
25 | 19 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13644 | 413,645
25 | 19 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13646 | 413,647
25 | 19 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13648 | 413,649
25 | 19 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13650 | 413,651
25 | 19 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13652 | 413,653
25 | 19 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 13654 | 413,655
25 | 19 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 13656 | 413,657
25 | 19 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 13658 | 413,659
25 | 19 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 13660 | 413,661
25 | 19 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 13662 | 413,663
25 | 20 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13680 | 413,681
25 | 20 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13682 | 413,683
25 | 20 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13684 | 413,685
25 | 20 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13686 | 413,687
25 | 20 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 13688 | 413,689
25 | 20 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13690 | 413,691
25 | 20 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13692 | 413,693
25 | 20 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13694 | 413,695
25 | 20 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13696 | 413,697
25 | 20 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13698 | 413,699
25 | 20 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13700 | 413,701
25 | 20 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13702 | 413,703
25 | 20 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13704 | 413,705
25 | 20 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13706 | 413,707
25 | 20 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13708 | 413,709
25 | 20 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 13710 | 413,711
25 | 20 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 13712 | 413,713
25 | 20 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 13714 | 413,715
25 | 20 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 13716 | 413,717
25 | 20 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 13718 | 413,719
25 | 20 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 13720 | 413,721
25 | 20 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 13722 | 413,723
25 | 20 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13724 | 413,725
25 | 20 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13726 | 413,727
25 | 20 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13728 | 413,729
25 | 20 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13730 | 413,731
25 | 20 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13732 | 413,733
25 | 20 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 13734 | 413,735
25 | 20 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 13736 | 413,737
25 | 20 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 13738 | 413,739
25 | 20 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 13740 | 413,741
25 | 20 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 13742 | 413,743
25 | 21 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13760 | 413,761
25 | 21 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13762 | 413,763
25 | 21 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13764 | 413,765
25 | 21 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13766 | 413,767
25 | 21 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 13768 | 413,769
25 | 21 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13770 | 413,771
25 | 21 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13772 | 413,773
25 | 21 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13774 | 413,775
25 | 21 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13776 | 413,777
25 | 21 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13778 | 413,779
25 | 21 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13780 | 413,781
25 | 21 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13782 | 413,783
25 | 21 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13784 | 413,785
25 | 21 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13786 | 413,787
25 | 21 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13788 | 413,789
25 | 21 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 13790 | 413,791
25 | 21 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 13792 | 413,793
25 | 21 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 13794 | 413,795
25 | 21 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 13796 | 413,797
25 | 21 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 13798 | 413,799
25 | 21 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 13800 | 413,801
25 | 21 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 13802 | 413,803
25 | 21 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13804 | 413,805
25 | 21 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13806 | 413,807
25 | 21 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13808 | 413,809
25 | 21 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13810 | 413,811
25 | 21 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13812 | 413,813
25 | 21 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 13814 | 413,815
25 | 21 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 13816 | 413,817
25 | 21 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 13818 | 413,819
25 | 21 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 13820 | 413,821
25 | 21 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 13822 | 413,823
25 | 22 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13840 | 413,841
25 | 22 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13842 | 413,843
25 | 22 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13844 | 413,845
25 | 22 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13846 | 413,847
25 | 22 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 13848 | 413,849
25 | 22 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13850 | 413,851
25 | 22 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13852 | 413,853
25 | 22 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13854 | 413,855
25 | 22 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13856 | 413,857
25 | 22 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13858 | 413,859
25 | 22 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13860 | 413,861
25 | 22 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13862 | 413,863
25 | 22 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13864 | 413,865
25 | 22 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13866 | 413,867
25 | 22 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13868 | 413,869
25 | 22 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 13870 | 413,871
25 | 22 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 13872 | 413,873
25 | 22 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 13874 | 413,875
25 | 22 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 13876 | 413,877
25 | 22 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 13878 | 413,879
25 | 22 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 13880 | 413,881
25 | 22 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 13882 | 413,883
25 | 22 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13884 | 413,885
25 | 22 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13886 | 413,887
25 | 22 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13888 | 413,889
25 | 22 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13890 | 413,891
25 | 22 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13892 | 413,893
25 | 22 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 13894 | 413,895
25 | 22 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 13896 | 413,897
25 | 22 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 13898 | 413,899
25 | 22 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 13900 | 413,901
25 | 22 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 13902 | 413,903
25 | 23 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13920 | 413,921
25 | 23 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13922 | 413,923
25 | 23 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13924 | 413,925
25 | 23 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 13926 | 413,927
25 | 23 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 13928 | 413,929
25 | 23 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13930 | 413,931
25 | 23 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13932 | 413,933
25 | 23 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13934 | 413,935
25 | 23 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13936 | 413,937
25 | 23 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 13938 | 413,939
25 | 23 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13940 | 413,941
25 | 23 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13942 | 413,943
25 | 23 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13944 | 413,945
25 | 23 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13946 | 413,947
25 | 23 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 13948 | 413,949
25 | 23 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 13950 | 413,951
25 | 23 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 13952 | 413,953
25 | 23 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 13954 | 413,955
25 | 23 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 13956 | 413,957
25 | 23 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 13958 | 413,959
25 | 23 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 13960 | 413,961
25 | 23 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 13962 | 413,963
25 | 23 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13964 | 413,965
25 | 23 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13966 | 413,967
25 | 23 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13968 | 413,969
25 | 23 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 13970 | 413,971
25 | 23 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 13972 | 413,973
25 | 23 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 13974 | 413,975
25 | 23 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 13976 | 413,977
25 | 23 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 13978 | 413,979
25 | 23 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 13980 | 413,981
25 | 23 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 13982 | 413,983
25 | 24 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14000 | 414,001
25 | 24 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14002 | 414,003
25 | 24 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14004 | 414,005
25 | 24 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 14006 | 414,007
25 | 24 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14008 | 414,009
25 | 24 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14010 | 414,011
25 | 24 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14012 | 414,013
25 | 24 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14014 | 414,015
25 | 24 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14016 | 414,017
25 | 24 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14018 | 414,019
25 | 24 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14020 | 414,021
25 | 24 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14022 | 414,023
25 | 24 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14024 | 414,025
25 | 24 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14026 | 414,027
25 | 24 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14028 | 414,029
25 | 24 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 14030 | 414,031
25 | 24 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 14032 | 414,033
25 | 24 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 14034 | 414,035
25 | 24 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 14036 | 414,037
25 | 24 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | Enumeration | R | 14038 | 414,039
25 | 24 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | Enumeration | R/W | 14040 | 414,041
25 | 24 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | IEEE Float | R | 14042 | 414,043
25 | 24 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14044 | 414,045
25 | 24 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14046 | 414,047
25 | 24 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 14048 | 414,049
25 | 24 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14050 | 414,051
25 | 24 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 14052 | 414,053
25 | 24 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 14054 | 414,055
25 | 24 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14056 | 414,057
25 | 24 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 14058 | 414,059
25 | 24 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 14060 | 414,061
25 | 24 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 14062 | 414,063
26 | 1 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14100 | 414,101
26 | 1 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14102 | 414,103
26 | 1 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14104 | 414,105
26 | 1 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14106 | 414,107
26 | 1 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14108 | 414,109
26 | 1 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14110 | 414,111
26 | 1 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14112 | 414,113
26 | 1 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14114 | 414,115
26 | 1 | 9 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14116 | 414,117
26 | 1 | 10 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14118 | 414,119
26 | 1 | 11 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14120 | 414,121
26 | 1 | 12 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14122 | 414,123
26 | 1 | 13 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14124 | 414,125
26 | 1 | 14 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14126 | 414,127
26 | 1 | 15 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14128 | 414,129
26 | 1 | 16 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 14130 | 414,131
26 | 1 | 17 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 14132 | 414,133
26 | 1 | 18 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 14134 | 414,135
26 | 1 | 19 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 14136 | 414,137
26 | 1 | 20 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 14138 | 414,139
26 | 1 | 21 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | Enumeration | R/W | 14140 | 414,141
26 | 1 | 22 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | IEEE Float | R | 14142 | 414,143
26 | 1 | 23 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14144 | 414,145
26 | 1 | 24 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 14146 | 414,147
26 | 1 | 25 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 14148 | 414,149
26 | 1 | 26 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 14150 | 414,151
26 | 1 | 27 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14152 | 414,153
26 | 1 | 28 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 14154 | 414,155
26 | 1 | 29 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 14156 | 414,157
26 | 1 | 30 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | IEEE Float | R/W | 14158 | 414,159
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49180 | 449,181
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49181 | 449,182
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49182 | 449,183
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49183 | 449,184
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49184 | 449,185
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49185 | 449,186
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49186 | 449,187
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49187 | 449,188
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49188 | 449,189
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49189 | 449,190
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49190 | 449,191
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49191 | 449,192
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49192 | 449,193
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49193 | 449,194
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49194 | 449,195
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49195 | 449,196
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49196 | 449,197
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49197 | 449,198
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49198 | 449,199
26 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49199 | 449,200
26 | 2 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14170 | 414,171
26 | 2 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14172 | 414,173
26 | 2 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14174 | 414,175
26 | 2 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14176 | 414,177
26 | 2 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14178 | 414,179
26 | 2 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14180 | 414,181
26 | 2 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14182 | 414,183
26 | 2 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14184 | 414,185
26 | 2 | 9 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14186 | 414,187
26 | 2 | 10 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14188 | 414,189
26 | 2 | 11 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14190 | 414,191
26 | 2 | 12 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14192 | 414,193
26 | 2 | 13 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14194 | 414,195
26 | 2 | 14 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14196 | 414,197
26 | 2 | 15 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14198 | 414,199
26 | 2 | 16 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 14200 | 414,201
26 | 2 | 17 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 14202 | 414,203
26 | 2 | 18 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 14204 | 414,205
26 | 2 | 19 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 14206 | 414,207
26 | 2 | 20 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 14208 | 414,209
26 | 2 | 21 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | Enumeration | R/W | 14210 | 414,211
26 | 2 | 22 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | IEEE Float | R | 14212 | 414,213
26 | 2 | 23 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14214 | 414,215
26 | 2 | 24 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 14216 | 414,217
26 | 2 | 25 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 14218 | 414,219
26 | 2 | 26 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 14220 | 414,221
26 | 2 | 27 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14222 | 414,223
26 | 2 | 28 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 14224 | 414,225
26 | 2 | 29 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 14226 | 414,227
26 | 2 | 30 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | IEEE Float | R/W | 14228 | 414,229
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49200 | 449,201
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49201 | 449,202
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49202 | 449,203
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49203 | 449,204
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49204 | 449,205
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49205 | 449,206
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49206 | 449,207
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49207 | 449,208
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49208 | 449,209
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49209 | 449,210
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49210 | 449,211
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49211 | 449,212
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49212 | 449,213
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49213 | 449,214
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49214 | 449,215
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49215 | 449,216
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49216 | 449,217
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49217 | 449,218
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49218 | 449,219
26 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49219 | 449,220
26 | 3 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14240 | 414,241
26 | 3 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14242 | 414,243
26 | 3 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14244 | 414,245
26 | 3 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14246 | 414,247
26 | 3 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14248 | 414,249
26 | 3 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14250 | 414,251
26 | 3 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14252 | 414,253
26 | 3 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14254 | 414,255
26 | 3 | 9 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14256 | 414,257
26 | 3 | 10 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14258 | 414,259
26 | 3 | 11 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14260 | 414,261
26 | 3 | 12 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14262 | 414,263
26 | 3 | 13 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14264 | 414,265
26 | 3 | 14 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14266 | 414,267
26 | 3 | 15 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14268 | 414,269
26 | 3 | 16 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 14270 | 414,271
26 | 3 | 17 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 14272 | 414,273
26 | 3 | 18 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 14274 | 414,275
26 | 3 | 19 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 14276 | 414,277
26 | 3 | 20 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 14278 | 414,279
26 | 3 | 21 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | Enumeration | R/W | 14280 | 414,281
26 | 3 | 22 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | IEEE Float | R | 14282 | 414,283
26 | 3 | 23 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14284 | 414,285
26 | 3 | 24 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 14286 | 414,287
26 | 3 | 25 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 14288 | 414,289
26 | 3 | 26 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 14290 | 414,291
26 | 3 | 27 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14292 | 414,293
26 | 3 | 28 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 14294 | 414,295
26 | 3 | 29 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 14296 | 414,297
26 | 3 | 30 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | IEEE Float | R/W | 14298 | 414,299
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49220 | 449,221
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49221 | 449,222
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49222 | 449,223
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49223 | 449,224
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49224 | 449,225
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49225 | 449,226
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49226 | 449,227
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49227 | 449,228
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49228 | 449,229
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49229 | 449,230
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49230 | 449,231
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49231 | 449,232
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49232 | 449,233
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49233 | 449,234
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49234 | 449,235
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49235 | 449,236
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49236 | 449,237
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49237 | 449,238
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49238 | 449,239
26 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49239 | 449,240
26 | 4 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14310 | 414,311
26 | 4 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14312 | 414,313
26 | 4 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14314 | 414,315
26 | 4 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14316 | 414,317
26 | 4 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14318 | 414,319
26 | 4 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14320 | 414,321
26 | 4 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14322 | 414,323
26 | 4 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14324 | 414,325
26 | 4 | 9 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14326 | 414,327
26 | 4 | 10 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14328 | 414,329
26 | 4 | 11 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14330 | 414,331
26 | 4 | 12 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14332 | 414,333
26 | 4 | 13 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14334 | 414,335
26 | 4 | 14 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14336 | 414,337
26 | 4 | 15 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14338 | 414,339
26 | 4 | 16 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 14340 | 414,341
26 | 4 | 17 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 14342 | 414,343
26 | 4 | 18 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 14344 | 414,345
26 | 4 | 19 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 14346 | 414,347
26 | 4 | 20 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 14348 | 414,349
26 | 4 | 21 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | Enumeration | R/W | 14350 | 414,351
26 | 4 | 22 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | IEEE Float | R | 14352 | 414,353
26 | 4 | 23 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14354 | 414,355
26 | 4 | 24 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 14356 | 414,357
26 | 4 | 25 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 14358 | 414,359
26 | 4 | 26 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 14360 | 414,361
26 | 4 | 27 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14362 | 414,363
26 | 4 | 28 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 14364 | 414,365
26 | 4 | 29 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 14366 | 414,367
26 | 4 | 30 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | IEEE Float | R/W | 14368 | 414,369
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49240 | 449,241
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49241 | 449,242
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49242 | 449,243
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49243 | 449,244
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49244 | 449,245
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49245 | 449,246
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49246 | 449,247
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49247 | 449,248
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49248 | 449,249
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49249 | 449,250
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49250 | 449,251
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49251 | 449,252
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49252 | 449,253
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49253 | 449,254
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49254 | 449,255
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49255 | 449,256
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49256 | 449,257
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49257 | 449,258
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49258 | 449,259
26 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49259 | 449,260
26 | 5 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14380 | 414,381
26 | 5 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14382 | 414,383
26 | 5 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14384 | 414,385
26 | 5 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14386 | 414,387
26 | 5 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14388 | 414,389
26 | 5 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14390 | 414,391
26 | 5 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14392 | 414,393
26 | 5 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14394 | 414,395
26 | 5 | 9 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14396 | 414,397
26 | 5 | 10 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14398 | 414,399
26 | 5 | 11 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14400 | 414,401
26 | 5 | 12 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14402 | 414,403
26 | 5 | 13 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14404 | 414,405
26 | 5 | 14 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14406 | 414,407
26 | 5 | 15 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14408 | 414,409
26 | 5 | 16 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 14410 | 414,411
26 | 5 | 17 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 14412 | 414,413
26 | 5 | 18 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 14414 | 414,415
26 | 5 | 19 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 14416 | 414,417
26 | 5 | 20 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 14418 | 414,419
26 | 5 | 21 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | Enumeration | R/W | 14420 | 414,421
26 | 5 | 22 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | IEEE Float | R | 14422 | 414,423
26 | 5 | 23 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14424 | 414,425
26 | 5 | 24 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 14426 | 414,427
26 | 5 | 25 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 14428 | 414,429
26 | 5 | 26 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 14430 | 414,431
26 | 5 | 27 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14432 | 414,433
26 | 5 | 28 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 14434 | 414,435
26 | 5 | 29 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 14436 | 414,437
26 | 5 | 30 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | IEEE Float | R/W | 14438 | 414,439
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49260 | 449,261
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49261 | 449,262
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49262 | 449,263
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49263 | 449,264
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49264 | 449,265
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49265 | 449,266
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49266 | 449,267
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49267 | 449,268
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49268 | 449,269
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49269 | 449,270
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49270 | 449,271
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49271 | 449,272
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49272 | 449,273
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49273 | 449,274
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49274 | 449,275
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49275 | 449,276
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49276 | 449,277
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49277 | 449,278
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49278 | 449,279
26 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49279 | 449,280
26 | 6 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14450 | 414,451
26 | 6 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14452 | 414,453
26 | 6 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14454 | 414,455
26 | 6 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14456 | 414,457
26 | 6 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14458 | 414,459
26 | 6 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14460 | 414,461
26 | 6 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14462 | 414,463
26 | 6 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14464 | 414,465
26 | 6 | 9 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14466 | 414,467
26 | 6 | 10 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14468 | 414,469
26 | 6 | 11 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14470 | 414,471
26 | 6 | 12 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14472 | 414,473
26 | 6 | 13 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14474 | 414,475
26 | 6 | 14 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14476 | 414,477
26 | 6 | 15 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14478 | 414,479
26 | 6 | 16 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 14480 | 414,481
26 | 6 | 17 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 14482 | 414,483
26 | 6 | 18 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 14484 | 414,485
26 | 6 | 19 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 14486 | 414,487
26 | 6 | 20 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 14488 | 414,489
26 | 6 | 21 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | Enumeration | R/W | 14490 | 414,491
26 | 6 | 22 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | IEEE Float | R | 14492 | 414,493
26 | 6 | 23 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14494 | 414,495
26 | 6 | 24 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 14496 | 414,497
26 | 6 | 25 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 14498 | 414,499
26 | 6 | 26 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 14500 | 414,501
26 | 6 | 27 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14502 | 414,503
26 | 6 | 28 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 14504 | 414,505
26 | 6 | 29 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 14506 | 414,507
26 | 6 | 30 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | IEEE Float | R/W | 14508 | 414,509
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49280 | 449,281
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49281 | 449,282
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49282 | 449,283
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49283 | 449,284
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49284 | 449,285
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49285 | 449,286
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49286 | 449,287
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49287 | 449,288
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49288 | 449,289
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49289 | 449,290
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49290 | 449,291
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49291 | 449,292
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49292 | 449,293
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49293 | 449,294
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49294 | 449,295
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49295 | 449,296
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49296 | 449,297
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49297 | 449,298
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49298 | 449,299
26 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49299 | 449,300
26 | 7 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14520 | 414,521
26 | 7 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14522 | 414,523
26 | 7 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14524 | 414,525
26 | 7 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14526 | 414,527
26 | 7 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14528 | 414,529
26 | 7 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14530 | 414,531
26 | 7 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14532 | 414,533
26 | 7 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14534 | 414,535
26 | 7 | 9 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14536 | 414,537
26 | 7 | 10 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14538 | 414,539
26 | 7 | 11 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14540 | 414,541
26 | 7 | 12 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14542 | 414,543
26 | 7 | 13 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14544 | 414,545
26 | 7 | 14 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14546 | 414,547
26 | 7 | 15 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14548 | 414,549
26 | 7 | 16 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 14550 | 414,551
26 | 7 | 17 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 14552 | 414,553
26 | 7 | 18 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 14554 | 414,555
26 | 7 | 19 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 14556 | 414,557
26 | 7 | 20 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 14558 | 414,559
26 | 7 | 21 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | Enumeration | R/W | 14560 | 414,561
26 | 7 | 22 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | IEEE Float | R | 14562 | 414,563
26 | 7 | 23 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14564 | 414,565
26 | 7 | 24 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 14566 | 414,567
26 | 7 | 25 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 14568 | 414,569
26 | 7 | 26 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 14570 | 414,571
26 | 7 | 27 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14572 | 414,573
26 | 7 | 28 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 14574 | 414,575
26 | 7 | 29 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 14576 | 414,577
26 | 7 | 30 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | IEEE Float | R/W | 14578 | 414,579
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49300 | 449,301
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49301 | 449,302
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49302 | 449,303
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49303 | 449,304
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49304 | 449,305
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49305 | 449,306
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49306 | 449,307
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49307 | 449,308
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49308 | 449,309
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49309 | 449,310
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49310 | 449,311
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49311 | 449,312
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49312 | 449,313
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49313 | 449,314
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49314 | 449,315
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49315 | 449,316
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49316 | 449,317
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49317 | 449,318
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49318 | 449,319
26 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49319 | 449,320
26 | 8 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14590 | 414,591
26 | 8 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14592 | 414,593
26 | 8 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14594 | 414,595
26 | 8 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | Enumeration | R/W | 14596 | 414,597
26 | 8 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 14598 | 414,599
26 | 8 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14600 | 414,601
26 | 8 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14602 | 414,603
26 | 8 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14604 | 414,605
26 | 8 | 9 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14606 | 414,607
26 | 8 | 10 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14608 | 414,609
26 | 8 | 11 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14610 | 414,611
26 | 8 | 12 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14612 | 414,613
26 | 8 | 13 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14614 | 414,615
26 | 8 | 14 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14616 | 414,617
26 | 8 | 15 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14618 | 414,619
26 | 8 | 16 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 14620 | 414,621
26 | 8 | 17 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 14622 | 414,623
26 | 8 | 18 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | IEEE Float | R | 14624 | 414,625
26 | 8 | 19 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | IEEE Float | R | 14626 | 414,627
26 | 8 | 20 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 14628 | 414,629
26 | 8 | 21 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | Enumeration | R/W | 14630 | 414,631
26 | 8 | 22 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | IEEE Float | R | 14632 | 414,633
26 | 8 | 23 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14634 | 414,635
26 | 8 | 24 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | IEEE Float | R/W | 14636 | 414,637
26 | 8 | 25 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 14638 | 414,639
26 | 8 | 26 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | IEEE Float | R/W | 14640 | 414,641
26 | 8 | 27 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14642 | 414,643
26 | 8 | 28 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | Enumeration | R/W | 14644 | 414,645
26 | 8 | 29 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | Enumeration | R/W | 14646 | 414,647
26 | 8 | 30 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | IEEE Float | R/W | 14648 | 414,649
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49320 | 449,321
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49321 | 449,322
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49322 | 449,323
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49323 | 449,324
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49324 | 449,325
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49325 | 449,326
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49326 | 449,327
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49327 | 449,328
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49328 | 449,329
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49329 | 449,330
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49330 | 449,331
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49331 | 449,332
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49332 | 449,333
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49333 | 449,334
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49334 | 449,335
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49335 | 449,336
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49336 | 449,337
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49337 | 449,338
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49338 | 449,339
26 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49339 | 449,340
27 | 1 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6920 | 406,921
27 | 1 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6922 | 406,923
27 | 1 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6924 | 406,925
27 | 1 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6926 | 406,927
27 | 1 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6928 | 406,929
27 | 1 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6930 | 406,931
27 | 1 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6932 | 406,933
27 | 1 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6934 | 406,935
27 | 1 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6936 | 406,937
27 | 1 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6938 | 406,939
27 | 1 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6940 | 406,941
27 | 1 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6942 | 406,943
27 | 1 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6944 | 406,945
27 | 1 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6946 | 406,947
27 | 1 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6948 | 406,949
27 | 1 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6950 | 406,951
27 | 1 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6952 | 406,953
27 | 1 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6954 | 406,955
27 | 1 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6956 | 406,957
27 | 1 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6958 | 406,959
27 | 1 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6960 | 406,961
27 | 1 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6962 | 406,963
27 | 1 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6964 | 406,965
27 | 1 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6966 | 406,967
27 | 1 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6968 | 406,969
27 | 1 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6970 | 406,971
27 | 1 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6972 | 406,973
27 | 1 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6974 | 406,975
27 | 1 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6976 | 406,977
27 | 1 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6978 | 406,979
27 | 1 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6980 | 406,981
27 | 1 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6982 | 406,983
27 | 1 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 6984 | 406,985
27 | 1 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 6986 | 406,987
27 | 1 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 6988 | 406,989
27 | 1 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 6990 | 406,991
27 | 2 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7010 | 407,011
27 | 2 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7012 | 407,013
27 | 2 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7014 | 407,015
27 | 2 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7016 | 407,017
27 | 2 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7018 | 407,019
27 | 2 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7020 | 407,021
27 | 2 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7022 | 407,023
27 | 2 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7024 | 407,025
27 | 2 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7026 | 407,027
27 | 2 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7028 | 407,029
27 | 2 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7030 | 407,031
27 | 2 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7032 | 407,033
27 | 2 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7034 | 407,035
27 | 2 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7036 | 407,037
27 | 2 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7038 | 407,039
27 | 2 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7040 | 407,041
27 | 2 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7042 | 407,043
27 | 2 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7044 | 407,045
27 | 2 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7046 | 407,047
27 | 2 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7048 | 407,049
27 | 2 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7050 | 407,051
27 | 2 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7052 | 407,053
27 | 2 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7054 | 407,055
27 | 2 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7056 | 407,057
27 | 2 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7058 | 407,059
27 | 2 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7060 | 407,061
27 | 2 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7062 | 407,063
27 | 2 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7064 | 407,065
27 | 2 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7066 | 407,067
27 | 2 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7068 | 407,069
27 | 2 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7070 | 407,071
27 | 2 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7072 | 407,073
27 | 2 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 7074 | 407,075
27 | 2 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 7076 | 407,077
27 | 2 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 7078 | 407,079
27 | 2 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 7080 | 407,081
27 | 3 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7100 | 407,101
27 | 3 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7102 | 407,103
27 | 3 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7104 | 407,105
27 | 3 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7106 | 407,107
27 | 3 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7108 | 407,109
27 | 3 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7110 | 407,111
27 | 3 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7112 | 407,113
27 | 3 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7114 | 407,115
27 | 3 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7116 | 407,117
27 | 3 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7118 | 407,119
27 | 3 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7120 | 407,121
27 | 3 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7122 | 407,123
27 | 3 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7124 | 407,125
27 | 3 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7126 | 407,127
27 | 3 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7128 | 407,129
27 | 3 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7130 | 407,131
27 | 3 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7132 | 407,133
27 | 3 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7134 | 407,135
27 | 3 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7136 | 407,137
27 | 3 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7138 | 407,139
27 | 3 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7140 | 407,141
27 | 3 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7142 | 407,143
27 | 3 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7144 | 407,145
27 | 3 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7146 | 407,147
27 | 3 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7148 | 407,149
27 | 3 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7150 | 407,151
27 | 3 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7152 | 407,153
27 | 3 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7154 | 407,155
27 | 3 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7156 | 407,157
27 | 3 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7158 | 407,159
27 | 3 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7160 | 407,161
27 | 3 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7162 | 407,163
27 | 3 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 7164 | 407,165
27 | 3 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 7166 | 407,167
27 | 3 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 7168 | 407,169
27 | 3 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 7170 | 407,171
27 | 4 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7190 | 407,191
27 | 4 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7192 | 407,193
27 | 4 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7194 | 407,195
27 | 4 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7196 | 407,197
27 | 4 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7198 | 407,199
27 | 4 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7200 | 407,201
27 | 4 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7202 | 407,203
27 | 4 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7204 | 407,205
27 | 4 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7206 | 407,207
27 | 4 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7208 | 407,209
27 | 4 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7210 | 407,211
27 | 4 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7212 | 407,213
27 | 4 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7214 | 407,215
27 | 4 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7216 | 407,217
27 | 4 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7218 | 407,219
27 | 4 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7220 | 407,221
27 | 4 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7222 | 407,223
27 | 4 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7224 | 407,225
27 | 4 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7226 | 407,227
27 | 4 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7228 | 407,229
27 | 4 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7230 | 407,231
27 | 4 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7232 | 407,233
27 | 4 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7234 | 407,235
27 | 4 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7236 | 407,237
27 | 4 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7238 | 407,239
27 | 4 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7240 | 407,241
27 | 4 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7242 | 407,243
27 | 4 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7244 | 407,245
27 | 4 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7246 | 407,247
27 | 4 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7248 | 407,249
27 | 4 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7250 | 407,251
27 | 4 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7252 | 407,253
27 | 4 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 7254 | 407,255
27 | 4 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 7256 | 407,257
27 | 4 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 7258 | 407,259
27 | 4 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 7260 | 407,261
27 | 5 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7280 | 407,281
27 | 5 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7282 | 407,283
27 | 5 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7284 | 407,285
27 | 5 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7286 | 407,287
27 | 5 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7288 | 407,289
27 | 5 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7290 | 407,291
27 | 5 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7292 | 407,293
27 | 5 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7294 | 407,295
27 | 5 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7296 | 407,297
27 | 5 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7298 | 407,299
27 | 5 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7300 | 407,301
27 | 5 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7302 | 407,303
27 | 5 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7304 | 407,305
27 | 5 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7306 | 407,307
27 | 5 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7308 | 407,309
27 | 5 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7310 | 407,311
27 | 5 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7312 | 407,313
27 | 5 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7314 | 407,315
27 | 5 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7316 | 407,317
27 | 5 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7318 | 407,319
27 | 5 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7320 | 407,321
27 | 5 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7322 | 407,323
27 | 5 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7324 | 407,325
27 | 5 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7326 | 407,327
27 | 5 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7328 | 407,329
27 | 5 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7330 | 407,331
27 | 5 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7332 | 407,333
27 | 5 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7334 | 407,335
27 | 5 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7336 | 407,337
27 | 5 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7338 | 407,339
27 | 5 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7340 | 407,341
27 | 5 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7342 | 407,343
27 | 5 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 7344 | 407,345
27 | 5 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 7346 | 407,347
27 | 5 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 7348 | 407,349
27 | 5 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 7350 | 407,351
27 | 6 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7370 | 407,371
27 | 6 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7372 | 407,373
27 | 6 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7374 | 407,375
27 | 6 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7376 | 407,377
27 | 6 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7378 | 407,379
27 | 6 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7380 | 407,381
27 | 6 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7382 | 407,383
27 | 6 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7384 | 407,385
27 | 6 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7386 | 407,387
27 | 6 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7388 | 407,389
27 | 6 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7390 | 407,391
27 | 6 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7392 | 407,393
27 | 6 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7394 | 407,395
27 | 6 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7396 | 407,397
27 | 6 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7398 | 407,399
27 | 6 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7400 | 407,401
27 | 6 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7402 | 407,403
27 | 6 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7404 | 407,405
27 | 6 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7406 | 407,407
27 | 6 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7408 | 407,409
27 | 6 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7410 | 407,411
27 | 6 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7412 | 407,413
27 | 6 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7414 | 407,415
27 | 6 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7416 | 407,417
27 | 6 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7418 | 407,419
27 | 6 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7420 | 407,421
27 | 6 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7422 | 407,423
27 | 6 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7424 | 407,425
27 | 6 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7426 | 407,427
27 | 6 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7428 | 407,429
27 | 6 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7430 | 407,431
27 | 6 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7432 | 407,433
27 | 6 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 7434 | 407,435
27 | 6 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 7436 | 407,437
27 | 6 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 7438 | 407,439
27 | 6 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 7440 | 407,441
27 | 7 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7460 | 407,461
27 | 7 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7462 | 407,463
27 | 7 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7464 | 407,465
27 | 7 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7466 | 407,467
27 | 7 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7468 | 407,469
27 | 7 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7470 | 407,471
27 | 7 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7472 | 407,473
27 | 7 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7474 | 407,475
27 | 7 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7476 | 407,477
27 | 7 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7478 | 407,479
27 | 7 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7480 | 407,481
27 | 7 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7482 | 407,483
27 | 7 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7484 | 407,485
27 | 7 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7486 | 407,487
27 | 7 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7488 | 407,489
27 | 7 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7490 | 407,491
27 | 7 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7492 | 407,493
27 | 7 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7494 | 407,495
27 | 7 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7496 | 407,497
27 | 7 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7498 | 407,499
27 | 7 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7500 | 407,501
27 | 7 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7502 | 407,503
27 | 7 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7504 | 407,505
27 | 7 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7506 | 407,507
27 | 7 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7508 | 407,509
27 | 7 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7510 | 407,511
27 | 7 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7512 | 407,513
27 | 7 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7514 | 407,515
27 | 7 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7516 | 407,517
27 | 7 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7518 | 407,519
27 | 7 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7520 | 407,521
27 | 7 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7522 | 407,523
27 | 7 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 7524 | 407,525
27 | 7 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 7526 | 407,527
27 | 7 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 7528 | 407,529
27 | 7 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 7530 | 407,531
27 | 8 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7550 | 407,551
27 | 8 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7552 | 407,553
27 | 8 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7554 | 407,555
27 | 8 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7556 | 407,557
27 | 8 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7558 | 407,559
27 | 8 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7560 | 407,561
27 | 8 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7562 | 407,563
27 | 8 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7564 | 407,565
27 | 8 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7566 | 407,567
27 | 8 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7568 | 407,569
27 | 8 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7570 | 407,571
27 | 8 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7572 | 407,573
27 | 8 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7574 | 407,575
27 | 8 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7576 | 407,577
27 | 8 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7578 | 407,579
27 | 8 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7580 | 407,581
27 | 8 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7582 | 407,583
27 | 8 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7584 | 407,585
27 | 8 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7586 | 407,587
27 | 8 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7588 | 407,589
27 | 8 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7590 | 407,591
27 | 8 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7592 | 407,593
27 | 8 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7594 | 407,595
27 | 8 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7596 | 407,597
27 | 8 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7598 | 407,599
27 | 8 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7600 | 407,601
27 | 8 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7602 | 407,603
27 | 8 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7604 | 407,605
27 | 8 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7606 | 407,607
27 | 8 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7608 | 407,609
27 | 8 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7610 | 407,611
27 | 8 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7612 | 407,613
27 | 8 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 7614 | 407,615
27 | 8 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 7616 | 407,617
27 | 8 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 7618 | 407,619
27 | 8 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 7620 | 407,621
27 | 9 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7640 | 407,641
27 | 9 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7642 | 407,643
27 | 9 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7644 | 407,645
27 | 9 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7646 | 407,647
27 | 9 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7648 | 407,649
27 | 9 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7650 | 407,651
27 | 9 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7652 | 407,653
27 | 9 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7654 | 407,655
27 | 9 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7656 | 407,657
27 | 9 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7658 | 407,659
27 | 9 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7660 | 407,661
27 | 9 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7662 | 407,663
27 | 9 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7664 | 407,665
27 | 9 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7666 | 407,667
27 | 9 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7668 | 407,669
27 | 9 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7670 | 407,671
27 | 9 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7672 | 407,673
27 | 9 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7674 | 407,675
27 | 9 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7676 | 407,677
27 | 9 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7678 | 407,679
27 | 9 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7680 | 407,681
27 | 9 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7682 | 407,683
27 | 9 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7684 | 407,685
27 | 9 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7686 | 407,687
27 | 9 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7688 | 407,689
27 | 9 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7690 | 407,691
27 | 9 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7692 | 407,693
27 | 9 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7694 | 407,695
27 | 9 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7696 | 407,697
27 | 9 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7698 | 407,699
27 | 9 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7700 | 407,701
27 | 9 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7702 | 407,703
27 | 9 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 7704 | 407,705
27 | 9 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 7706 | 407,707
27 | 9 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 7708 | 407,709
27 | 9 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 7710 | 407,711
27 | 10 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7730 | 407,731
27 | 10 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7732 | 407,733
27 | 10 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7734 | 407,735
27 | 10 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7736 | 407,737
27 | 10 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7738 | 407,739
27 | 10 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7740 | 407,741
27 | 10 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7742 | 407,743
27 | 10 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7744 | 407,745
27 | 10 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7746 | 407,747
27 | 10 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7748 | 407,749
27 | 10 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7750 | 407,751
27 | 10 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7752 | 407,753
27 | 10 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7754 | 407,755
27 | 10 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7756 | 407,757
27 | 10 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7758 | 407,759
27 | 10 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7760 | 407,761
27 | 10 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7762 | 407,763
27 | 10 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7764 | 407,765
27 | 10 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7766 | 407,767
27 | 10 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7768 | 407,769
27 | 10 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7770 | 407,771
27 | 10 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7772 | 407,773
27 | 10 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7774 | 407,775
27 | 10 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7776 | 407,777
27 | 10 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7778 | 407,779
27 | 10 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7780 | 407,781
27 | 10 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7782 | 407,783
27 | 10 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7784 | 407,785
27 | 10 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7786 | 407,787
27 | 10 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7788 | 407,789
27 | 10 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7790 | 407,791
27 | 10 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7792 | 407,793
27 | 10 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 7794 | 407,795
27 | 10 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 7796 | 407,797
27 | 10 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 7798 | 407,799
27 | 10 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 7800 | 407,801
27 | 11 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7820 | 407,821
27 | 11 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7822 | 407,823
27 | 11 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7824 | 407,825
27 | 11 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7826 | 407,827
27 | 11 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7828 | 407,829
27 | 11 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7830 | 407,831
27 | 11 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7832 | 407,833
27 | 11 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7834 | 407,835
27 | 11 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7836 | 407,837
27 | 11 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7838 | 407,839
27 | 11 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7840 | 407,841
27 | 11 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7842 | 407,843
27 | 11 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7844 | 407,845
27 | 11 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7846 | 407,847
27 | 11 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7848 | 407,849
27 | 11 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7850 | 407,851
27 | 11 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7852 | 407,853
27 | 11 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7854 | 407,855
27 | 11 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7856 | 407,857
27 | 11 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7858 | 407,859
27 | 11 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7860 | 407,861
27 | 11 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7862 | 407,863
27 | 11 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7864 | 407,865
27 | 11 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7866 | 407,867
27 | 11 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7868 | 407,869
27 | 11 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7870 | 407,871
27 | 11 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7872 | 407,873
27 | 11 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7874 | 407,875
27 | 11 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7876 | 407,877
27 | 11 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7878 | 407,879
27 | 11 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7880 | 407,881
27 | 11 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7882 | 407,883
27 | 11 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 7884 | 407,885
27 | 11 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 7886 | 407,887
27 | 11 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 7888 | 407,889
27 | 11 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 7890 | 407,891
27 | 12 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7910 | 407,911
27 | 12 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7912 | 407,913
27 | 12 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7914 | 407,915
27 | 12 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7916 | 407,917
27 | 12 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7918 | 407,919
27 | 12 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7920 | 407,921
27 | 12 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7922 | 407,923
27 | 12 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 7924 | 407,925
27 | 12 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7926 | 407,927
27 | 12 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7928 | 407,929
27 | 12 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7930 | 407,931
27 | 12 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7932 | 407,933
27 | 12 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7934 | 407,935
27 | 12 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7936 | 407,937
27 | 12 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7938 | 407,939
27 | 12 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 7940 | 407,941
27 | 12 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7942 | 407,943
27 | 12 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7944 | 407,945
27 | 12 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7946 | 407,947
27 | 12 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7948 | 407,949
27 | 12 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7950 | 407,951
27 | 12 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7952 | 407,953
27 | 12 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7954 | 407,955
27 | 12 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 7956 | 407,957
27 | 12 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7958 | 407,959
27 | 12 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7960 | 407,961
27 | 12 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7962 | 407,963
27 | 12 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7964 | 407,965
27 | 12 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7966 | 407,967
27 | 12 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7968 | 407,969
27 | 12 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7970 | 407,971
27 | 12 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 7972 | 407,973
27 | 12 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 7974 | 407,975
27 | 12 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 7976 | 407,977
27 | 12 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 7978 | 407,979
27 | 12 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 7980 | 407,981
27 | 13 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8000 | 408,001
27 | 13 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8002 | 408,003
27 | 13 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8004 | 408,005
27 | 13 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8006 | 408,007
27 | 13 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8008 | 408,009
27 | 13 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8010 | 408,011
27 | 13 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8012 | 408,013
27 | 13 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8014 | 408,015
27 | 13 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8016 | 408,017
27 | 13 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8018 | 408,019
27 | 13 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8020 | 408,021
27 | 13 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8022 | 408,023
27 | 13 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8024 | 408,025
27 | 13 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8026 | 408,027
27 | 13 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8028 | 408,029
27 | 13 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8030 | 408,031
27 | 13 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8032 | 408,033
27 | 13 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8034 | 408,035
27 | 13 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8036 | 408,037
27 | 13 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8038 | 408,039
27 | 13 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8040 | 408,041
27 | 13 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8042 | 408,043
27 | 13 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8044 | 408,045
27 | 13 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8046 | 408,047
27 | 13 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8048 | 408,049
27 | 13 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8050 | 408,051
27 | 13 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8052 | 408,053
27 | 13 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8054 | 408,055
27 | 13 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8056 | 408,057
27 | 13 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8058 | 408,059
27 | 13 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8060 | 408,061
27 | 13 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8062 | 408,063
27 | 13 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 8064 | 408,065
27 | 13 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 8066 | 408,067
27 | 13 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 8068 | 408,069
27 | 13 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8070 | 408,071
27 | 14 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8090 | 408,091
27 | 14 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8092 | 408,093
27 | 14 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8094 | 408,095
27 | 14 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8096 | 408,097
27 | 14 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8098 | 408,099
27 | 14 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8100 | 408,101
27 | 14 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8102 | 408,103
27 | 14 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8104 | 408,105
27 | 14 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8106 | 408,107
27 | 14 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8108 | 408,109
27 | 14 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8110 | 408,111
27 | 14 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8112 | 408,113
27 | 14 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8114 | 408,115
27 | 14 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8116 | 408,117
27 | 14 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8118 | 408,119
27 | 14 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8120 | 408,121
27 | 14 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8122 | 408,123
27 | 14 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8124 | 408,125
27 | 14 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8126 | 408,127
27 | 14 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8128 | 408,129
27 | 14 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8130 | 408,131
27 | 14 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8132 | 408,133
27 | 14 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8134 | 408,135
27 | 14 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8136 | 408,137
27 | 14 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8138 | 408,139
27 | 14 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8140 | 408,141
27 | 14 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8142 | 408,143
27 | 14 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8144 | 408,145
27 | 14 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8146 | 408,147
27 | 14 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8148 | 408,149
27 | 14 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8150 | 408,151
27 | 14 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8152 | 408,153
27 | 14 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 8154 | 408,155
27 | 14 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 8156 | 408,157
27 | 14 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 8158 | 408,159
27 | 14 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8160 | 408,161
27 | 15 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8180 | 408,181
27 | 15 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8182 | 408,183
27 | 15 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8184 | 408,185
27 | 15 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8186 | 408,187
27 | 15 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8188 | 408,189
27 | 15 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8190 | 408,191
27 | 15 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8192 | 408,193
27 | 15 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8194 | 408,195
27 | 15 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8196 | 408,197
27 | 15 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8198 | 408,199
27 | 15 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8200 | 408,201
27 | 15 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8202 | 408,203
27 | 15 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8204 | 408,205
27 | 15 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8206 | 408,207
27 | 15 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8208 | 408,209
27 | 15 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8210 | 408,211
27 | 15 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8212 | 408,213
27 | 15 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8214 | 408,215
27 | 15 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8216 | 408,217
27 | 15 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8218 | 408,219
27 | 15 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8220 | 408,221
27 | 15 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8222 | 408,223
27 | 15 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8224 | 408,225
27 | 15 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8226 | 408,227
27 | 15 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8228 | 408,229
27 | 15 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8230 | 408,231
27 | 15 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8232 | 408,233
27 | 15 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8234 | 408,235
27 | 15 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8236 | 408,237
27 | 15 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8238 | 408,239
27 | 15 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8240 | 408,241
27 | 15 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8242 | 408,243
27 | 15 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 8244 | 408,245
27 | 15 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 8246 | 408,247
27 | 15 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 8248 | 408,249
27 | 15 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8250 | 408,251
27 | 16 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8270 | 408,271
27 | 16 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8272 | 408,273
27 | 16 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8274 | 408,275
27 | 16 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8276 | 408,277
27 | 16 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8278 | 408,279
27 | 16 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8280 | 408,281
27 | 16 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8282 | 408,283
27 | 16 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8284 | 408,285
27 | 16 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8286 | 408,287
27 | 16 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8288 | 408,289
27 | 16 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8290 | 408,291
27 | 16 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8292 | 408,293
27 | 16 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8294 | 408,295
27 | 16 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8296 | 408,297
27 | 16 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8298 | 408,299
27 | 16 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8300 | 408,301
27 | 16 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8302 | 408,303
27 | 16 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8304 | 408,305
27 | 16 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8306 | 408,307
27 | 16 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8308 | 408,309
27 | 16 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8310 | 408,311
27 | 16 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8312 | 408,313
27 | 16 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8314 | 408,315
27 | 16 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8316 | 408,317
27 | 16 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8318 | 408,319
27 | 16 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8320 | 408,321
27 | 16 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8322 | 408,323
27 | 16 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8324 | 408,325
27 | 16 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8326 | 408,327
27 | 16 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8328 | 408,329
27 | 16 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8330 | 408,331
27 | 16 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8332 | 408,333
27 | 16 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 8334 | 408,335
27 | 16 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 8336 | 408,337
27 | 16 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 8338 | 408,339
27 | 16 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8340 | 408,341
27 | 17 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8360 | 408,361
27 | 17 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8362 | 408,363
27 | 17 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8364 | 408,365
27 | 17 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8366 | 408,367
27 | 17 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8368 | 408,369
27 | 17 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8370 | 408,371
27 | 17 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8372 | 408,373
27 | 17 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8374 | 408,375
27 | 17 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8376 | 408,377
27 | 17 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8378 | 408,379
27 | 17 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8380 | 408,381
27 | 17 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8382 | 408,383
27 | 17 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8384 | 408,385
27 | 17 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8386 | 408,387
27 | 17 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8388 | 408,389
27 | 17 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8390 | 408,391
27 | 17 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8392 | 408,393
27 | 17 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8394 | 408,395
27 | 17 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8396 | 408,397
27 | 17 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8398 | 408,399
27 | 17 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8400 | 408,401
27 | 17 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8402 | 408,403
27 | 17 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8404 | 408,405
27 | 17 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8406 | 408,407
27 | 17 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8408 | 408,409
27 | 17 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8410 | 408,411
27 | 17 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8412 | 408,413
27 | 17 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8414 | 408,415
27 | 17 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8416 | 408,417
27 | 17 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8418 | 408,419
27 | 17 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8420 | 408,421
27 | 17 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8422 | 408,423
27 | 17 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 8424 | 408,425
27 | 17 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 8426 | 408,427
27 | 17 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 8428 | 408,429
27 | 17 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8430 | 408,431
27 | 18 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8450 | 408,451
27 | 18 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8452 | 408,453
27 | 18 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8454 | 408,455
27 | 18 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8456 | 408,457
27 | 18 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8458 | 408,459
27 | 18 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8460 | 408,461
27 | 18 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8462 | 408,463
27 | 18 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8464 | 408,465
27 | 18 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8466 | 408,467
27 | 18 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8468 | 408,469
27 | 18 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8470 | 408,471
27 | 18 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8472 | 408,473
27 | 18 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8474 | 408,475
27 | 18 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8476 | 408,477
27 | 18 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8478 | 408,479
27 | 18 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8480 | 408,481
27 | 18 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8482 | 408,483
27 | 18 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8484 | 408,485
27 | 18 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8486 | 408,487
27 | 18 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8488 | 408,489
27 | 18 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8490 | 408,491
27 | 18 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8492 | 408,493
27 | 18 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8494 | 408,495
27 | 18 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8496 | 408,497
27 | 18 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8498 | 408,499
27 | 18 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8500 | 408,501
27 | 18 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8502 | 408,503
27 | 18 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8504 | 408,505
27 | 18 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8506 | 408,507
27 | 18 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8508 | 408,509
27 | 18 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8510 | 408,511
27 | 18 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8512 | 408,513
27 | 18 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 8514 | 408,515
27 | 18 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 8516 | 408,517
27 | 18 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 8518 | 408,519
27 | 18 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8520 | 408,521
27 | 19 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8540 | 408,541
27 | 19 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8542 | 408,543
27 | 19 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8544 | 408,545
27 | 19 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8546 | 408,547
27 | 19 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8548 | 408,549
27 | 19 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8550 | 408,551
27 | 19 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8552 | 408,553
27 | 19 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8554 | 408,555
27 | 19 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8556 | 408,557
27 | 19 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8558 | 408,559
27 | 19 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8560 | 408,561
27 | 19 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8562 | 408,563
27 | 19 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8564 | 408,565
27 | 19 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8566 | 408,567
27 | 19 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8568 | 408,569
27 | 19 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8570 | 408,571
27 | 19 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8572 | 408,573
27 | 19 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8574 | 408,575
27 | 19 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8576 | 408,577
27 | 19 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8578 | 408,579
27 | 19 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8580 | 408,581
27 | 19 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8582 | 408,583
27 | 19 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8584 | 408,585
27 | 19 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8586 | 408,587
27 | 19 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8588 | 408,589
27 | 19 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8590 | 408,591
27 | 19 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8592 | 408,593
27 | 19 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8594 | 408,595
27 | 19 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8596 | 408,597
27 | 19 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8598 | 408,599
27 | 19 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8600 | 408,601
27 | 19 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8602 | 408,603
27 | 19 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 8604 | 408,605
27 | 19 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 8606 | 408,607
27 | 19 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 8608 | 408,609
27 | 19 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8610 | 408,611
27 | 20 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8630 | 408,631
27 | 20 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8632 | 408,633
27 | 20 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8634 | 408,635
27 | 20 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8636 | 408,637
27 | 20 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8638 | 408,639
27 | 20 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8640 | 408,641
27 | 20 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8642 | 408,643
27 | 20 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8644 | 408,645
27 | 20 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8646 | 408,647
27 | 20 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8648 | 408,649
27 | 20 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8650 | 408,651
27 | 20 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8652 | 408,653
27 | 20 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8654 | 408,655
27 | 20 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8656 | 408,657
27 | 20 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8658 | 408,659
27 | 20 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8660 | 408,661
27 | 20 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8662 | 408,663
27 | 20 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8664 | 408,665
27 | 20 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8666 | 408,667
27 | 20 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8668 | 408,669
27 | 20 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8670 | 408,671
27 | 20 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8672 | 408,673
27 | 20 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8674 | 408,675
27 | 20 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8676 | 408,677
27 | 20 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8678 | 408,679
27 | 20 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8680 | 408,681
27 | 20 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8682 | 408,683
27 | 20 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8684 | 408,685
27 | 20 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8686 | 408,687
27 | 20 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8688 | 408,689
27 | 20 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8690 | 408,691
27 | 20 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8692 | 408,693
27 | 20 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 8694 | 408,695
27 | 20 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 8696 | 408,697
27 | 20 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 8698 | 408,699
27 | 20 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8700 | 408,701
27 | 21 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8720 | 408,721
27 | 21 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8722 | 408,723
27 | 21 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8724 | 408,725
27 | 21 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8726 | 408,727
27 | 21 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8728 | 408,729
27 | 21 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8730 | 408,731
27 | 21 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8732 | 408,733
27 | 21 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8734 | 408,735
27 | 21 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8736 | 408,737
27 | 21 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8738 | 408,739
27 | 21 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8740 | 408,741
27 | 21 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8742 | 408,743
27 | 21 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8744 | 408,745
27 | 21 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8746 | 408,747
27 | 21 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8748 | 408,749
27 | 21 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8750 | 408,751
27 | 21 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8752 | 408,753
27 | 21 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8754 | 408,755
27 | 21 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8756 | 408,757
27 | 21 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8758 | 408,759
27 | 21 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8760 | 408,761
27 | 21 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8762 | 408,763
27 | 21 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8764 | 408,765
27 | 21 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8766 | 408,767
27 | 21 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8768 | 408,769
27 | 21 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8770 | 408,771
27 | 21 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8772 | 408,773
27 | 21 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8774 | 408,775
27 | 21 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8776 | 408,777
27 | 21 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8778 | 408,779
27 | 21 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8780 | 408,781
27 | 21 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8782 | 408,783
27 | 21 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 8784 | 408,785
27 | 21 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 8786 | 408,787
27 | 21 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 8788 | 408,789
27 | 21 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8790 | 408,791
27 | 22 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8810 | 408,811
27 | 22 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8812 | 408,813
27 | 22 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8814 | 408,815
27 | 22 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8816 | 408,817
27 | 22 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8818 | 408,819
27 | 22 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8820 | 408,821
27 | 22 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8822 | 408,823
27 | 22 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8824 | 408,825
27 | 22 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8826 | 408,827
27 | 22 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8828 | 408,829
27 | 22 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8830 | 408,831
27 | 22 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8832 | 408,833
27 | 22 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8834 | 408,835
27 | 22 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8836 | 408,837
27 | 22 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8838 | 408,839
27 | 22 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8840 | 408,841
27 | 22 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8842 | 408,843
27 | 22 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8844 | 408,845
27 | 22 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8846 | 408,847
27 | 22 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8848 | 408,849
27 | 22 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8850 | 408,851
27 | 22 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8852 | 408,853
27 | 22 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8854 | 408,855
27 | 22 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8856 | 408,857
27 | 22 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8858 | 408,859
27 | 22 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8860 | 408,861
27 | 22 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8862 | 408,863
27 | 22 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8864 | 408,865
27 | 22 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8866 | 408,867
27 | 22 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8868 | 408,869
27 | 22 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8870 | 408,871
27 | 22 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8872 | 408,873
27 | 22 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 8874 | 408,875
27 | 22 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 8876 | 408,877
27 | 22 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 8878 | 408,879
27 | 22 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8880 | 408,881
27 | 23 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8900 | 408,901
27 | 23 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8902 | 408,903
27 | 23 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8904 | 408,905
27 | 23 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8906 | 408,907
27 | 23 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8908 | 408,909
27 | 23 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8910 | 408,911
27 | 23 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8912 | 408,913
27 | 23 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8914 | 408,915
27 | 23 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8916 | 408,917
27 | 23 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8918 | 408,919
27 | 23 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8920 | 408,921
27 | 23 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8922 | 408,923
27 | 23 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8924 | 408,925
27 | 23 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8926 | 408,927
27 | 23 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8928 | 408,929
27 | 23 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 8930 | 408,931
27 | 23 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8932 | 408,933
27 | 23 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8934 | 408,935
27 | 23 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8936 | 408,937
27 | 23 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8938 | 408,939
27 | 23 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8940 | 408,941
27 | 23 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8942 | 408,943
27 | 23 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8944 | 408,945
27 | 23 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 8946 | 408,947
27 | 23 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8948 | 408,949
27 | 23 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8950 | 408,951
27 | 23 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8952 | 408,953
27 | 23 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8954 | 408,955
27 | 23 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8956 | 408,957
27 | 23 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8958 | 408,959
27 | 23 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8960 | 408,961
27 | 23 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 8962 | 408,963
27 | 23 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 8964 | 408,965
27 | 23 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 8966 | 408,967
27 | 23 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 8968 | 408,969
27 | 23 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 8970 | 408,971
27 | 24 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8990 | 408,991
27 | 24 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8992 | 408,993
27 | 24 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8994 | 408,995
27 | 24 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8996 | 408,997
27 | 24 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 8998 | 408,999
27 | 24 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 9000 | 409,001
27 | 24 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 9002 | 409,003
27 | 24 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 9004 | 409,005
27 | 24 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 9006 | 409,007
27 | 24 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 9008 | 409,009
27 | 24 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 9010 | 409,011
27 | 24 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 9012 | 409,013
27 | 24 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 9014 | 409,015
27 | 24 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 9016 | 409,017
27 | 24 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 9018 | 409,019
27 | 24 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 9020 | 409,021
27 | 24 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 9022 | 409,023
27 | 24 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 9024 | 409,025
27 | 24 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 9026 | 409,027
27 | 24 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 9028 | 409,029
27 | 24 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 9030 | 409,031
27 | 24 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 9032 | 409,033
27 | 24 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 9034 | 409,035
27 | 24 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 9036 | 409,037
27 | 24 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | Enumeration | R | 9038 | 409,039
27 | 24 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | Enumeration | R | 9040 | 409,041
27 | 24 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | Enumeration | R | 9042 | 409,043
27 | 24 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | Enumeration | R | 9044 | 409,045
27 | 24 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | Enumeration | R | 9046 | 409,047
27 | 24 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | Enumeration | R | 9048 | 409,049
27 | 24 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | Enumeration | R | 9050 | 409,051
27 | 24 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | Enumeration | R | 9052 | 409,053
27 | 24 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | Enumeration | R/W | 9054 | 409,055
27 | 24 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | Enumeration | R | 9056 | 409,057
27 | 24 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 9058 | 409,059
27 | 24 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 9060 | 409,061
28 | 1 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 4810 | 404,811
28 | 1 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 4812 | 404,813
28 | 1 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4814 | 404,815
28 | 1 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4816 | 404,817
28 | 1 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4818 | 404,819
28 | 1 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4820 | 404,821
28 | 1 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 4822 | 404,823
28 | 1 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 4824 | 404,825
28 | 1 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 4826 | 404,827
28 | 1 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 4828 | 404,829
28 | 1 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 4830 | 404,831
28 | 1 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 4832 | 404,833
28 | 1 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4834 | 404,835
28 | 2 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 4850 | 404,851
28 | 2 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 4852 | 404,853
28 | 2 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4854 | 404,855
28 | 2 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4856 | 404,857
28 | 2 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4858 | 404,859
28 | 2 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4860 | 404,861
28 | 2 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 4862 | 404,863
28 | 2 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 4864 | 404,865
28 | 2 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 4866 | 404,867
28 | 2 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 4868 | 404,869
28 | 2 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 4870 | 404,871
28 | 2 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 4872 | 404,873
28 | 2 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4874 | 404,875
28 | 3 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 4890 | 404,891
28 | 3 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 4892 | 404,893
28 | 3 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4894 | 404,895
28 | 3 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4896 | 404,897
28 | 3 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4898 | 404,899
28 | 3 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4900 | 404,901
28 | 3 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 4902 | 404,903
28 | 3 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 4904 | 404,905
28 | 3 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 4906 | 404,907
28 | 3 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 4908 | 404,909
28 | 3 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 4910 | 404,911
28 | 3 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 4912 | 404,913
28 | 3 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4914 | 404,915
28 | 4 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 4930 | 404,931
28 | 4 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 4932 | 404,933
28 | 4 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4934 | 404,935
28 | 4 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4936 | 404,937
28 | 4 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4938 | 404,939
28 | 4 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4940 | 404,941
28 | 4 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 4942 | 404,943
28 | 4 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 4944 | 404,945
28 | 4 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 4946 | 404,947
28 | 4 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 4948 | 404,949
28 | 4 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 4950 | 404,951
28 | 4 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 4952 | 404,953
28 | 4 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4954 | 404,955
28 | 5 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 4970 | 404,971
28 | 5 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 4972 | 404,973
28 | 5 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4974 | 404,975
28 | 5 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 4976 | 404,977
28 | 5 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4978 | 404,979
28 | 5 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 4980 | 404,981
28 | 5 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 4982 | 404,983
28 | 5 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 4984 | 404,985
28 | 5 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 4986 | 404,987
28 | 5 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 4988 | 404,989
28 | 5 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 4990 | 404,991
28 | 5 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 4992 | 404,993
28 | 5 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 4994 | 404,995
28 | 6 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5010 | 405,011
28 | 6 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5012 | 405,013
28 | 6 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5014 | 405,015
28 | 6 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5016 | 405,017
28 | 6 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5018 | 405,019
28 | 6 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5020 | 405,021
28 | 6 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 5022 | 405,023
28 | 6 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 5024 | 405,025
28 | 6 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 5026 | 405,027
28 | 6 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 5028 | 405,029
28 | 6 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 5030 | 405,031
28 | 6 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 5032 | 405,033
28 | 6 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5034 | 405,035
28 | 7 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5050 | 405,051
28 | 7 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5052 | 405,053
28 | 7 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5054 | 405,055
28 | 7 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5056 | 405,057
28 | 7 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5058 | 405,059
28 | 7 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5060 | 405,061
28 | 7 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 5062 | 405,063
28 | 7 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 5064 | 405,065
28 | 7 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 5066 | 405,067
28 | 7 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 5068 | 405,069
28 | 7 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 5070 | 405,071
28 | 7 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 5072 | 405,073
28 | 7 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5074 | 405,075
28 | 8 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5090 | 405,091
28 | 8 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5092 | 405,093
28 | 8 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5094 | 405,095
28 | 8 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5096 | 405,097
28 | 8 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5098 | 405,099
28 | 8 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5100 | 405,101
28 | 8 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 5102 | 405,103
28 | 8 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 5104 | 405,105
28 | 8 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 5106 | 405,107
28 | 8 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 5108 | 405,109
28 | 8 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 5110 | 405,111
28 | 8 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 5112 | 405,113
28 | 8 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5114 | 405,115
28 | 9 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5130 | 405,131
28 | 9 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5132 | 405,133
28 | 9 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5134 | 405,135
28 | 9 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5136 | 405,137
28 | 9 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5138 | 405,139
28 | 9 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5140 | 405,141
28 | 9 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 5142 | 405,143
28 | 9 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 5144 | 405,145
28 | 9 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 5146 | 405,147
28 | 9 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 5148 | 405,149
28 | 9 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 5150 | 405,151
28 | 9 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 5152 | 405,153
28 | 9 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5154 | 405,155
28 | 10 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5170 | 405,171
28 | 10 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5172 | 405,173
28 | 10 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5174 | 405,175
28 | 10 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5176 | 405,177
28 | 10 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5178 | 405,179
28 | 10 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5180 | 405,181
28 | 10 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 5182 | 405,183
28 | 10 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 5184 | 405,185
28 | 10 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 5186 | 405,187
28 | 10 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 5188 | 405,189
28 | 10 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 5190 | 405,191
28 | 10 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 5192 | 405,193
28 | 10 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5194 | 405,195
28 | 11 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5210 | 405,211
28 | 11 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5212 | 405,213
28 | 11 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5214 | 405,215
28 | 11 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5216 | 405,217
28 | 11 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5218 | 405,219
28 | 11 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5220 | 405,221
28 | 11 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 5222 | 405,223
28 | 11 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 5224 | 405,225
28 | 11 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 5226 | 405,227
28 | 11 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 5228 | 405,229
28 | 11 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 5230 | 405,231
28 | 11 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 5232 | 405,233
28 | 11 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5234 | 405,235
28 | 12 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5250 | 405,251
28 | 12 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5252 | 405,253
28 | 12 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5254 | 405,255
28 | 12 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5256 | 405,257
28 | 12 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5258 | 405,259
28 | 12 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5260 | 405,261
28 | 12 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 5262 | 405,263
28 | 12 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 5264 | 405,265
28 | 12 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 5266 | 405,267
28 | 12 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 5268 | 405,269
28 | 12 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 5270 | 405,271
28 | 12 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 5272 | 405,273
28 | 12 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5274 | 405,275
28 | 13 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5290 | 405,291
28 | 13 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5292 | 405,293
28 | 13 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5294 | 405,295
28 | 13 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5296 | 405,297
28 | 13 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5298 | 405,299
28 | 13 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5300 | 405,301
28 | 13 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 5302 | 405,303
28 | 13 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 5304 | 405,305
28 | 13 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 5306 | 405,307
28 | 13 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 5308 | 405,309
28 | 13 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 5310 | 405,311
28 | 13 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 5312 | 405,313
28 | 13 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5314 | 405,315
28 | 14 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5330 | 405,331
28 | 14 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5332 | 405,333
28 | 14 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5334 | 405,335
28 | 14 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5336 | 405,337
28 | 14 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5338 | 405,339
28 | 14 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5340 | 405,341
28 | 14 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 5342 | 405,343
28 | 14 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 5344 | 405,345
28 | 14 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 5346 | 405,347
28 | 14 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 5348 | 405,349
28 | 14 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 5350 | 405,351
28 | 14 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 5352 | 405,353
28 | 14 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5354 | 405,355
28 | 15 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5370 | 405,371
28 | 15 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5372 | 405,373
28 | 15 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5374 | 405,375
28 | 15 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5376 | 405,377
28 | 15 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5378 | 405,379
28 | 15 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5380 | 405,381
28 | 15 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 5382 | 405,383
28 | 15 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 5384 | 405,385
28 | 15 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 5386 | 405,387
28 | 15 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 5388 | 405,389
28 | 15 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 5390 | 405,391
28 | 15 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 5392 | 405,393
28 | 15 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5394 | 405,395
28 | 16 | 1 | Compare | Base | Source Function A | Set the Source A for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5410 | 405,411
28 | 16 | 2 | Compare | Base | Source Function B | Set the Source B for the receiver in the Compare block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 5412 | 405,413
28 | 16 | 3 | Compare | Base | Source Instance A | Set the Source Instance A for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5414 | 405,415
28 | 16 | 4 | Compare | Base | Source Instance B | Set the Source Instance B for the receiver in the Compare block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5416 | 405,417
28 | 16 | 5 | Compare | Base | Source Zone A | Set the Source Zone A for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5418 | 405,419
28 | 16 | 6 | Compare | Base | Source Zone B | Set the Source Zone B for the receiver in the Compare block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5420 | 405,421
28 | 16 | 7 | Compare | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 5422 | 405,423
28 | 16 | 8 | Compare | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 5424 | 405,425
28 | 16 | 9 | Compare | Base | Function | Set the Function of the Compare block. | Off (62), Greater Than (1435), Less Than (1436), Equal To (1437), Not Equal To (1438), Greater or Equal (1439), Less or Equal (1440) | Off (62) | Enumeration | R/W | 5426 | 405,427
28 | 16 | 10 | Compare | Base | Output Value | Monitor the output value of the Compare block. | On (63), Off (62) |  | Enumeration | R | 5428 | 405,429
28 | 16 | 11 | Compare | Base | Tolerance | Set Tolerance to set how precisely A and B must match to be considered equal. | 0 to 99,999.0 | 0.1 | IEEE Float | R/W | 5430 | 405,431
28 | 16 | 12 | Compare | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | Enumeration | R/W | 5432 | 405,433
28 | 16 | 13 | Compare | Base | Error | Monitor the Logic block for input or compare errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5434 | 405,435
30 | 1 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5450 | 405,451
30 | 1 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5452 | 405,453
30 | 1 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5454 | 405,455
30 | 1 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5456 | 405,457
30 | 1 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5458 | 405,459
30 | 1 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5460 | 405,461
30 | 1 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5462 | 405,463
30 | 1 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5464 | 405,465
30 | 1 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 5466 | 405,467
30 | 1 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 5468 | 405,469
30 | 1 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 5470 | 405,471
30 | 1 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 5472 | 405,473
30 | 1 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 5474 | 405,475
30 | 1 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 5476 | 405,477
30 | 1 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 5478 | 405,479
30 | 1 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5480 | 405,481
30 | 1 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 5482 | 405,483
30 | 2 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5500 | 405,501
30 | 2 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5502 | 405,503
30 | 2 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5504 | 405,505
30 | 2 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5506 | 405,507
30 | 2 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5508 | 405,509
30 | 2 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5510 | 405,511
30 | 2 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5512 | 405,513
30 | 2 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5514 | 405,515
30 | 2 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 5516 | 405,517
30 | 2 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 5518 | 405,519
30 | 2 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 5520 | 405,521
30 | 2 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 5522 | 405,523
30 | 2 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 5524 | 405,525
30 | 2 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 5526 | 405,527
30 | 2 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 5528 | 405,529
30 | 2 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5530 | 405,531
30 | 2 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 5532 | 405,533
30 | 3 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5550 | 405,551
30 | 3 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5552 | 405,553
30 | 3 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5554 | 405,555
30 | 3 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5556 | 405,557
30 | 3 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5558 | 405,559
30 | 3 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5560 | 405,561
30 | 3 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5562 | 405,563
30 | 3 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5564 | 405,565
30 | 3 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 5566 | 405,567
30 | 3 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 5568 | 405,569
30 | 3 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 5570 | 405,571
30 | 3 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 5572 | 405,573
30 | 3 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 5574 | 405,575
30 | 3 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 5576 | 405,577
30 | 3 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 5578 | 405,579
30 | 3 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5580 | 405,581
30 | 3 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 5582 | 405,583
30 | 4 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5600 | 405,601
30 | 4 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5602 | 405,603
30 | 4 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5604 | 405,605
30 | 4 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5606 | 405,607
30 | 4 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5608 | 405,609
30 | 4 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5610 | 405,611
30 | 4 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5612 | 405,613
30 | 4 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5614 | 405,615
30 | 4 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 5616 | 405,617
30 | 4 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 5618 | 405,619
30 | 4 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 5620 | 405,621
30 | 4 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 5622 | 405,623
30 | 4 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 5624 | 405,625
30 | 4 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 5626 | 405,627
30 | 4 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 5628 | 405,629
30 | 4 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5630 | 405,631
30 | 4 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 5632 | 405,633
30 | 5 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5650 | 405,651
30 | 5 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5652 | 405,653
30 | 5 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5654 | 405,655
30 | 5 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5656 | 405,657
30 | 5 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5658 | 405,659
30 | 5 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5660 | 405,661
30 | 5 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5662 | 405,663
30 | 5 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5664 | 405,665
30 | 5 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 5666 | 405,667
30 | 5 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 5668 | 405,669
30 | 5 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 5670 | 405,671
30 | 5 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 5672 | 405,673
30 | 5 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 5674 | 405,675
30 | 5 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 5676 | 405,677
30 | 5 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 5678 | 405,679
30 | 5 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5680 | 405,681
30 | 5 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 5682 | 405,683
30 | 6 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5700 | 405,701
30 | 6 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5702 | 405,703
30 | 6 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5704 | 405,705
30 | 6 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5706 | 405,707
30 | 6 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5708 | 405,709
30 | 6 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5710 | 405,711
30 | 6 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5712 | 405,713
30 | 6 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5714 | 405,715
30 | 6 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 5716 | 405,717
30 | 6 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 5718 | 405,719
30 | 6 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 5720 | 405,721
30 | 6 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 5722 | 405,723
30 | 6 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 5724 | 405,725
30 | 6 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 5726 | 405,727
30 | 6 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 5728 | 405,729
30 | 6 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5730 | 405,731
30 | 6 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 5732 | 405,733
30 | 7 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5750 | 405,751
30 | 7 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5752 | 405,753
30 | 7 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5754 | 405,755
30 | 7 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5756 | 405,757
30 | 7 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5758 | 405,759
30 | 7 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5760 | 405,761
30 | 7 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5762 | 405,763
30 | 7 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5764 | 405,765
30 | 7 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 5766 | 405,767
30 | 7 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 5768 | 405,769
30 | 7 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 5770 | 405,771
30 | 7 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 5772 | 405,773
30 | 7 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 5774 | 405,775
30 | 7 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 5776 | 405,777
30 | 7 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 5778 | 405,779
30 | 7 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5780 | 405,781
30 | 7 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 5782 | 405,783
30 | 8 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5800 | 405,801
30 | 8 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5802 | 405,803
30 | 8 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5804 | 405,805
30 | 8 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5806 | 405,807
30 | 8 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5808 | 405,809
30 | 8 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5810 | 405,811
30 | 8 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5812 | 405,813
30 | 8 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5814 | 405,815
30 | 8 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 5816 | 405,817
30 | 8 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 5818 | 405,819
30 | 8 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 5820 | 405,821
30 | 8 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 5822 | 405,823
30 | 8 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 5824 | 405,825
30 | 8 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 5826 | 405,827
30 | 8 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 5828 | 405,829
30 | 8 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5830 | 405,831
30 | 8 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 5832 | 405,833
30 | 9 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5850 | 405,851
30 | 9 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5852 | 405,853
30 | 9 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5854 | 405,855
30 | 9 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5856 | 405,857
30 | 9 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5858 | 405,859
30 | 9 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5860 | 405,861
30 | 9 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5862 | 405,863
30 | 9 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5864 | 405,865
30 | 9 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 5866 | 405,867
30 | 9 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 5868 | 405,869
30 | 9 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 5870 | 405,871
30 | 9 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 5872 | 405,873
30 | 9 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 5874 | 405,875
30 | 9 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 5876 | 405,877
30 | 9 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 5878 | 405,879
30 | 9 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5880 | 405,881
30 | 9 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 5882 | 405,883
30 | 10 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5900 | 405,901
30 | 10 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5902 | 405,903
30 | 10 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5904 | 405,905
30 | 10 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5906 | 405,907
30 | 10 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5908 | 405,909
30 | 10 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5910 | 405,911
30 | 10 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5912 | 405,913
30 | 10 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5914 | 405,915
30 | 10 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 5916 | 405,917
30 | 10 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 5918 | 405,919
30 | 10 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 5920 | 405,921
30 | 10 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 5922 | 405,923
30 | 10 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 5924 | 405,925
30 | 10 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 5926 | 405,927
30 | 10 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 5928 | 405,929
30 | 10 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5930 | 405,931
30 | 10 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 5932 | 405,933
30 | 11 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5950 | 405,951
30 | 11 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 5952 | 405,953
30 | 11 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5954 | 405,955
30 | 11 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 5956 | 405,957
30 | 11 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5958 | 405,959
30 | 11 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 5960 | 405,961
30 | 11 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5962 | 405,963
30 | 11 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 5964 | 405,965
30 | 11 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 5966 | 405,967
30 | 11 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 5968 | 405,969
30 | 11 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 5970 | 405,971
30 | 11 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 5972 | 405,973
30 | 11 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 5974 | 405,975
30 | 11 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 5976 | 405,977
30 | 11 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 5978 | 405,979
30 | 11 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 5980 | 405,981
30 | 11 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 5982 | 405,983
30 | 12 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6000 | 406,001
30 | 12 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6002 | 406,003
30 | 12 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6004 | 406,005
30 | 12 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6006 | 406,007
30 | 12 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6008 | 406,009
30 | 12 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6010 | 406,011
30 | 12 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6012 | 406,013
30 | 12 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6014 | 406,015
30 | 12 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 6016 | 406,017
30 | 12 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 6018 | 406,019
30 | 12 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 6020 | 406,021
30 | 12 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 6022 | 406,023
30 | 12 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 6024 | 406,025
30 | 12 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 6026 | 406,027
30 | 12 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 6028 | 406,029
30 | 12 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 6030 | 406,031
30 | 12 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 6032 | 406,033
30 | 13 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6050 | 406,051
30 | 13 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6052 | 406,053
30 | 13 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6054 | 406,055
30 | 13 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6056 | 406,057
30 | 13 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6058 | 406,059
30 | 13 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6060 | 406,061
30 | 13 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6062 | 406,063
30 | 13 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6064 | 406,065
30 | 13 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 6066 | 406,067
30 | 13 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 6068 | 406,069
30 | 13 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 6070 | 406,071
30 | 13 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 6072 | 406,073
30 | 13 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 6074 | 406,075
30 | 13 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 6076 | 406,077
30 | 13 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 6078 | 406,079
30 | 13 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 6080 | 406,081
30 | 13 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 6082 | 406,083
30 | 14 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6100 | 406,101
30 | 14 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6102 | 406,103
30 | 14 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6104 | 406,105
30 | 14 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6106 | 406,107
30 | 14 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6108 | 406,109
30 | 14 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6110 | 406,111
30 | 14 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6112 | 406,113
30 | 14 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6114 | 406,115
30 | 14 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 6116 | 406,117
30 | 14 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 6118 | 406,119
30 | 14 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 6120 | 406,121
30 | 14 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 6122 | 406,123
30 | 14 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 6124 | 406,125
30 | 14 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 6126 | 406,127
30 | 14 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 6128 | 406,129
30 | 14 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 6130 | 406,131
30 | 14 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 6132 | 406,133
30 | 15 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6150 | 406,151
30 | 15 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6152 | 406,153
30 | 15 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6154 | 406,155
30 | 15 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6156 | 406,157
30 | 15 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6158 | 406,159
30 | 15 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6160 | 406,161
30 | 15 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6162 | 406,163
30 | 15 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6164 | 406,165
30 | 15 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 6166 | 406,167
30 | 15 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 6168 | 406,169
30 | 15 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 6170 | 406,171
30 | 15 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 6172 | 406,173
30 | 15 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 6174 | 406,175
30 | 15 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 6176 | 406,177
30 | 15 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 6178 | 406,179
30 | 15 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 6180 | 406,181
30 | 15 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 6182 | 406,183
30 | 16 | 1 | Counter | Base | Source Function A | Set the Source CNT receiver in the Counter block. A transition on this receiver changes the count by one. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6200 | 406,201
30 | 16 | 2 | Counter | Base | Source Function B | Set the Source RST receiver in the Counter block. A transition on this receiver resets the count to preloaded value. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 6202 | 406,203
30 | 16 | 3 | Counter | Base | Source Instance A | Set the Source Instance CNT receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6204 | 406,205
30 | 16 | 4 | Counter | Base | Source Instance B | Set the Source Instance RST receiver in the Counter block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 6206 | 406,207
30 | 16 | 5 | Counter | Base | Source Zone A | Set the Source Zone A (CNT) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6208 | 406,209
30 | 16 | 6 | Counter | Base | Source Zone B | Set the Source Zone B (RST) driving this receiver. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 6210 | 406,211
30 | 16 | 7 | Counter | Base | Source Value A | Monitor the Source Value A (CNT) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6212 | 406,213
30 | 16 | 8 | Counter | Base | Source Value B | Monitor the Source Value B (RST) driving this receiver. | On (63), Off (62) |  | Enumeration | R | 6214 | 406,215
30 | 16 | 9 | Counter | Base | Function | Set direction of count. | Up (1456), Down (1457) | Up (1456) | Enumeration | R/W | 6216 | 406,217
30 | 16 | 10 | Counter | Base | Output Value | Monitor output value of counter block. | On (63), Off (62) |  | Enumeration | R | 6218 | 406,219
30 | 16 | 11 | Counter | Base | Count Active Level | Set which state changes at CNT are counted. | High (37), Low (53), Both (13) | High (37) | Enumeration | R/W | 6220 | 406,221
30 | 16 | 12 | Counter | Base | Reset Active Level | Set which state change at RST sets Count equal to Load Value. | High (37), Low (53) | High (37) | Enumeration | R/W | 6222 | 406,223
30 | 16 | 13 | Counter | Base | Load Value | Set the preloaded value for the count. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 6224 | 406,225
30 | 16 | 14 | Counter | Base | Target Value | Set the count value at which OUT turns on. | 0 to 9,999 | 9,999 | Unsigned 16-bit | R/W | 6226 | 406,227
30 | 16 | 15 | Counter | Base | Count | Monitor the count value. |  |  | Unsigned 16-bit | R | 6228 | 406,229
30 | 16 | 16 | Counter | Base | Error | Monitor the Count block for input or count errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 6230 | 406,231
30 | 16 | 17 | Counter | Base | Latching | Set the behavior for the output when Count exceeds the Target Value. | No (59), Yes (106) | No (59) | Enumeration | R/W | 6232 | 406,233
31 | 1 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15016 | 415,017
31 | 1 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15018 | 415,019
31 | 1 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15020 | 415,021
31 | 1 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15022 | 415,023
31 | 1 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15024 | 415,025
31 | 1 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15026 | 415,027
31 | 1 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 15028 | 415,029
31 | 1 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 15030 | 415,031
31 | 1 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 15032 | 415,033
31 | 1 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 15034 | 415,035
31 | 1 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 15036 | 415,037
31 | 1 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 15038 | 415,039
31 | 1 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 15040 | 415,041
31 | 1 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 15042 | 415,043
31 | 1 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 15044 | 415,045
31 | 1 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 15046 | 415,047
31 | 1 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 15048 | 415,049
31 | 1 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 15050 | 415,051
31 | 2 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15066 | 415,067
31 | 2 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15068 | 415,069
31 | 2 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15070 | 415,071
31 | 2 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15072 | 415,073
31 | 2 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15074 | 415,075
31 | 2 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15076 | 415,077
31 | 2 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 15078 | 415,079
31 | 2 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 15080 | 415,081
31 | 2 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 15082 | 415,083
31 | 2 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 15084 | 415,085
31 | 2 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 15086 | 415,087
31 | 2 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 15088 | 415,089
31 | 2 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 15090 | 415,091
31 | 2 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 15092 | 415,093
31 | 2 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 15094 | 415,095
31 | 2 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 15096 | 415,097
31 | 2 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 15098 | 415,099
31 | 2 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 15100 | 415,101
31 | 3 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15116 | 415,117
31 | 3 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15118 | 415,119
31 | 3 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15120 | 415,121
31 | 3 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15122 | 415,123
31 | 3 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15124 | 415,125
31 | 3 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15126 | 415,127
31 | 3 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 15128 | 415,129
31 | 3 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 15130 | 415,131
31 | 3 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 15132 | 415,133
31 | 3 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 15134 | 415,135
31 | 3 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 15136 | 415,137
31 | 3 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 15138 | 415,139
31 | 3 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 15140 | 415,141
31 | 3 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 15142 | 415,143
31 | 3 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 15144 | 415,145
31 | 3 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 15146 | 415,147
31 | 3 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 15148 | 415,149
31 | 3 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 15150 | 415,151
31 | 4 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15166 | 415,167
31 | 4 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15168 | 415,169
31 | 4 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15170 | 415,171
31 | 4 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15172 | 415,173
31 | 4 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15174 | 415,175
31 | 4 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15176 | 415,177
31 | 4 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 15178 | 415,179
31 | 4 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 15180 | 415,181
31 | 4 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 15182 | 415,183
31 | 4 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 15184 | 415,185
31 | 4 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 15186 | 415,187
31 | 4 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 15188 | 415,189
31 | 4 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 15190 | 415,191
31 | 4 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 15192 | 415,193
31 | 4 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 15194 | 415,195
31 | 4 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 15196 | 415,197
31 | 4 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 15198 | 415,199
31 | 4 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 15200 | 415,201
31 | 5 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15216 | 415,217
31 | 5 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15218 | 415,219
31 | 5 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15220 | 415,221
31 | 5 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15222 | 415,223
31 | 5 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15224 | 415,225
31 | 5 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15226 | 415,227
31 | 5 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 15228 | 415,229
31 | 5 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 15230 | 415,231
31 | 5 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 15232 | 415,233
31 | 5 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 15234 | 415,235
31 | 5 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 15236 | 415,237
31 | 5 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 15238 | 415,239
31 | 5 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 15240 | 415,241
31 | 5 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 15242 | 415,243
31 | 5 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 15244 | 415,245
31 | 5 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 15246 | 415,247
31 | 5 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 15248 | 415,249
31 | 5 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 15250 | 415,251
31 | 6 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15266 | 415,267
31 | 6 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15268 | 415,269
31 | 6 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15270 | 415,271
31 | 6 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15272 | 415,273
31 | 6 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15274 | 415,275
31 | 6 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15276 | 415,277
31 | 6 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 15278 | 415,279
31 | 6 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 15280 | 415,281
31 | 6 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 15282 | 415,283
31 | 6 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 15284 | 415,285
31 | 6 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 15286 | 415,287
31 | 6 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 15288 | 415,289
31 | 6 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 15290 | 415,291
31 | 6 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 15292 | 415,293
31 | 6 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 15294 | 415,295
31 | 6 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 15296 | 415,297
31 | 6 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 15298 | 415,299
31 | 6 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 15300 | 415,301
31 | 7 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15316 | 415,317
31 | 7 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15318 | 415,319
31 | 7 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15320 | 415,321
31 | 7 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15322 | 415,323
31 | 7 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15324 | 415,325
31 | 7 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15326 | 415,327
31 | 7 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 15328 | 415,329
31 | 7 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 15330 | 415,331
31 | 7 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 15332 | 415,333
31 | 7 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 15334 | 415,335
31 | 7 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 15336 | 415,337
31 | 7 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 15338 | 415,339
31 | 7 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 15340 | 415,341
31 | 7 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 15342 | 415,343
31 | 7 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 15344 | 415,345
31 | 7 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 15346 | 415,347
31 | 7 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 15348 | 415,349
31 | 7 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 15350 | 415,351
31 | 8 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15366 | 415,367
31 | 8 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15368 | 415,369
31 | 8 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15370 | 415,371
31 | 8 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15372 | 415,373
31 | 8 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15374 | 415,375
31 | 8 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15376 | 415,377
31 | 8 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 15378 | 415,379
31 | 8 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 15380 | 415,381
31 | 8 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 15382 | 415,383
31 | 8 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 15384 | 415,385
31 | 8 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 15386 | 415,387
31 | 8 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 15388 | 415,389
31 | 8 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 15390 | 415,391
31 | 8 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 15392 | 415,393
31 | 8 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 15394 | 415,395
31 | 8 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 15396 | 415,397
31 | 8 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 15398 | 415,399
31 | 8 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 15400 | 415,401
31 | 9 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15416 | 415,417
31 | 9 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15418 | 415,419
31 | 9 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15420 | 415,421
31 | 9 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15422 | 415,423
31 | 9 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15424 | 415,425
31 | 9 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15426 | 415,427
31 | 9 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 15428 | 415,429
31 | 9 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 15430 | 415,431
31 | 9 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 15432 | 415,433
31 | 9 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 15434 | 415,435
31 | 9 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 15436 | 415,437
31 | 9 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 15438 | 415,439
31 | 9 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 15440 | 415,441
31 | 9 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 15442 | 415,443
31 | 9 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 15444 | 415,445
31 | 9 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 15446 | 415,447
31 | 9 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 15448 | 415,449
31 | 9 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 15450 | 415,451
31 | 10 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15466 | 415,467
31 | 10 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15468 | 415,469
31 | 10 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15470 | 415,471
31 | 10 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15472 | 415,473
31 | 10 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15474 | 415,475
31 | 10 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15476 | 415,477
31 | 10 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 15478 | 415,479
31 | 10 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 15480 | 415,481
31 | 10 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 15482 | 415,483
31 | 10 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 15484 | 415,485
31 | 10 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 15486 | 415,487
31 | 10 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 15488 | 415,489
31 | 10 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 15490 | 415,491
31 | 10 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 15492 | 415,493
31 | 10 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 15494 | 415,495
31 | 10 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 15496 | 415,497
31 | 10 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 15498 | 415,499
31 | 10 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 15500 | 415,501
31 | 11 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15516 | 415,517
31 | 11 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15518 | 415,519
31 | 11 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15520 | 415,521
31 | 11 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15522 | 415,523
31 | 11 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15524 | 415,525
31 | 11 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15526 | 415,527
31 | 11 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 15528 | 415,529
31 | 11 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 15530 | 415,531
31 | 11 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 15532 | 415,533
31 | 11 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 15534 | 415,535
31 | 11 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 15536 | 415,537
31 | 11 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 15538 | 415,539
31 | 11 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 15540 | 415,541
31 | 11 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 15542 | 415,543
31 | 11 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 15544 | 415,545
31 | 11 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 15546 | 415,547
31 | 11 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 15548 | 415,549
31 | 11 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 15550 | 415,551
31 | 12 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15566 | 415,567
31 | 12 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15568 | 415,569
31 | 12 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15570 | 415,571
31 | 12 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15572 | 415,573
31 | 12 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15574 | 415,575
31 | 12 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15576 | 415,577
31 | 12 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 15578 | 415,579
31 | 12 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 15580 | 415,581
31 | 12 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 15582 | 415,583
31 | 12 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 15584 | 415,585
31 | 12 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 15586 | 415,587
31 | 12 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 15588 | 415,589
31 | 12 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 15590 | 415,591
31 | 12 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 15592 | 415,593
31 | 12 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 15594 | 415,595
31 | 12 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 15596 | 415,597
31 | 12 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 15598 | 415,599
31 | 12 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 15600 | 415,601
31 | 13 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15616 | 415,617
31 | 13 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15618 | 415,619
31 | 13 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15620 | 415,621
31 | 13 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15622 | 415,623
31 | 13 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15624 | 415,625
31 | 13 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15626 | 415,627
31 | 13 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 15628 | 415,629
31 | 13 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 15630 | 415,631
31 | 13 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 15632 | 415,633
31 | 13 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 15634 | 415,635
31 | 13 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 15636 | 415,637
31 | 13 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 15638 | 415,639
31 | 13 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 15640 | 415,641
31 | 13 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 15642 | 415,643
31 | 13 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 15644 | 415,645
31 | 13 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 15646 | 415,647
31 | 13 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 15648 | 415,649
31 | 13 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 15650 | 415,651
31 | 14 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15666 | 415,667
31 | 14 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15668 | 415,669
31 | 14 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15670 | 415,671
31 | 14 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15672 | 415,673
31 | 14 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15674 | 415,675
31 | 14 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15676 | 415,677
31 | 14 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 15678 | 415,679
31 | 14 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 15680 | 415,681
31 | 14 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 15682 | 415,683
31 | 14 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 15684 | 415,685
31 | 14 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 15686 | 415,687
31 | 14 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 15688 | 415,689
31 | 14 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 15690 | 415,691
31 | 14 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 15692 | 415,693
31 | 14 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 15694 | 415,695
31 | 14 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 15696 | 415,697
31 | 14 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 15698 | 415,699
31 | 14 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 15700 | 415,701
31 | 15 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15716 | 415,717
31 | 15 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15718 | 415,719
31 | 15 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15720 | 415,721
31 | 15 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15722 | 415,723
31 | 15 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15724 | 415,725
31 | 15 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15726 | 415,727
31 | 15 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 15728 | 415,729
31 | 15 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 15730 | 415,731
31 | 15 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 15732 | 415,733
31 | 15 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 15734 | 415,735
31 | 15 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 15736 | 415,737
31 | 15 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 15738 | 415,739
31 | 15 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 15740 | 415,741
31 | 15 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 15742 | 415,743
31 | 15 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 15744 | 415,745
31 | 15 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 15746 | 415,747
31 | 15 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 15748 | 415,749
31 | 15 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 15750 | 415,751
31 | 16 | 1 | Timer | Base | Source Function A | Set the Source Function A (Run) receiver in the Timer block. A transition on this receiver causes retentive timer to run, delay timer to delay, or one shot timers to produce a pulse of desired duration. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15766 | 415,767
31 | 16 | 2 | Timer | Base | Source Function B | Set the Source Function B (RST) receiver in the Timer block. A transition on this receiver resets the timer value when function is retentive timer. Receiver not used for other timer functions. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 15768 | 415,769
31 | 16 | 3 | Timer | Base | Source Instance A | Set the Source Instance A (Run) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15770 | 415,771
31 | 16 | 4 | Timer | Base | Source Instance B | Set the Source Instance B (RST) receiver in the Timer block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 15772 | 415,773
31 | 16 | 5 | Timer | Base | Source Zone A | Set the Source Zone A (Run) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15774 | 415,775
31 | 16 | 6 | Timer | Base | Source Zone B | Set the Source Zone B (RST) receiver in the Timer block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 15776 | 415,777
31 | 16 | 7 | Timer | Base | Source Value A | Monitor Source Value A (Run). | On (63), Off (62) |  | Enumeration | R | 15778 | 415,779
31 | 16 | 8 | Timer | Base | Source Value B | Monitor Source Value B (RST). | On (63), Off (62) |  | Enumeration | R | 15780 | 415,781
31 | 16 | 9 | Timer | Base | Function | Set a timer when applications require timed control of outputs or a delay to an output for a specific length of time. | Off (62), On Pulse (1471), Delay (1472), One Shot (1473), Retentive (1474) | Off (62) | Enumeration | R/W | 15782 | 415,783
31 | 16 | 10 | Timer | Base | Output Value | Monitor the output value of the Timer block. | On (63), Off (62) |  | Enumeration | R | 15784 | 415,785
31 | 16 | 11 | Timer | Base | Run Active Level | Set which state change at RUN receiver sets the output to its active state and starts the timer. | High (37), Low (53) | High (37) | Enumeration | R/W | 15786 | 415,787
31 | 16 | 12 | Timer | Base | Reset Active Level | Set which state change at RST resets the retentive timer.. | High (37), Low (53) | High (37) | Enumeration | R/W | 15788 | 415,789
31 | 16 | 13 | Timer | Base | Time | Set the cumulative amount of time the input must be active before the output becomes active for retentive timer, the amount of time to count up for one shot timer, or how long the input must be continuously active before the output becomes active for delay timer, how long the output is held in its active state once the timer is triggered by the input for on pulse timer. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 15790 | 415,791
31 | 16 | 14 | Timer | Base | Transmitter Active Level | Set the output's active state. | High (37), Low (53) | High (37) | Enumeration | R/W | 15792 | 415,793
31 | 16 | 15 | Timer | Base | Running | Monitor the timer status. | On (63), Off (62) |  | Enumeration | R | 15794 | 415,795
31 | 16 | 16 | Timer | Base | Elapsed Time | Monitor the amount of time since the timer was triggered while the timer is running. |  |  | IEEE Float | R | 15796 | 415,797
31 | 16 | 17 | Timer | Base | Output | Monitor the timer output. | On (63), Off (62) |  | Enumeration | R | 15798 | 415,799
31 | 16 | 18 | Timer | Base | Error | Monitor the Timer block for input or timer errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 15800 | 415,801
34 | 1 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 11600 | 411,601
34 | 1 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 11602 | 411,603
34 | 1 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 11604 | 411,605
34 | 1 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | IEEE Float | R | 11606 | 411,607
34 | 1 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | Enumeration | R/W | 11608 | 411,609
34 | 1 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11610 | 411,611
34 | 1 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | IEEE Float | R | 11612 | 411,613
34 | 1 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11614 | 411,615
34 | 1 | 9 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 11616 | 411,617
34 | 1 | 10 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 11618 | 411,619
34 | 1 | 11 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 11620 | 411,621
34 | 1 | 12 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 11622 | 411,623
34 | 1 | 13 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 11624 | 411,625
34 | 1 | 14 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 11626 | 411,627
34 | 1 | 15 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 11628 | 411,629
34 | 1 | 16 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 11630 | 411,631
34 | 1 | 17 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 11632 | 411,633
34 | 1 | 18 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11634 | 411,635
34 | 1 | 19 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 11636 | 411,637
34 | 1 | 20 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 11638 | 411,639
34 | 1 | 21 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 11640 | 411,641
34 | 1 | 22 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 11642 | 411,643
34 | 1 | 23 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 11644 | 411,645
34 | 1 | 24 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 11646 | 411,647
34 | 1 | 25 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 11648 | 411,649
34 | 1 | 26 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 11650 | 411,651
34 | 1 | 27 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 11652 | 411,653
34 | 1 | 28 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 11654 | 411,655
34 | 1 | 29 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 11656 | 411,657
34 | 2 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 11670 | 411,671
34 | 2 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 11672 | 411,673
34 | 2 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 11674 | 411,675
34 | 2 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | IEEE Float | R | 11676 | 411,677
34 | 2 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | Enumeration | R/W | 11678 | 411,679
34 | 2 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11680 | 411,681
34 | 2 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | IEEE Float | R | 11682 | 411,683
34 | 2 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11684 | 411,685
34 | 2 | 9 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 11686 | 411,687
34 | 2 | 10 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 11688 | 411,689
34 | 2 | 11 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 11690 | 411,691
34 | 2 | 12 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 11692 | 411,693
34 | 2 | 13 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 11694 | 411,695
34 | 2 | 14 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 11696 | 411,697
34 | 2 | 15 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 11698 | 411,699
34 | 2 | 16 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 11700 | 411,701
34 | 2 | 17 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 11702 | 411,703
34 | 2 | 18 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11704 | 411,705
34 | 2 | 19 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 11706 | 411,707
34 | 2 | 20 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 11708 | 411,709
34 | 2 | 21 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 11710 | 411,711
34 | 2 | 22 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 11712 | 411,713
34 | 2 | 23 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 11714 | 411,715
34 | 2 | 24 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 11716 | 411,717
34 | 2 | 25 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 11718 | 411,719
34 | 2 | 26 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 11720 | 411,721
34 | 2 | 27 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 11722 | 411,723
34 | 2 | 28 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 11724 | 411,725
34 | 2 | 29 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 11726 | 411,727
34 | 3 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 11740 | 411,741
34 | 3 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 11742 | 411,743
34 | 3 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 11744 | 411,745
34 | 3 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | IEEE Float | R | 11746 | 411,747
34 | 3 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | Enumeration | R/W | 11748 | 411,749
34 | 3 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11750 | 411,751
34 | 3 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | IEEE Float | R | 11752 | 411,753
34 | 3 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11754 | 411,755
34 | 3 | 9 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 11756 | 411,757
34 | 3 | 10 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 11758 | 411,759
34 | 3 | 11 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 11760 | 411,761
34 | 3 | 12 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 11762 | 411,763
34 | 3 | 13 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 11764 | 411,765
34 | 3 | 14 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 11766 | 411,767
34 | 3 | 15 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 11768 | 411,769
34 | 3 | 16 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 11770 | 411,771
34 | 3 | 17 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 11772 | 411,773
34 | 3 | 18 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11774 | 411,775
34 | 3 | 19 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 11776 | 411,777
34 | 3 | 20 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 11778 | 411,779
34 | 3 | 21 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 11780 | 411,781
34 | 3 | 22 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 11782 | 411,783
34 | 3 | 23 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 11784 | 411,785
34 | 3 | 24 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 11786 | 411,787
34 | 3 | 25 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 11788 | 411,789
34 | 3 | 26 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 11790 | 411,791
34 | 3 | 27 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 11792 | 411,793
34 | 3 | 28 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 11794 | 411,795
34 | 3 | 29 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 11796 | 411,797
34 | 4 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 11810 | 411,811
34 | 4 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 11812 | 411,813
34 | 4 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 11814 | 411,815
34 | 4 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | IEEE Float | R | 11816 | 411,817
34 | 4 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | Enumeration | R/W | 11818 | 411,819
34 | 4 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11820 | 411,821
34 | 4 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | IEEE Float | R | 11822 | 411,823
34 | 4 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11824 | 411,825
34 | 4 | 9 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 11826 | 411,827
34 | 4 | 10 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 11828 | 411,829
34 | 4 | 11 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 11830 | 411,831
34 | 4 | 12 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 11832 | 411,833
34 | 4 | 13 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 11834 | 411,835
34 | 4 | 14 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 11836 | 411,837
34 | 4 | 15 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 11838 | 411,839
34 | 4 | 16 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 11840 | 411,841
34 | 4 | 17 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 11842 | 411,843
34 | 4 | 18 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11844 | 411,845
34 | 4 | 19 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 11846 | 411,847
34 | 4 | 20 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 11848 | 411,849
34 | 4 | 21 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 11850 | 411,851
34 | 4 | 22 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 11852 | 411,853
34 | 4 | 23 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 11854 | 411,855
34 | 4 | 24 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 11856 | 411,857
34 | 4 | 25 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 11858 | 411,859
34 | 4 | 26 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 11860 | 411,861
34 | 4 | 27 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 11862 | 411,863
34 | 4 | 28 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 11864 | 411,865
34 | 4 | 29 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 11866 | 411,867
34 | 5 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 11880 | 411,881
34 | 5 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 11882 | 411,883
34 | 5 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 11884 | 411,885
34 | 5 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | IEEE Float | R | 11886 | 411,887
34 | 5 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | Enumeration | R/W | 11888 | 411,889
34 | 5 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11890 | 411,891
34 | 5 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | IEEE Float | R | 11892 | 411,893
34 | 5 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11894 | 411,895
34 | 5 | 9 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 11896 | 411,897
34 | 5 | 10 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 11898 | 411,899
34 | 5 | 11 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 11900 | 411,901
34 | 5 | 12 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 11902 | 411,903
34 | 5 | 13 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 11904 | 411,905
34 | 5 | 14 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 11906 | 411,907
34 | 5 | 15 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 11908 | 411,909
34 | 5 | 16 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 11910 | 411,911
34 | 5 | 17 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 11912 | 411,913
34 | 5 | 18 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11914 | 411,915
34 | 5 | 19 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 11916 | 411,917
34 | 5 | 20 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 11918 | 411,919
34 | 5 | 21 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 11920 | 411,921
34 | 5 | 22 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 11922 | 411,923
34 | 5 | 23 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 11924 | 411,925
34 | 5 | 24 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 11926 | 411,927
34 | 5 | 25 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 11928 | 411,929
34 | 5 | 26 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 11930 | 411,931
34 | 5 | 27 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 11932 | 411,933
34 | 5 | 28 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 11934 | 411,935
34 | 5 | 29 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 11936 | 411,937
34 | 6 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 11950 | 411,951
34 | 6 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 11952 | 411,953
34 | 6 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 11954 | 411,955
34 | 6 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | IEEE Float | R | 11956 | 411,957
34 | 6 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | Enumeration | R/W | 11958 | 411,959
34 | 6 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11960 | 411,961
34 | 6 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | IEEE Float | R | 11962 | 411,963
34 | 6 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11964 | 411,965
34 | 6 | 9 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 11966 | 411,967
34 | 6 | 10 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 11968 | 411,969
34 | 6 | 11 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 11970 | 411,971
34 | 6 | 12 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 11972 | 411,973
34 | 6 | 13 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 11974 | 411,975
34 | 6 | 14 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 11976 | 411,977
34 | 6 | 15 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 11978 | 411,979
34 | 6 | 16 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 11980 | 411,981
34 | 6 | 17 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 11982 | 411,983
34 | 6 | 18 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 11984 | 411,985
34 | 6 | 19 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 11986 | 411,987
34 | 6 | 20 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 11988 | 411,989
34 | 6 | 21 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 11990 | 411,991
34 | 6 | 22 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 11992 | 411,993
34 | 6 | 23 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 11994 | 411,995
34 | 6 | 24 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 11996 | 411,997
34 | 6 | 25 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 11998 | 411,999
34 | 6 | 26 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 12000 | 412,001
34 | 6 | 27 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 12002 | 412,003
34 | 6 | 28 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 12004 | 412,005
34 | 6 | 29 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 12006 | 412,007
34 | 7 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12020 | 412,021
34 | 7 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12022 | 412,023
34 | 7 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12024 | 412,025
34 | 7 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | IEEE Float | R | 12026 | 412,027
34 | 7 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | Enumeration | R/W | 12028 | 412,029
34 | 7 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12030 | 412,031
34 | 7 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | IEEE Float | R | 12032 | 412,033
34 | 7 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12034 | 412,035
34 | 7 | 9 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12036 | 412,037
34 | 7 | 10 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 12038 | 412,039
34 | 7 | 11 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 12040 | 412,041
34 | 7 | 12 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 12042 | 412,043
34 | 7 | 13 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 12044 | 412,045
34 | 7 | 14 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 12046 | 412,047
34 | 7 | 15 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 12048 | 412,049
34 | 7 | 16 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 12050 | 412,051
34 | 7 | 17 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 12052 | 412,053
34 | 7 | 18 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12054 | 412,055
34 | 7 | 19 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12056 | 412,057
34 | 7 | 20 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 12058 | 412,059
34 | 7 | 21 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 12060 | 412,061
34 | 7 | 22 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 12062 | 412,063
34 | 7 | 23 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 12064 | 412,065
34 | 7 | 24 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 12066 | 412,067
34 | 7 | 25 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 12068 | 412,069
34 | 7 | 26 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 12070 | 412,071
34 | 7 | 27 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 12072 | 412,073
34 | 7 | 28 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 12074 | 412,075
34 | 7 | 29 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 12076 | 412,077
34 | 8 | 1 | Linearization | Base | Source Function A | Set the Source Function A receiver in the Linearize block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 12090 | 412,091
34 | 8 | 2 | Linearization | Base | Source Instance A | Set the Source Instance A receiver in the Linearize block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 12092 | 412,093
34 | 8 | 3 | Linearization | Base | Source Zone A | Set the Source Zone A receiver in the Linearize block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 12094 | 412,095
34 | 8 | 4 | Linearization | Base | Source Value A | Monitor Source Value A. |  |  | IEEE Float | R | 12096 | 412,097
34 | 8 | 5 | Linearization | Base | Function | Set method of Linearize block to scale an analog signal according to a 10-point scaling curve and an offset. | Off (62), Interpolated (1482), Stepped (1483) | Off (62) | Enumeration | R/W | 12098 | 412,099
34 | 8 | 6 | Linearization | Base | Offset | Set an offset to the output of the Linearize block. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12100 | 412,101
34 | 8 | 7 | Linearization | Base | Output Value | Monitor the linearization output value. |  |  | IEEE Float | R | 12102 | 412,103
34 | 8 | 8 | Linearization | Base | Input Point 1 | Set the minimum input value to be scaled. This value and all lesser values are scaled to Output Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12104 | 412,105
34 | 8 | 9 | Linearization | Base | Input Point 2 | Set the second lowest input value on the scaling curve. This value is scaled to Output Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12106 | 412,107
34 | 8 | 10 | Linearization | Base | Input Point 3 | Set the third lowest input value on the scaling curve. This value is scaled to Output Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 12108 | 412,109
34 | 8 | 11 | Linearization | Base | Input Point 4 | Set the forth lowest input value on the scaling curve. This value is scaled to Output Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 12110 | 412,111
34 | 8 | 12 | Linearization | Base | Input Point 5 | Set the fifth lowest input value on the scaling curve. This value is scaled to Output Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 12112 | 412,113
34 | 8 | 13 | Linearization | Base | Input Point 6 | Set the sixth lowest input value on the scaling curve. This value is scaled to Output Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 12114 | 412,115
34 | 8 | 14 | Linearization | Base | Input Point 7 | Set the seventh lowest input value on the scaling curve. This value is scaled to Output Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 12116 | 412,117
34 | 8 | 15 | Linearization | Base | Input Point 8 | Set the eighth lowest input value on the scaling curve. This value is scaled to Output Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 12118 | 412,119
34 | 8 | 16 | Linearization | Base | Input Point 9 | Set the ninth lowest input value on the scaling curve. This value is scaled to Output Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 12120 | 412,121
34 | 8 | 17 | Linearization | Base | Input Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 12122 | 412,123
34 | 8 | 18 | Linearization | Base | Output Point 1 | Set the value to which the input is scaled when the input is equal to or less than Input Point 1. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 12124 | 412,125
34 | 8 | 19 | Linearization | Base | Output Point 2 | Set the value to which the input is scaled when the input is equal to Input Point 2. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 12126 | 412,127
34 | 8 | 20 | Linearization | Base | Output Point 3 | Set the value to which the input is scaled when the input is equal to Input Point 3. | -99,999.0 to 99,999.0 | 2.0 | IEEE Float | R/W | 12128 | 412,129
34 | 8 | 21 | Linearization | Base | Output Point 4 | Set the value to which the input is scaled when the input is equal to Input Point 4. | -99,999.0 to 99,999.0 | 3.0 | IEEE Float | R/W | 12130 | 412,131
34 | 8 | 22 | Linearization | Base | Output Point 5 | Set the value to which the input is scaled when the input is equal to Input Point 5. | -99,999.0 to 99,999.0 | 4.0 | IEEE Float | R/W | 12132 | 412,133
34 | 8 | 23 | Linearization | Base | Output Point 6 | Set the value to which the input is scaled when the input is equal to Input Point 6. | -99,999.0 to 99,999.0 | 5.0 | IEEE Float | R/W | 12134 | 412,135
34 | 8 | 24 | Linearization | Base | Output Point 7 | Set the value to which the input is scaled when the input is equal to Input Point 7. | -99,999.0 to 99,999.0 | 6.0 | IEEE Float | R/W | 12136 | 412,137
34 | 8 | 25 | Linearization | Base | Output Point 8 | Set the value to which the input is scaled when the input is equal to Input Point 8. | -99,999.0 to 99,999.0 | 7.0 | IEEE Float | R/W | 12138 | 412,139
34 | 8 | 26 | Linearization | Base | Output Point 9 | Set the value to which the input is scaled when the input is equal to Input Point 9. | -99,999.0 to 99,999.0 | 8.0 | IEEE Float | R/W | 12140 | 412,141
34 | 8 | 27 | Linearization | Base | Output Point 10 | Set the value to which the input is scaled when the input is equal to Input Point 10. | -99,999.0 to 99,999.0 | 9.0 | IEEE Float | R/W | 12142 | 412,143
34 | 8 | 28 | Linearization | Base | Error | Monitor the Linearize block for input or linearization errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 12144 | 412,145
34 | 8 | 29 | Linearization | Base | Units | Set the units of the output value. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | Enumeration | R/W | 12146 | 412,147
35 | 1 | 1 | Function | Base | Source Function A | Set the Source A for the receiver in the Special Output Function block. | None (61), Analog Input (142), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | Enumeration | R/W | 14696 | 414,697
35 | 1 | 2 | Function | Base | Source Function B | Set the Source B for the receiver in the Special Output Function block. | None (61), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | Enumeration | R/W | 14698 | 414,699
35 | 1 | 3 | Function | Base | Source Instance A | Set the Source Instance A for the receiver in the Special Output Function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14700 | 414,701
35 | 1 | 4 | Function | Base | Source Instance B | Set the Source Instance B for the receiver in the Special Output Function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14702 | 414,703
35 | 1 | 5 | Function | Base | Source Zone A | Set the Source Zone A for the receiver in the Special Output Function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14704 | 414,705
35 | 1 | 6 | Function | Base | Source Zone B | Set the Source Zone B for the receiver in the Special Output Function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14706 | 414,707
35 | 1 | 7 | Function | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 14708 | 414,709
35 | 1 | 8 | Function | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 14710 | 414,711
35 | 1 | 9 | Function | Base | Function | Set the Special Output Function block's purpose. | Off (62), Compressor Control (1506), Sequencer (1507), Motorized Valve (1508) | Off (62) | Enumeration | R/W | 14712 | 414,713
35 | 1 | 10 | Function | Base | Output Value 1 | Monitor the output value of the Special Output Function block transmitter 1. |  |  | IEEE Float | R | 14714 | 414,715
35 | 1 | 11 | Function | Base | Error | Monitor the error status for transmitter 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14716 | 414,717
35 | 1 | 12 | Function | Base | Output Value 2 | Monitor the output value of the Special Output Function block transmitter 2. |  |  | IEEE Float | R | 14718 | 414,719
35 | 1 | 13 | Function | Base | Error | Monitor the error status for transmitter 2. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14720 | 414,721
35 | 1 | 14 | Function | Base | Output Value 3 | Monitor the output value of the Special Output Function block transmitter 3. |  |  | IEEE Float | R | 14722 | 414,723
35 | 1 | 15 | Function | Base | Error | Monitor the error status for transmitter 3. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14724 | 414,725
35 | 1 | 16 | Function | Base | Output Value 4 | Monitor the output value of the Special Output Function block transmitter 4. |  |  | IEEE Float | R | 14726 | 414,727
35 | 1 | 17 | Function | Base | Error | Monitor the error status for transmitter 4. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14728 | 414,729
35 | 1 | 18 | Function | Base | Input A Turn On | Set the value of the signal at receiver A that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | IEEE Float | R/W | 14730 | 414,731
35 | 1 | 19 | Function | Base | Input A Turn Off | Set the value of the signal at receiver A that indicates there is no demand for the compressor to be on. | -100.00 to 100.00 | 5.0 | IEEE Float | R/W | 14732 | 414,733
35 | 1 | 20 | Function | Base | Input B Turn On | Set the value of the signal at receiver B that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | IEEE Float | R/W | 14734 | 414,735
35 | 1 | 21 | Function | Base | Input B Turn Off | Set the value of the signal at receiver B that indicates there is no demand for the compressor | -100.00 to 100.00 | 5.0 | IEEE Float | R/W | 14736 | 414,737
35 | 1 | 22 | Function | Base | Minimum On Time | Set the minimum amount of time the compressor must be on before it can be turned off again. | 0 to 9,999 | 20 | Unsigned 16-bit | R/W | 14738 | 414,739
35 | 1 | 23 | Function | Base | Minimum Off Time | Set the minimum amount of time the compressor is kept off before it can be turned on again. | 0 to 9,999 | 20 | Unsigned 16-bit | R/W | 14740 | 414,741
35 | 1 | 24 | Function | Base | Valve Travel Time | Set when used for motorized valve the time the valve takes to travel between fully closed and fully open. | 10 to 9,999 | 120 | Unsigned 16-bit | R/W | 14742 | 414,743
35 | 1 | 25 | Function | Base | Dead Band | Set when used for motorized valve the minimum amount for a single adjustment to the valve position. | 1.0 to 100.0 | 2.0 | IEEE Float | R/W | 14744 | 414,745
35 | 1 | 26 | Function | Base | Time Delay | Set when used for sequencer control minimum amount of time to wait between turning on one on-off output and the next. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14746 | 414,747
35 | 1 | 27 | Function | Base | Output Order | Set when sequencer the method by which outputs 2, 3 and 4 are sequenced. | Linear (1509), Progressive (1510) | Linear (1509) | Enumeration | R/W | 14748 | 414,749
35 | 1 | 28 | Function | Base | Output 1 Size | Set when sequencer the proportion of the total power that is controlled by the proportional (vernier) output. | 0 to 99,999.0 | 10.0 | IEEE Float | R/W | 14750 | 414,751
35 | 1 | 29 | Function | Base | Output 2 Size | Set when sequencer the proportion of the total power that is switched by on-off output 2. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14752 | 414,753
35 | 1 | 30 | Function | Base | Output 3 Size | Set when sequencer the proportion of the total power that is switched by on-off output 3. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14754 | 414,755
35 | 1 | 31 | Function | Base | Output 4 Size | Set when sequencer the proportion of the total power that is switched by on-off output 4. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14756 | 414,757
35 | 1 | 32 | Function | Base | Value | Monitor the Special Output Function value. | 0.000 to 100.000 |  | IEEE Float | R | 14758 | 414,759
35 | 1 | 35 | Function | Base | Off Delay | Set when used for compressor control an amount of time the output signal remains on after the Minimum On Time is satisfied and the signals at A and B indicate the compressor is no longer needed. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14764 | 414,765
35 | 2 | 1 | Function | Base | Source Function A | Set the Source A for the receiver in the Special Output Function block. | None (61), Analog Input (142), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | Enumeration | R/W | 14776 | 414,777
35 | 2 | 2 | Function | Base | Source Function B | Set the Source B for the receiver in the Special Output Function block. | None (61), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | Enumeration | R/W | 14778 | 414,779
35 | 2 | 3 | Function | Base | Source Instance A | Set the Source Instance A for the receiver in the Special Output Function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14780 | 414,781
35 | 2 | 4 | Function | Base | Source Instance B | Set the Source Instance B for the receiver in the Special Output Function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14782 | 414,783
35 | 2 | 5 | Function | Base | Source Zone A | Set the Source Zone A for the receiver in the Special Output Function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14784 | 414,785
35 | 2 | 6 | Function | Base | Source Zone B | Set the Source Zone B for the receiver in the Special Output Function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14786 | 414,787
35 | 2 | 7 | Function | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 14788 | 414,789
35 | 2 | 8 | Function | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 14790 | 414,791
35 | 2 | 9 | Function | Base | Function | Set the Special Output Function block's purpose. | Off (62), Compressor Control (1506), Sequencer (1507), Motorized Valve (1508) | Off (62) | Enumeration | R/W | 14792 | 414,793
35 | 2 | 10 | Function | Base | Output Value 1 | Monitor the output value of the Special Output Function block transmitter 1. |  |  | IEEE Float | R | 14794 | 414,795
35 | 2 | 11 | Function | Base | Error | Monitor the error status for transmitter 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14796 | 414,797
35 | 2 | 12 | Function | Base | Output Value 2 | Monitor the output value of the Special Output Function block transmitter 2. |  |  | IEEE Float | R | 14798 | 414,799
35 | 2 | 13 | Function | Base | Error | Monitor the error status for transmitter 2. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14800 | 414,801
35 | 2 | 14 | Function | Base | Output Value 3 | Monitor the output value of the Special Output Function block transmitter 3. |  |  | IEEE Float | R | 14802 | 414,803
35 | 2 | 15 | Function | Base | Error | Monitor the error status for transmitter 3. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14804 | 414,805
35 | 2 | 16 | Function | Base | Output Value 4 | Monitor the output value of the Special Output Function block transmitter 4. |  |  | IEEE Float | R | 14806 | 414,807
35 | 2 | 17 | Function | Base | Error | Monitor the error status for transmitter 4. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14808 | 414,809
35 | 2 | 18 | Function | Base | Input A Turn On | Set the value of the signal at receiver A that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | IEEE Float | R/W | 14810 | 414,811
35 | 2 | 19 | Function | Base | Input A Turn Off | Set the value of the signal at receiver A that indicates there is no demand for the compressor to be on. | -100.00 to 100.00 | 5.0 | IEEE Float | R/W | 14812 | 414,813
35 | 2 | 20 | Function | Base | Input B Turn On | Set the value of the signal at receiver B that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | IEEE Float | R/W | 14814 | 414,815
35 | 2 | 21 | Function | Base | Input B Turn Off | Set the value of the signal at receiver B that indicates there is no demand for the compressor | -100.00 to 100.00 | 5.0 | IEEE Float | R/W | 14816 | 414,817
35 | 2 | 22 | Function | Base | Minimum On Time | Set the minimum amount of time the compressor must be on before it can be turned off again. | 0 to 9,999 | 20 | Unsigned 16-bit | R/W | 14818 | 414,819
35 | 2 | 23 | Function | Base | Minimum Off Time | Set the minimum amount of time the compressor is kept off before it can be turned on again. | 0 to 9,999 | 20 | Unsigned 16-bit | R/W | 14820 | 414,821
35 | 2 | 24 | Function | Base | Valve Travel Time | Set when used for motorized valve the time the valve takes to travel between fully closed and fully open. | 10 to 9,999 | 120 | Unsigned 16-bit | R/W | 14822 | 414,823
35 | 2 | 25 | Function | Base | Dead Band | Set when used for motorized valve the minimum amount for a single adjustment to the valve position. | 1.0 to 100.0 | 2.0 | IEEE Float | R/W | 14824 | 414,825
35 | 2 | 26 | Function | Base | Time Delay | Set when used for sequencer control minimum amount of time to wait between turning on one on-off output and the next. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14826 | 414,827
35 | 2 | 27 | Function | Base | Output Order | Set when sequencer the method by which outputs 2, 3 and 4 are sequenced. | Linear (1509), Progressive (1510) | Linear (1509) | Enumeration | R/W | 14828 | 414,829
35 | 2 | 28 | Function | Base | Output 1 Size | Set when sequencer the proportion of the total power that is controlled by the proportional (vernier) output. | 0 to 99,999.0 | 10.0 | IEEE Float | R/W | 14830 | 414,831
35 | 2 | 29 | Function | Base | Output 2 Size | Set when sequencer the proportion of the total power that is switched by on-off output 2. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14832 | 414,833
35 | 2 | 30 | Function | Base | Output 3 Size | Set when sequencer the proportion of the total power that is switched by on-off output 3. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14834 | 414,835
35 | 2 | 31 | Function | Base | Output 4 Size | Set when sequencer the proportion of the total power that is switched by on-off output 4. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14836 | 414,837
35 | 2 | 32 | Function | Base | Value | Monitor the Special Output Function value. | 0.000 to 100.000 |  | IEEE Float | R | 14838 | 414,839
35 | 2 | 35 | Function | Base | Off Delay | Set when used for compressor control an amount of time the output signal remains on after the Minimum On Time is satisfied and the signals at A and B indicate the compressor is no longer needed. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14844 | 414,845
35 | 3 | 1 | Function | Base | Source Function A | Set the Source A for the receiver in the Special Output Function block. | None (61), Analog Input (142), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | Enumeration | R/W | 14856 | 414,857
35 | 3 | 2 | Function | Base | Source Function B | Set the Source B for the receiver in the Special Output Function block. | None (61), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | Enumeration | R/W | 14858 | 414,859
35 | 3 | 3 | Function | Base | Source Instance A | Set the Source Instance A for the receiver in the Special Output Function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14860 | 414,861
35 | 3 | 4 | Function | Base | Source Instance B | Set the Source Instance B for the receiver in the Special Output Function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14862 | 414,863
35 | 3 | 5 | Function | Base | Source Zone A | Set the Source Zone A for the receiver in the Special Output Function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14864 | 414,865
35 | 3 | 6 | Function | Base | Source Zone B | Set the Source Zone B for the receiver in the Special Output Function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14866 | 414,867
35 | 3 | 7 | Function | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 14868 | 414,869
35 | 3 | 8 | Function | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 14870 | 414,871
35 | 3 | 9 | Function | Base | Function | Set the Special Output Function block's purpose. | Off (62), Compressor Control (1506), Sequencer (1507), Motorized Valve (1508) | Off (62) | Enumeration | R/W | 14872 | 414,873
35 | 3 | 10 | Function | Base | Output Value 1 | Monitor the output value of the Special Output Function block transmitter 1. |  |  | IEEE Float | R | 14874 | 414,875
35 | 3 | 11 | Function | Base | Error | Monitor the error status for transmitter 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14876 | 414,877
35 | 3 | 12 | Function | Base | Output Value 2 | Monitor the output value of the Special Output Function block transmitter 2. |  |  | IEEE Float | R | 14878 | 414,879
35 | 3 | 13 | Function | Base | Error | Monitor the error status for transmitter 2. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14880 | 414,881
35 | 3 | 14 | Function | Base | Output Value 3 | Monitor the output value of the Special Output Function block transmitter 3. |  |  | IEEE Float | R | 14882 | 414,883
35 | 3 | 15 | Function | Base | Error | Monitor the error status for transmitter 3. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14884 | 414,885
35 | 3 | 16 | Function | Base | Output Value 4 | Monitor the output value of the Special Output Function block transmitter 4. |  |  | IEEE Float | R | 14886 | 414,887
35 | 3 | 17 | Function | Base | Error | Monitor the error status for transmitter 4. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14888 | 414,889
35 | 3 | 18 | Function | Base | Input A Turn On | Set the value of the signal at receiver A that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | IEEE Float | R/W | 14890 | 414,891
35 | 3 | 19 | Function | Base | Input A Turn Off | Set the value of the signal at receiver A that indicates there is no demand for the compressor to be on. | -100.00 to 100.00 | 5.0 | IEEE Float | R/W | 14892 | 414,893
35 | 3 | 20 | Function | Base | Input B Turn On | Set the value of the signal at receiver B that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | IEEE Float | R/W | 14894 | 414,895
35 | 3 | 21 | Function | Base | Input B Turn Off | Set the value of the signal at receiver B that indicates there is no demand for the compressor | -100.00 to 100.00 | 5.0 | IEEE Float | R/W | 14896 | 414,897
35 | 3 | 22 | Function | Base | Minimum On Time | Set the minimum amount of time the compressor must be on before it can be turned off again. | 0 to 9,999 | 20 | Unsigned 16-bit | R/W | 14898 | 414,899
35 | 3 | 23 | Function | Base | Minimum Off Time | Set the minimum amount of time the compressor is kept off before it can be turned on again. | 0 to 9,999 | 20 | Unsigned 16-bit | R/W | 14900 | 414,901
35 | 3 | 24 | Function | Base | Valve Travel Time | Set when used for motorized valve the time the valve takes to travel between fully closed and fully open. | 10 to 9,999 | 120 | Unsigned 16-bit | R/W | 14902 | 414,903
35 | 3 | 25 | Function | Base | Dead Band | Set when used for motorized valve the minimum amount for a single adjustment to the valve position. | 1.0 to 100.0 | 2.0 | IEEE Float | R/W | 14904 | 414,905
35 | 3 | 26 | Function | Base | Time Delay | Set when used for sequencer control minimum amount of time to wait between turning on one on-off output and the next. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14906 | 414,907
35 | 3 | 27 | Function | Base | Output Order | Set when sequencer the method by which outputs 2, 3 and 4 are sequenced. | Linear (1509), Progressive (1510) | Linear (1509) | Enumeration | R/W | 14908 | 414,909
35 | 3 | 28 | Function | Base | Output 1 Size | Set when sequencer the proportion of the total power that is controlled by the proportional (vernier) output. | 0 to 99,999.0 | 10.0 | IEEE Float | R/W | 14910 | 414,911
35 | 3 | 29 | Function | Base | Output 2 Size | Set when sequencer the proportion of the total power that is switched by on-off output 2. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14912 | 414,913
35 | 3 | 30 | Function | Base | Output 3 Size | Set when sequencer the proportion of the total power that is switched by on-off output 3. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14914 | 414,915
35 | 3 | 31 | Function | Base | Output 4 Size | Set when sequencer the proportion of the total power that is switched by on-off output 4. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14916 | 414,917
35 | 3 | 32 | Function | Base | Value | Monitor the Special Output Function value. | 0.000 to 100.000 |  | IEEE Float | R | 14918 | 414,919
35 | 3 | 35 | Function | Base | Off Delay | Set when used for compressor control an amount of time the output signal remains on after the Minimum On Time is satisfied and the signals at A and B indicate the compressor is no longer needed. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14924 | 414,925
35 | 4 | 1 | Function | Base | Source Function A | Set the Source A for the receiver in the Special Output Function block. | None (61), Analog Input (142), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | Enumeration | R/W | 14936 | 414,937
35 | 4 | 2 | Function | Base | Source Function B | Set the Source B for the receiver in the Special Output Function block. | None (61), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Variable (245), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796) | None (61) | Enumeration | R/W | 14938 | 414,939
35 | 4 | 3 | Function | Base | Source Instance A | Set the Source Instance A for the receiver in the Special Output Function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14940 | 414,941
35 | 4 | 4 | Function | Base | Source Instance B | Set the Source Instance B for the receiver in the Special Output Function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 14942 | 414,943
35 | 4 | 5 | Function | Base | Source Zone A | Set the Source Zone A for the receiver in the Special Output Function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14944 | 414,945
35 | 4 | 6 | Function | Base | Source Zone B | Set the Source Zone B for the receiver in the Special Output Function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 14946 | 414,947
35 | 4 | 7 | Function | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | IEEE Float | R | 14948 | 414,949
35 | 4 | 8 | Function | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | IEEE Float | R | 14950 | 414,951
35 | 4 | 9 | Function | Base | Function | Set the Special Output Function block's purpose. | Off (62), Compressor Control (1506), Sequencer (1507), Motorized Valve (1508) | Off (62) | Enumeration | R/W | 14952 | 414,953
35 | 4 | 10 | Function | Base | Output Value 1 | Monitor the output value of the Special Output Function block transmitter 1. |  |  | IEEE Float | R | 14954 | 414,955
35 | 4 | 11 | Function | Base | Error | Monitor the error status for transmitter 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14956 | 414,957
35 | 4 | 12 | Function | Base | Output Value 2 | Monitor the output value of the Special Output Function block transmitter 2. |  |  | IEEE Float | R | 14958 | 414,959
35 | 4 | 13 | Function | Base | Error | Monitor the error status for transmitter 2. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14960 | 414,961
35 | 4 | 14 | Function | Base | Output Value 3 | Monitor the output value of the Special Output Function block transmitter 3. |  |  | IEEE Float | R | 14962 | 414,963
35 | 4 | 15 | Function | Base | Error | Monitor the error status for transmitter 3. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14964 | 414,965
35 | 4 | 16 | Function | Base | Output Value 4 | Monitor the output value of the Special Output Function block transmitter 4. |  |  | IEEE Float | R | 14966 | 414,967
35 | 4 | 17 | Function | Base | Error | Monitor the error status for transmitter 4. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 14968 | 414,969
35 | 4 | 18 | Function | Base | Input A Turn On | Set the value of the signal at receiver A that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | IEEE Float | R/W | 14970 | 414,971
35 | 4 | 19 | Function | Base | Input A Turn Off | Set the value of the signal at receiver A that indicates there is no demand for the compressor to be on. | -100.00 to 100.00 | 5.0 | IEEE Float | R/W | 14972 | 414,973
35 | 4 | 20 | Function | Base | Input B Turn On | Set the value of the signal at receiver B that indicates demand for the compressor to turn on. | -100.00 to 100.00 | 0.0 | IEEE Float | R/W | 14974 | 414,975
35 | 4 | 21 | Function | Base | Input B Turn Off | Set the value of the signal at receiver B that indicates there is no demand for the compressor | -100.00 to 100.00 | 5.0 | IEEE Float | R/W | 14976 | 414,977
35 | 4 | 22 | Function | Base | Minimum On Time | Set the minimum amount of time the compressor must be on before it can be turned off again. | 0 to 9,999 | 20 | Unsigned 16-bit | R/W | 14978 | 414,979
35 | 4 | 23 | Function | Base | Minimum Off Time | Set the minimum amount of time the compressor is kept off before it can be turned on again. | 0 to 9,999 | 20 | Unsigned 16-bit | R/W | 14980 | 414,981
35 | 4 | 24 | Function | Base | Valve Travel Time | Set when used for motorized valve the time the valve takes to travel between fully closed and fully open. | 10 to 9,999 | 120 | Unsigned 16-bit | R/W | 14982 | 414,983
35 | 4 | 25 | Function | Base | Dead Band | Set when used for motorized valve the minimum amount for a single adjustment to the valve position. | 1.0 to 100.0 | 2.0 | IEEE Float | R/W | 14984 | 414,985
35 | 4 | 26 | Function | Base | Time Delay | Set when used for sequencer control minimum amount of time to wait between turning on one on-off output and the next. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 14986 | 414,987
35 | 4 | 27 | Function | Base | Output Order | Set when sequencer the method by which outputs 2, 3 and 4 are sequenced. | Linear (1509), Progressive (1510) | Linear (1509) | Enumeration | R/W | 14988 | 414,989
35 | 4 | 28 | Function | Base | Output 1 Size | Set when sequencer the proportion of the total power that is controlled by the proportional (vernier) output. | 0 to 99,999.0 | 10.0 | IEEE Float | R/W | 14990 | 414,991
35 | 4 | 29 | Function | Base | Output 2 Size | Set when sequencer the proportion of the total power that is switched by on-off output 2. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14992 | 414,993
35 | 4 | 30 | Function | Base | Output 3 Size | Set when sequencer the proportion of the total power that is switched by on-off output 3. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14994 | 414,995
35 | 4 | 31 | Function | Base | Output 4 Size | Set when sequencer the proportion of the total power that is switched by on-off output 4. | 0 to 99,999.0 | 0.0 | IEEE Float | R/W | 14996 | 414,997
35 | 4 | 32 | Function | Base | Value | Monitor the Special Output Function value. | 0.000 to 100.000 |  | IEEE Float | R | 14998 | 414,999
35 | 4 | 35 | Function | Base | Off Delay | Set when used for compressor control an amount of time the output signal remains on after the Minimum On Time is satisfied and the signals at A and B indicate the compressor is no longer needed. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 15004 | 415,005
36 | 1 | 1 | Real Time Clock | Base | Time of Day | Monitor the time of day in seconds. | 0 to 86,399 |  | Unsigned 32-bit | R | 14660 | 414,661
36 | 1 | 3 | Real Time Clock | Base | Hours | Set the time of day (hours portion). | 0 to 23 |  | Unsigned 8-bit | R/W | 14664 | 414,665
36 | 1 | 4 | Real Time Clock | Base | Minutes | Set the time of day (minutes portion). | 0 to 59 |  | Unsigned 8-bit | R/W | 14666 | 414,667
36 | 1 | 5 | Real Time Clock | Base | Seconds | Set the time of day (seconds portion). | 0 to 59 |  | Unsigned 8-bit | R/W | 14668 | 414,669
36 | 1 | 6 | Real Time Clock | Base | Month | Set the time of day (month portion). | 1 to 12 |  | Unsigned 8-bit | R/W | 14670 | 414,671
36 | 1 | 7 | Real Time Clock | Base | Date | Set the time of day (date portion). | 1 to 31 |  | Unsigned 8-bit | R/W | 14672 | 414,673
36 | 1 | 8 | Real Time Clock | Base | Year | Set the time of day (year portion). | 2,008 to 2,100 |  | Unsigned 16-bit | R/W | 14674 | 414,675
37 | 1 | 2 | Data Logging | Base | Status | Monitor the datalogging status. | Not Ready (1660), OK (138), No Memory (1637), USB (1653) |  | Enumeration | R | 42348 | 442,349
37 | 1 | 3 | Data Logging | Base | Memory Full Action | Set action to take when memory is full. | Stop (1638), Overwrite (1639) | Stop (1638) | Enumeration | R/W | 42350 | 442,351
37 | 1 | 4 | Data Logging | Base | Available Logging Memory (MB) | Monitor the available memory usable for datalogging. | 0 to 4,294,967,295 |  | Unsigned 32-bit | R | 42352 | 442,353
37 | 1 | 5 | Data Logging | Base | Available Logging Time (Hours) | Monitor the time remaining before memory is full. | 0 to 4,294,967,295 |  | Unsigned 32-bit | R | 42354 | 442,355
37 | 1 | 6 | Data Logging | Base | Source Function A | Set source to trigger logging action. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42356 | 442,357
37 | 1 | 7 | Data Logging | Base | Source Instance A | Set source instance to trigger logging action. | 1 to 24 | 1 | Unsigned 8-bit | R/W | 42358 | 442,359
37 | 1 | 9 | Data Logging | Base | Source Value A | Monitor state of trigger for logging action. | Off (62), On (63) |  | Enumeration | R | 42362 | 442,363
37 | 1 | 12 | Data Logging | Base | Logging Status | Monitor data log action. | Recording (1990), Not Recording (1991) | Not Recording (1991) | Enumeration | R | 42368 | 442,369
37 | 1 | 14 | Data Logging | Base | File Size Limit (MB) | Set size of data log file. | 1 to 4,294,967,295 | 0 | Unsigned 32-bit | R/W | 42372 | 442,373
37 | 1 | 19 | Data Logging | Base | Date Format | Set date format recorded on each record. | MM/DD/YYYY (1631), DD/MM/YYYY (1632) | MM/DD/YYYY (1631) | Enumeration | R/W | 42382 | 442,383
37 | 1 | 20 | Data Logging | Base | Time Format | Set time format recorded on each record. | 12 Hour (1966), 24 Hour (1967) | 12 Hour (1966) | Enumeration | R/W | 42384 | 442,385
37 | 1 | 21 | Data Logging | Base | Log Action | Set data log action. | None (61), Start (1782), Stop (1638) |  | Enumeration | R/W | 42386 | 442,387
37 | 1 | 22 | Data Logging | Base | Log Interval | Set the interval at which to log data. | 0.1 sec (1971), 0.2 sec (1972), 0.5 sec (1973), 1 sec (1974), 2 sec (1975), 5 sec (1976), 10 sec (1977), 15 sec (1978), 30 sec (1979), 1 min (1980), 2 min (1985), 5 min (1981), 10 min (1986), 15 min (1987), 30 min (1988), 60 min (1989) | 5 min (1981) | Enumeration | R/W | 42388 | 442,389
37 | 1 | 23 | Data Logging | Base | Log To | Set location to store the data log file. | Internal (2057), USB Device (2058) | Internal (2057) | Enumeration | R/W | 42390 | 442,391
37 | 1 | 24 | Data Logging | Base | File Type | Set file type of the data log file. | Encrypted (2064), CSV (2063), Both (13) | Encrypted (2064) | Enumeration | R/W | 42392 | 442,393
37 | 1 | 32 | Data Logging | Base | Remote Transfer Interval In Hours | Set time before auto transfer occurs. | 0 to 65,535 | 0 | Unsigned 16-bit | R/W | 42398 | 442,399
37 | 1 | 33 | Data Logging | Base | Remote Transfer on Percent full | Set when to perform auto transfer based on memory fill. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 42400 | 442,401
37 | 1 | 34 | Data Logging | Base | Transfer Files Now by | Set to trigger data log transfer from internal memory to remote location.. | None (61), TFTP (2085), Samba (2086) | None (61) | Enumeration | R/W | 42402 | 442,403
37 | 1 | 38 | Data Logging | Base | Auto Transfer Type | Set where auto transfer should store files. | None (61), TFTP (2085), Samba (2086), USB (1653) | None (61) | Enumeration | R/W | 42404 | 442,405
39 | 1 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42406 | 442,407
39 | 1 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42408 | 442,409
39 | 1 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42412 | 442,413
39 | 1 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42414 | 442,415
39 | 1 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42416 | 442,417
39 | 1 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42418 | 442,419
39 | 1 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42420 | 442,421
39 | 1 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42422 | 442,423
39 | 1 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42424 | 442,425
39 | 1 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42426 | 442,427
39 | 2 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42432 | 442,433
39 | 2 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42434 | 442,435
39 | 2 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42438 | 442,439
39 | 2 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42440 | 442,441
39 | 2 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42442 | 442,443
39 | 2 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42444 | 442,445
39 | 2 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42446 | 442,447
39 | 2 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42448 | 442,449
39 | 2 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42450 | 442,451
39 | 2 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42452 | 442,453
39 | 3 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42458 | 442,459
39 | 3 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42460 | 442,461
39 | 3 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42464 | 442,465
39 | 3 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42466 | 442,467
39 | 3 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42468 | 442,469
39 | 3 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42470 | 442,471
39 | 3 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42472 | 442,473
39 | 3 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42474 | 442,475
39 | 3 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42476 | 442,477
39 | 3 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42478 | 442,479
39 | 4 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42484 | 442,485
39 | 4 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42486 | 442,487
39 | 4 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42490 | 442,491
39 | 4 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42492 | 442,493
39 | 4 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42494 | 442,495
39 | 4 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42496 | 442,497
39 | 4 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42498 | 442,499
39 | 4 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42500 | 442,501
39 | 4 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42502 | 442,503
39 | 4 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42504 | 442,505
39 | 5 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42510 | 442,511
39 | 5 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42512 | 442,513
39 | 5 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42516 | 442,517
39 | 5 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42518 | 442,519
39 | 5 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42520 | 442,521
39 | 5 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42522 | 442,523
39 | 5 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42524 | 442,525
39 | 5 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42526 | 442,527
39 | 5 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42528 | 442,529
39 | 5 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42530 | 442,531
39 | 6 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42536 | 442,537
39 | 6 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42538 | 442,539
39 | 6 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42542 | 442,543
39 | 6 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42544 | 442,545
39 | 6 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42546 | 442,547
39 | 6 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42548 | 442,549
39 | 6 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42550 | 442,551
39 | 6 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42552 | 442,553
39 | 6 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42554 | 442,555
39 | 6 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42556 | 442,557
39 | 7 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42562 | 442,563
39 | 7 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42564 | 442,565
39 | 7 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42568 | 442,569
39 | 7 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42570 | 442,571
39 | 7 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42572 | 442,573
39 | 7 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42574 | 442,575
39 | 7 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42576 | 442,577
39 | 7 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42578 | 442,579
39 | 7 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42580 | 442,581
39 | 7 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42582 | 442,583
39 | 8 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42588 | 442,589
39 | 8 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42590 | 442,591
39 | 8 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42594 | 442,595
39 | 8 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42596 | 442,597
39 | 8 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42598 | 442,599
39 | 8 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42600 | 442,601
39 | 8 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42602 | 442,603
39 | 8 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42604 | 442,605
39 | 8 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42606 | 442,607
39 | 8 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42608 | 442,609
39 | 9 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42614 | 442,615
39 | 9 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42616 | 442,617
39 | 9 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42620 | 442,621
39 | 9 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42622 | 442,623
39 | 9 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42624 | 442,625
39 | 9 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42626 | 442,627
39 | 9 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42628 | 442,629
39 | 9 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42630 | 442,631
39 | 9 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42632 | 442,633
39 | 9 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42634 | 442,635
39 | 10 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42640 | 442,641
39 | 10 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42642 | 442,643
39 | 10 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42646 | 442,647
39 | 10 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42648 | 442,649
39 | 10 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42650 | 442,651
39 | 10 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42652 | 442,653
39 | 10 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42654 | 442,655
39 | 10 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42656 | 442,657
39 | 10 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42658 | 442,659
39 | 10 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42660 | 442,661
39 | 11 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42666 | 442,667
39 | 11 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42668 | 442,669
39 | 11 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42672 | 442,673
39 | 11 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42674 | 442,675
39 | 11 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42676 | 442,677
39 | 11 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42678 | 442,679
39 | 11 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42680 | 442,681
39 | 11 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42682 | 442,683
39 | 11 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42684 | 442,685
39 | 11 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42686 | 442,687
39 | 12 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42692 | 442,693
39 | 12 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42694 | 442,695
39 | 12 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42698 | 442,699
39 | 12 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42700 | 442,701
39 | 12 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42702 | 442,703
39 | 12 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42704 | 442,705
39 | 12 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42706 | 442,707
39 | 12 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42708 | 442,709
39 | 12 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42710 | 442,711
39 | 12 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42712 | 442,713
39 | 13 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42718 | 442,719
39 | 13 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42720 | 442,721
39 | 13 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42724 | 442,725
39 | 13 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42726 | 442,727
39 | 13 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42728 | 442,729
39 | 13 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42730 | 442,731
39 | 13 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42732 | 442,733
39 | 13 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42734 | 442,735
39 | 13 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42736 | 442,737
39 | 13 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42738 | 442,739
39 | 14 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42744 | 442,745
39 | 14 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42746 | 442,747
39 | 14 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42750 | 442,751
39 | 14 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42752 | 442,753
39 | 14 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42754 | 442,755
39 | 14 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42756 | 442,757
39 | 14 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42758 | 442,759
39 | 14 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42760 | 442,761
39 | 14 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42762 | 442,763
39 | 14 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42764 | 442,765
39 | 15 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42770 | 442,771
39 | 15 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42772 | 442,773
39 | 15 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42776 | 442,777
39 | 15 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42778 | 442,779
39 | 15 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42780 | 442,781
39 | 15 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42782 | 442,783
39 | 15 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42784 | 442,785
39 | 15 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42786 | 442,787
39 | 15 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42788 | 442,789
39 | 15 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42790 | 442,791
39 | 16 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42796 | 442,797
39 | 16 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42798 | 442,799
39 | 16 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42802 | 442,803
39 | 16 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42804 | 442,805
39 | 16 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42806 | 442,807
39 | 16 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42808 | 442,809
39 | 16 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42810 | 442,811
39 | 16 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42812 | 442,813
39 | 16 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42814 | 442,815
39 | 16 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42816 | 442,817
39 | 17 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42822 | 442,823
39 | 17 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42824 | 442,825
39 | 17 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42828 | 442,829
39 | 17 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42830 | 442,831
39 | 17 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42832 | 442,833
39 | 17 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42834 | 442,835
39 | 17 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42836 | 442,837
39 | 17 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42838 | 442,839
39 | 17 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42840 | 442,841
39 | 17 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42842 | 442,843
39 | 18 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42848 | 442,849
39 | 18 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42850 | 442,851
39 | 18 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42854 | 442,855
39 | 18 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42856 | 442,857
39 | 18 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42858 | 442,859
39 | 18 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42860 | 442,861
39 | 18 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42862 | 442,863
39 | 18 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42864 | 442,865
39 | 18 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42866 | 442,867
39 | 18 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42868 | 442,869
39 | 19 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42874 | 442,875
39 | 19 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42876 | 442,877
39 | 19 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42880 | 442,881
39 | 19 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42882 | 442,883
39 | 19 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42884 | 442,885
39 | 19 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42886 | 442,887
39 | 19 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42888 | 442,889
39 | 19 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42890 | 442,891
39 | 19 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42892 | 442,893
39 | 19 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42894 | 442,895
39 | 20 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42900 | 442,901
39 | 20 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42902 | 442,903
39 | 20 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42906 | 442,907
39 | 20 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42908 | 442,909
39 | 20 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42910 | 442,911
39 | 20 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42912 | 442,913
39 | 20 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42914 | 442,915
39 | 20 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42916 | 442,917
39 | 20 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42918 | 442,919
39 | 20 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42920 | 442,921
39 | 21 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42926 | 442,927
39 | 21 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42928 | 442,929
39 | 21 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42932 | 442,933
39 | 21 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42934 | 442,935
39 | 21 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42936 | 442,937
39 | 21 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42938 | 442,939
39 | 21 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42940 | 442,941
39 | 21 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42942 | 442,943
39 | 21 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42944 | 442,945
39 | 21 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42946 | 442,947
39 | 22 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42952 | 442,953
39 | 22 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42954 | 442,955
39 | 22 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42958 | 442,959
39 | 22 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42960 | 442,961
39 | 22 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42962 | 442,963
39 | 22 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42964 | 442,965
39 | 22 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42966 | 442,967
39 | 22 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42968 | 442,969
39 | 22 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42970 | 442,971
39 | 22 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42972 | 442,973
39 | 23 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 42978 | 442,979
39 | 23 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 42980 | 442,981
39 | 23 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 42984 | 442,985
39 | 23 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42986 | 442,987
39 | 23 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 42988 | 442,989
39 | 23 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 42990 | 442,991
39 | 23 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 42992 | 442,993
39 | 23 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 42994 | 442,995
39 | 23 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42996 | 442,997
39 | 23 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 42998 | 442,999
39 | 24 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43004 | 443,005
39 | 24 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43006 | 443,007
39 | 24 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43010 | 443,011
39 | 24 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43012 | 443,013
39 | 24 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43014 | 443,015
39 | 24 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43016 | 443,017
39 | 24 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43018 | 443,019
39 | 24 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43020 | 443,021
39 | 24 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43022 | 443,023
39 | 24 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43024 | 443,025
39 | 25 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43030 | 443,031
39 | 25 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43032 | 443,033
39 | 25 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43036 | 443,037
39 | 25 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43038 | 443,039
39 | 25 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43040 | 443,041
39 | 25 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43042 | 443,043
39 | 25 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43044 | 443,045
39 | 25 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43046 | 443,047
39 | 25 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43048 | 443,049
39 | 25 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43050 | 443,051
39 | 26 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43056 | 443,057
39 | 26 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43058 | 443,059
39 | 26 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43062 | 443,063
39 | 26 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43064 | 443,065
39 | 26 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43066 | 443,067
39 | 26 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43068 | 443,069
39 | 26 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43070 | 443,071
39 | 26 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43072 | 443,073
39 | 26 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43074 | 443,075
39 | 26 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43076 | 443,077
39 | 27 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43082 | 443,083
39 | 27 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43084 | 443,085
39 | 27 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43088 | 443,089
39 | 27 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43090 | 443,091
39 | 27 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43092 | 443,093
39 | 27 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43094 | 443,095
39 | 27 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43096 | 443,097
39 | 27 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43098 | 443,099
39 | 27 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43100 | 443,101
39 | 27 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43102 | 443,103
39 | 28 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43108 | 443,109
39 | 28 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43110 | 443,111
39 | 28 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43114 | 443,115
39 | 28 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43116 | 443,117
39 | 28 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43118 | 443,119
39 | 28 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43120 | 443,121
39 | 28 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43122 | 443,123
39 | 28 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43124 | 443,125
39 | 28 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43126 | 443,127
39 | 28 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43128 | 443,129
39 | 29 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43134 | 443,135
39 | 29 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43136 | 443,137
39 | 29 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43140 | 443,141
39 | 29 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43142 | 443,143
39 | 29 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43144 | 443,145
39 | 29 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43146 | 443,147
39 | 29 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43148 | 443,149
39 | 29 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43150 | 443,151
39 | 29 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43152 | 443,153
39 | 29 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43154 | 443,155
39 | 30 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43160 | 443,161
39 | 30 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43162 | 443,163
39 | 30 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43166 | 443,167
39 | 30 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43168 | 443,169
39 | 30 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43170 | 443,171
39 | 30 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43172 | 443,173
39 | 30 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43174 | 443,175
39 | 30 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43176 | 443,177
39 | 30 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43178 | 443,179
39 | 30 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43180 | 443,181
39 | 31 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43186 | 443,187
39 | 31 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43188 | 443,189
39 | 31 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43192 | 443,193
39 | 31 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43194 | 443,195
39 | 31 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43196 | 443,197
39 | 31 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43198 | 443,199
39 | 31 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43200 | 443,201
39 | 31 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43202 | 443,203
39 | 31 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43204 | 443,205
39 | 31 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43206 | 443,207
39 | 32 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43212 | 443,213
39 | 32 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43214 | 443,215
39 | 32 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43218 | 443,219
39 | 32 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43220 | 443,221
39 | 32 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43222 | 443,223
39 | 32 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43224 | 443,225
39 | 32 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43226 | 443,227
39 | 32 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43228 | 443,229
39 | 32 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43230 | 443,231
39 | 32 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43232 | 443,233
39 | 33 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43238 | 443,239
39 | 33 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43240 | 443,241
39 | 33 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43244 | 443,245
39 | 33 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43246 | 443,247
39 | 33 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43248 | 443,249
39 | 33 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43250 | 443,251
39 | 33 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43252 | 443,253
39 | 33 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43254 | 443,255
39 | 33 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43256 | 443,257
39 | 33 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43258 | 443,259
39 | 34 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43264 | 443,265
39 | 34 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43266 | 443,267
39 | 34 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43270 | 443,271
39 | 34 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43272 | 443,273
39 | 34 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43274 | 443,275
39 | 34 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43276 | 443,277
39 | 34 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43278 | 443,279
39 | 34 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43280 | 443,281
39 | 34 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43282 | 443,283
39 | 34 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43284 | 443,285
39 | 35 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43290 | 443,291
39 | 35 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43292 | 443,293
39 | 35 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43296 | 443,297
39 | 35 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43298 | 443,299
39 | 35 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43300 | 443,301
39 | 35 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43302 | 443,303
39 | 35 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43304 | 443,305
39 | 35 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43306 | 443,307
39 | 35 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43308 | 443,309
39 | 35 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43310 | 443,311
39 | 36 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43316 | 443,317
39 | 36 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43318 | 443,319
39 | 36 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43322 | 443,323
39 | 36 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43324 | 443,325
39 | 36 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43326 | 443,327
39 | 36 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43328 | 443,329
39 | 36 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43330 | 443,331
39 | 36 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43332 | 443,333
39 | 36 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43334 | 443,335
39 | 36 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43336 | 443,337
39 | 37 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43342 | 443,343
39 | 37 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43344 | 443,345
39 | 37 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43348 | 443,349
39 | 37 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43350 | 443,351
39 | 37 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43352 | 443,353
39 | 37 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43354 | 443,355
39 | 37 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43356 | 443,357
39 | 37 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43358 | 443,359
39 | 37 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43360 | 443,361
39 | 37 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43362 | 443,363
39 | 38 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43368 | 443,369
39 | 38 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43370 | 443,371
39 | 38 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43374 | 443,375
39 | 38 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43376 | 443,377
39 | 38 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43378 | 443,379
39 | 38 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43380 | 443,381
39 | 38 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43382 | 443,383
39 | 38 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43384 | 443,385
39 | 38 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43386 | 443,387
39 | 38 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43388 | 443,389
39 | 39 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43394 | 443,395
39 | 39 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43396 | 443,397
39 | 39 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43400 | 443,401
39 | 39 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43402 | 443,403
39 | 39 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43404 | 443,405
39 | 39 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43406 | 443,407
39 | 39 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43408 | 443,409
39 | 39 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43410 | 443,411
39 | 39 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43412 | 443,413
39 | 39 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43414 | 443,415
39 | 40 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43420 | 443,421
39 | 40 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43422 | 443,423
39 | 40 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43426 | 443,427
39 | 40 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43428 | 443,429
39 | 40 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43430 | 443,431
39 | 40 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43432 | 443,433
39 | 40 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43434 | 443,435
39 | 40 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43436 | 443,437
39 | 40 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43438 | 443,439
39 | 40 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43440 | 443,441
39 | 41 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43446 | 443,447
39 | 41 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43448 | 443,449
39 | 41 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43452 | 443,453
39 | 41 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43454 | 443,455
39 | 41 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43456 | 443,457
39 | 41 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43458 | 443,459
39 | 41 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43460 | 443,461
39 | 41 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43462 | 443,463
39 | 41 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43464 | 443,465
39 | 41 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43466 | 443,467
39 | 42 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43472 | 443,473
39 | 42 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43474 | 443,475
39 | 42 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43478 | 443,479
39 | 42 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43480 | 443,481
39 | 42 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43482 | 443,483
39 | 42 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43484 | 443,485
39 | 42 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43486 | 443,487
39 | 42 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43488 | 443,489
39 | 42 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43490 | 443,491
39 | 42 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43492 | 443,493
39 | 43 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43498 | 443,499
39 | 43 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43500 | 443,501
39 | 43 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43504 | 443,505
39 | 43 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43506 | 443,507
39 | 43 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43508 | 443,509
39 | 43 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43510 | 443,511
39 | 43 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43512 | 443,513
39 | 43 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43514 | 443,515
39 | 43 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43516 | 443,517
39 | 43 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43518 | 443,519
39 | 44 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43524 | 443,525
39 | 44 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43526 | 443,527
39 | 44 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43530 | 443,531
39 | 44 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43532 | 443,533
39 | 44 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43534 | 443,535
39 | 44 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43536 | 443,537
39 | 44 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43538 | 443,539
39 | 44 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43540 | 443,541
39 | 44 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43542 | 443,543
39 | 44 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43544 | 443,545
39 | 45 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43550 | 443,551
39 | 45 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43552 | 443,553
39 | 45 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43556 | 443,557
39 | 45 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43558 | 443,559
39 | 45 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43560 | 443,561
39 | 45 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43562 | 443,563
39 | 45 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43564 | 443,565
39 | 45 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43566 | 443,567
39 | 45 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43568 | 443,569
39 | 45 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43570 | 443,571
39 | 46 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43576 | 443,577
39 | 46 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43578 | 443,579
39 | 46 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43582 | 443,583
39 | 46 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43584 | 443,585
39 | 46 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43586 | 443,587
39 | 46 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43588 | 443,589
39 | 46 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43590 | 443,591
39 | 46 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43592 | 443,593
39 | 46 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43594 | 443,595
39 | 46 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43596 | 443,597
39 | 47 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43602 | 443,603
39 | 47 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43604 | 443,605
39 | 47 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43608 | 443,609
39 | 47 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43610 | 443,611
39 | 47 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43612 | 443,613
39 | 47 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43614 | 443,615
39 | 47 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43616 | 443,617
39 | 47 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43618 | 443,619
39 | 47 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43620 | 443,621
39 | 47 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43622 | 443,623
39 | 48 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43628 | 443,629
39 | 48 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43630 | 443,631
39 | 48 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43634 | 443,635
39 | 48 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43636 | 443,637
39 | 48 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43638 | 443,639
39 | 48 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43640 | 443,641
39 | 48 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43642 | 443,643
39 | 48 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43644 | 443,645
39 | 48 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43646 | 443,647
39 | 48 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43648 | 443,649
39 | 49 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43654 | 443,655
39 | 49 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43656 | 443,657
39 | 49 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43660 | 443,661
39 | 49 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43662 | 443,663
39 | 49 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43664 | 443,665
39 | 49 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43666 | 443,667
39 | 49 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43668 | 443,669
39 | 49 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43670 | 443,671
39 | 49 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43672 | 443,673
39 | 49 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43674 | 443,675
39 | 50 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43680 | 443,681
39 | 50 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43682 | 443,683
39 | 50 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43686 | 443,687
39 | 50 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43688 | 443,689
39 | 50 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43690 | 443,691
39 | 50 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43692 | 443,693
39 | 50 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43694 | 443,695
39 | 50 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43696 | 443,697
39 | 50 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43698 | 443,699
39 | 50 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43700 | 443,701
39 | 51 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43706 | 443,707
39 | 51 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43708 | 443,709
39 | 51 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43712 | 443,713
39 | 51 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43714 | 443,715
39 | 51 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43716 | 443,717
39 | 51 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43718 | 443,719
39 | 51 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43720 | 443,721
39 | 51 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43722 | 443,723
39 | 51 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43724 | 443,725
39 | 51 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43726 | 443,727
39 | 52 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43732 | 443,733
39 | 52 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43734 | 443,735
39 | 52 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43738 | 443,739
39 | 52 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43740 | 443,741
39 | 52 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43742 | 443,743
39 | 52 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43744 | 443,745
39 | 52 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43746 | 443,747
39 | 52 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43748 | 443,749
39 | 52 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43750 | 443,751
39 | 52 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43752 | 443,753
39 | 53 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43758 | 443,759
39 | 53 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43760 | 443,761
39 | 53 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43764 | 443,765
39 | 53 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43766 | 443,767
39 | 53 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43768 | 443,769
39 | 53 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43770 | 443,771
39 | 53 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43772 | 443,773
39 | 53 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43774 | 443,775
39 | 53 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43776 | 443,777
39 | 53 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43778 | 443,779
39 | 54 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43784 | 443,785
39 | 54 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43786 | 443,787
39 | 54 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43790 | 443,791
39 | 54 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43792 | 443,793
39 | 54 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43794 | 443,795
39 | 54 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43796 | 443,797
39 | 54 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43798 | 443,799
39 | 54 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43800 | 443,801
39 | 54 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43802 | 443,803
39 | 54 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43804 | 443,805
39 | 55 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43810 | 443,811
39 | 55 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43812 | 443,813
39 | 55 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43816 | 443,817
39 | 55 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43818 | 443,819
39 | 55 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43820 | 443,821
39 | 55 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43822 | 443,823
39 | 55 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43824 | 443,825
39 | 55 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43826 | 443,827
39 | 55 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43828 | 443,829
39 | 55 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43830 | 443,831
39 | 56 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43836 | 443,837
39 | 56 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43838 | 443,839
39 | 56 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43842 | 443,843
39 | 56 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43844 | 443,845
39 | 56 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43846 | 443,847
39 | 56 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43848 | 443,849
39 | 56 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43850 | 443,851
39 | 56 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43852 | 443,853
39 | 56 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43854 | 443,855
39 | 56 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43856 | 443,857
39 | 57 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43862 | 443,863
39 | 57 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43864 | 443,865
39 | 57 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43868 | 443,869
39 | 57 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43870 | 443,871
39 | 57 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43872 | 443,873
39 | 57 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43874 | 443,875
39 | 57 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43876 | 443,877
39 | 57 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43878 | 443,879
39 | 57 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43880 | 443,881
39 | 57 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43882 | 443,883
39 | 58 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43888 | 443,889
39 | 58 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43890 | 443,891
39 | 58 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43894 | 443,895
39 | 58 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43896 | 443,897
39 | 58 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43898 | 443,899
39 | 58 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43900 | 443,901
39 | 58 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43902 | 443,903
39 | 58 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43904 | 443,905
39 | 58 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43906 | 443,907
39 | 58 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43908 | 443,909
39 | 59 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43914 | 443,915
39 | 59 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43916 | 443,917
39 | 59 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43920 | 443,921
39 | 59 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43922 | 443,923
39 | 59 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43924 | 443,925
39 | 59 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43926 | 443,927
39 | 59 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43928 | 443,929
39 | 59 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43930 | 443,931
39 | 59 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43932 | 443,933
39 | 59 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43934 | 443,935
39 | 60 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43940 | 443,941
39 | 60 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43942 | 443,943
39 | 60 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43946 | 443,947
39 | 60 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43948 | 443,949
39 | 60 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43950 | 443,951
39 | 60 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43952 | 443,953
39 | 60 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43954 | 443,955
39 | 60 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43956 | 443,957
39 | 60 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43958 | 443,959
39 | 60 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43960 | 443,961
39 | 61 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43966 | 443,967
39 | 61 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43968 | 443,969
39 | 61 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43972 | 443,973
39 | 61 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43974 | 443,975
39 | 61 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 43976 | 443,977
39 | 61 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 43978 | 443,979
39 | 61 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 43980 | 443,981
39 | 61 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 43982 | 443,983
39 | 61 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43984 | 443,985
39 | 61 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 43986 | 443,987
39 | 62 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 43992 | 443,993
39 | 62 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 43994 | 443,995
39 | 62 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 43998 | 443,999
39 | 62 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44000 | 444,001
39 | 62 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44002 | 444,003
39 | 62 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44004 | 444,005
39 | 62 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44006 | 444,007
39 | 62 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44008 | 444,009
39 | 62 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44010 | 444,011
39 | 62 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44012 | 444,013
39 | 63 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44018 | 444,019
39 | 63 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44020 | 444,021
39 | 63 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44024 | 444,025
39 | 63 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44026 | 444,027
39 | 63 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44028 | 444,029
39 | 63 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44030 | 444,031
39 | 63 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44032 | 444,033
39 | 63 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44034 | 444,035
39 | 63 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44036 | 444,037
39 | 63 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44038 | 444,039
39 | 64 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44044 | 444,045
39 | 64 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44046 | 444,047
39 | 64 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44050 | 444,051
39 | 64 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44052 | 444,053
39 | 64 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44054 | 444,055
39 | 64 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44056 | 444,057
39 | 64 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44058 | 444,059
39 | 64 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44060 | 444,061
39 | 64 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44062 | 444,063
39 | 64 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44064 | 444,065
39 | 65 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44070 | 444,071
39 | 65 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44072 | 444,073
39 | 65 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44076 | 444,077
39 | 65 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44078 | 444,079
39 | 65 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44080 | 444,081
39 | 65 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44082 | 444,083
39 | 65 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44084 | 444,085
39 | 65 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44086 | 444,087
39 | 65 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44088 | 444,089
39 | 65 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44090 | 444,091
39 | 66 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44096 | 444,097
39 | 66 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44098 | 444,099
39 | 66 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44102 | 444,103
39 | 66 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44104 | 444,105
39 | 66 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44106 | 444,107
39 | 66 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44108 | 444,109
39 | 66 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44110 | 444,111
39 | 66 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44112 | 444,113
39 | 66 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44114 | 444,115
39 | 66 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44116 | 444,117
39 | 67 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44122 | 444,123
39 | 67 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44124 | 444,125
39 | 67 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44128 | 444,129
39 | 67 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44130 | 444,131
39 | 67 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44132 | 444,133
39 | 67 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44134 | 444,135
39 | 67 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44136 | 444,137
39 | 67 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44138 | 444,139
39 | 67 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44140 | 444,141
39 | 67 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44142 | 444,143
39 | 68 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44148 | 444,149
39 | 68 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44150 | 444,151
39 | 68 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44154 | 444,155
39 | 68 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44156 | 444,157
39 | 68 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44158 | 444,159
39 | 68 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44160 | 444,161
39 | 68 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44162 | 444,163
39 | 68 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44164 | 444,165
39 | 68 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44166 | 444,167
39 | 68 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44168 | 444,169
39 | 69 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44174 | 444,175
39 | 69 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44176 | 444,177
39 | 69 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44180 | 444,181
39 | 69 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44182 | 444,183
39 | 69 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44184 | 444,185
39 | 69 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44186 | 444,187
39 | 69 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44188 | 444,189
39 | 69 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44190 | 444,191
39 | 69 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44192 | 444,193
39 | 69 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44194 | 444,195
39 | 70 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44200 | 444,201
39 | 70 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44202 | 444,203
39 | 70 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44206 | 444,207
39 | 70 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44208 | 444,209
39 | 70 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44210 | 444,211
39 | 70 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44212 | 444,213
39 | 70 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44214 | 444,215
39 | 70 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44216 | 444,217
39 | 70 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44218 | 444,219
39 | 70 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44220 | 444,221
39 | 71 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44226 | 444,227
39 | 71 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44228 | 444,229
39 | 71 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44232 | 444,233
39 | 71 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44234 | 444,235
39 | 71 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44236 | 444,237
39 | 71 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44238 | 444,239
39 | 71 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44240 | 444,241
39 | 71 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44242 | 444,243
39 | 71 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44244 | 444,245
39 | 71 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44246 | 444,247
39 | 72 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44252 | 444,253
39 | 72 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44254 | 444,255
39 | 72 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44258 | 444,259
39 | 72 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44260 | 444,261
39 | 72 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44262 | 444,263
39 | 72 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44264 | 444,265
39 | 72 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44266 | 444,267
39 | 72 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44268 | 444,269
39 | 72 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44270 | 444,271
39 | 72 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44272 | 444,273
39 | 73 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44278 | 444,279
39 | 73 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44280 | 444,281
39 | 73 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44284 | 444,285
39 | 73 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44286 | 444,287
39 | 73 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44288 | 444,289
39 | 73 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44290 | 444,291
39 | 73 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44292 | 444,293
39 | 73 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44294 | 444,295
39 | 73 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44296 | 444,297
39 | 73 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44298 | 444,299
39 | 74 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44304 | 444,305
39 | 74 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44306 | 444,307
39 | 74 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44310 | 444,311
39 | 74 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44312 | 444,313
39 | 74 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44314 | 444,315
39 | 74 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44316 | 444,317
39 | 74 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44318 | 444,319
39 | 74 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44320 | 444,321
39 | 74 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44322 | 444,323
39 | 74 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44324 | 444,325
39 | 75 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44330 | 444,331
39 | 75 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44332 | 444,333
39 | 75 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44336 | 444,337
39 | 75 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44338 | 444,339
39 | 75 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44340 | 444,341
39 | 75 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44342 | 444,343
39 | 75 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44344 | 444,345
39 | 75 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44346 | 444,347
39 | 75 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44348 | 444,349
39 | 75 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44350 | 444,351
39 | 76 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44356 | 444,357
39 | 76 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44358 | 444,359
39 | 76 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44362 | 444,363
39 | 76 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44364 | 444,365
39 | 76 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44366 | 444,367
39 | 76 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44368 | 444,369
39 | 76 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44370 | 444,371
39 | 76 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44372 | 444,373
39 | 76 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44374 | 444,375
39 | 76 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44376 | 444,377
39 | 77 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44382 | 444,383
39 | 77 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44384 | 444,385
39 | 77 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44388 | 444,389
39 | 77 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44390 | 444,391
39 | 77 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44392 | 444,393
39 | 77 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44394 | 444,395
39 | 77 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44396 | 444,397
39 | 77 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44398 | 444,399
39 | 77 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44400 | 444,401
39 | 77 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44402 | 444,403
39 | 78 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44408 | 444,409
39 | 78 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44410 | 444,411
39 | 78 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44414 | 444,415
39 | 78 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44416 | 444,417
39 | 78 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44418 | 444,419
39 | 78 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44420 | 444,421
39 | 78 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44422 | 444,423
39 | 78 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44424 | 444,425
39 | 78 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44426 | 444,427
39 | 78 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44428 | 444,429
39 | 79 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44434 | 444,435
39 | 79 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44436 | 444,437
39 | 79 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44440 | 444,441
39 | 79 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44442 | 444,443
39 | 79 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44444 | 444,445
39 | 79 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44446 | 444,447
39 | 79 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44448 | 444,449
39 | 79 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44450 | 444,451
39 | 79 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44452 | 444,453
39 | 79 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44454 | 444,455
39 | 80 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44460 | 444,461
39 | 80 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44462 | 444,463
39 | 80 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44466 | 444,467
39 | 80 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44468 | 444,469
39 | 80 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44470 | 444,471
39 | 80 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44472 | 444,473
39 | 80 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44474 | 444,475
39 | 80 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44476 | 444,477
39 | 80 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44478 | 444,479
39 | 80 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44480 | 444,481
39 | 81 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44486 | 444,487
39 | 81 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44488 | 444,489
39 | 81 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44492 | 444,493
39 | 81 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44494 | 444,495
39 | 81 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44496 | 444,497
39 | 81 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44498 | 444,499
39 | 81 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44500 | 444,501
39 | 81 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44502 | 444,503
39 | 81 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44504 | 444,505
39 | 81 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44506 | 444,507
39 | 82 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44512 | 444,513
39 | 82 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44514 | 444,515
39 | 82 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44518 | 444,519
39 | 82 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44520 | 444,521
39 | 82 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44522 | 444,523
39 | 82 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44524 | 444,525
39 | 82 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44526 | 444,527
39 | 82 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44528 | 444,529
39 | 82 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44530 | 444,531
39 | 82 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44532 | 444,533
39 | 83 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44538 | 444,539
39 | 83 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44540 | 444,541
39 | 83 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44544 | 444,545
39 | 83 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44546 | 444,547
39 | 83 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44548 | 444,549
39 | 83 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44550 | 444,551
39 | 83 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44552 | 444,553
39 | 83 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44554 | 444,555
39 | 83 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44556 | 444,557
39 | 83 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44558 | 444,559
39 | 84 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44564 | 444,565
39 | 84 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44566 | 444,567
39 | 84 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44570 | 444,571
39 | 84 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44572 | 444,573
39 | 84 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44574 | 444,575
39 | 84 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44576 | 444,577
39 | 84 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44578 | 444,579
39 | 84 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44580 | 444,581
39 | 84 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44582 | 444,583
39 | 84 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44584 | 444,585
39 | 85 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44590 | 444,591
39 | 85 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44592 | 444,593
39 | 85 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44596 | 444,597
39 | 85 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44598 | 444,599
39 | 85 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44600 | 444,601
39 | 85 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44602 | 444,603
39 | 85 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44604 | 444,605
39 | 85 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44606 | 444,607
39 | 85 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44608 | 444,609
39 | 85 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44610 | 444,611
39 | 86 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44616 | 444,617
39 | 86 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44618 | 444,619
39 | 86 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44622 | 444,623
39 | 86 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44624 | 444,625
39 | 86 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44626 | 444,627
39 | 86 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44628 | 444,629
39 | 86 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44630 | 444,631
39 | 86 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44632 | 444,633
39 | 86 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44634 | 444,635
39 | 86 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44636 | 444,637
39 | 87 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44642 | 444,643
39 | 87 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44644 | 444,645
39 | 87 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44648 | 444,649
39 | 87 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44650 | 444,651
39 | 87 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44652 | 444,653
39 | 87 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44654 | 444,655
39 | 87 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44656 | 444,657
39 | 87 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44658 | 444,659
39 | 87 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44660 | 444,661
39 | 87 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44662 | 444,663
39 | 88 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44668 | 444,669
39 | 88 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44670 | 444,671
39 | 88 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44674 | 444,675
39 | 88 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44676 | 444,677
39 | 88 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44678 | 444,679
39 | 88 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44680 | 444,681
39 | 88 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44682 | 444,683
39 | 88 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44684 | 444,685
39 | 88 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44686 | 444,687
39 | 88 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44688 | 444,689
39 | 89 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44694 | 444,695
39 | 89 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44696 | 444,697
39 | 89 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44700 | 444,701
39 | 89 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44702 | 444,703
39 | 89 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44704 | 444,705
39 | 89 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44706 | 444,707
39 | 89 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44708 | 444,709
39 | 89 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44710 | 444,711
39 | 89 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44712 | 444,713
39 | 89 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44714 | 444,715
39 | 90 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44720 | 444,721
39 | 90 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44722 | 444,723
39 | 90 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44726 | 444,727
39 | 90 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44728 | 444,729
39 | 90 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44730 | 444,731
39 | 90 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44732 | 444,733
39 | 90 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44734 | 444,735
39 | 90 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44736 | 444,737
39 | 90 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44738 | 444,739
39 | 90 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44740 | 444,741
39 | 91 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44746 | 444,747
39 | 91 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44748 | 444,749
39 | 91 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44752 | 444,753
39 | 91 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44754 | 444,755
39 | 91 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44756 | 444,757
39 | 91 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44758 | 444,759
39 | 91 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44760 | 444,761
39 | 91 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44762 | 444,763
39 | 91 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44764 | 444,765
39 | 91 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44766 | 444,767
39 | 92 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44772 | 444,773
39 | 92 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44774 | 444,775
39 | 92 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44778 | 444,779
39 | 92 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44780 | 444,781
39 | 92 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44782 | 444,783
39 | 92 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44784 | 444,785
39 | 92 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44786 | 444,787
39 | 92 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44788 | 444,789
39 | 92 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44790 | 444,791
39 | 92 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44792 | 444,793
39 | 93 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44798 | 444,799
39 | 93 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44800 | 444,801
39 | 93 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44804 | 444,805
39 | 93 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44806 | 444,807
39 | 93 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44808 | 444,809
39 | 93 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44810 | 444,811
39 | 93 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44812 | 444,813
39 | 93 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44814 | 444,815
39 | 93 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44816 | 444,817
39 | 93 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44818 | 444,819
39 | 94 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44824 | 444,825
39 | 94 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44826 | 444,827
39 | 94 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44830 | 444,831
39 | 94 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44832 | 444,833
39 | 94 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44834 | 444,835
39 | 94 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44836 | 444,837
39 | 94 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44838 | 444,839
39 | 94 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44840 | 444,841
39 | 94 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44842 | 444,843
39 | 94 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44844 | 444,845
39 | 95 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44850 | 444,851
39 | 95 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44852 | 444,853
39 | 95 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44856 | 444,857
39 | 95 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44858 | 444,859
39 | 95 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44860 | 444,861
39 | 95 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44862 | 444,863
39 | 95 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44864 | 444,865
39 | 95 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44866 | 444,867
39 | 95 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44868 | 444,869
39 | 95 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44870 | 444,871
39 | 96 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44876 | 444,877
39 | 96 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44878 | 444,879
39 | 96 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44882 | 444,883
39 | 96 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44884 | 444,885
39 | 96 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44886 | 444,887
39 | 96 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44888 | 444,889
39 | 96 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44890 | 444,891
39 | 96 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44892 | 444,893
39 | 96 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44894 | 444,895
39 | 96 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44896 | 444,897
39 | 97 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44902 | 444,903
39 | 97 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44904 | 444,905
39 | 97 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44908 | 444,909
39 | 97 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44910 | 444,911
39 | 97 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44912 | 444,913
39 | 97 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44914 | 444,915
39 | 97 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44916 | 444,917
39 | 97 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44918 | 444,919
39 | 97 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44920 | 444,921
39 | 97 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44922 | 444,923
39 | 98 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44928 | 444,929
39 | 98 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44930 | 444,931
39 | 98 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44934 | 444,935
39 | 98 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44936 | 444,937
39 | 98 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44938 | 444,939
39 | 98 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44940 | 444,941
39 | 98 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44942 | 444,943
39 | 98 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44944 | 444,945
39 | 98 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44946 | 444,947
39 | 98 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44948 | 444,949
39 | 99 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44954 | 444,955
39 | 99 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44956 | 444,957
39 | 99 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44960 | 444,961
39 | 99 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44962 | 444,963
39 | 99 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44964 | 444,965
39 | 99 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44966 | 444,967
39 | 99 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44968 | 444,969
39 | 99 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44970 | 444,971
39 | 99 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44972 | 444,973
39 | 99 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44974 | 444,975
39 | 100 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 44980 | 444,981
39 | 100 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 44982 | 444,983
39 | 100 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 44986 | 444,987
39 | 100 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44988 | 444,989
39 | 100 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 44990 | 444,991
39 | 100 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 44992 | 444,993
39 | 100 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 44994 | 444,995
39 | 100 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 44996 | 444,997
39 | 100 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 44998 | 444,999
39 | 100 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45000 | 445,001
39 | 101 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45006 | 445,007
39 | 101 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45008 | 445,009
39 | 101 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45012 | 445,013
39 | 101 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45014 | 445,015
39 | 101 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45016 | 445,017
39 | 101 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45018 | 445,019
39 | 101 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45020 | 445,021
39 | 101 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45022 | 445,023
39 | 101 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45024 | 445,025
39 | 101 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45026 | 445,027
39 | 102 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45032 | 445,033
39 | 102 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45034 | 445,035
39 | 102 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45038 | 445,039
39 | 102 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45040 | 445,041
39 | 102 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45042 | 445,043
39 | 102 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45044 | 445,045
39 | 102 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45046 | 445,047
39 | 102 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45048 | 445,049
39 | 102 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45050 | 445,051
39 | 102 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45052 | 445,053
39 | 103 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45058 | 445,059
39 | 103 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45060 | 445,061
39 | 103 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45064 | 445,065
39 | 103 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45066 | 445,067
39 | 103 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45068 | 445,069
39 | 103 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45070 | 445,071
39 | 103 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45072 | 445,073
39 | 103 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45074 | 445,075
39 | 103 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45076 | 445,077
39 | 103 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45078 | 445,079
39 | 104 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45084 | 445,085
39 | 104 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45086 | 445,087
39 | 104 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45090 | 445,091
39 | 104 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45092 | 445,093
39 | 104 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45094 | 445,095
39 | 104 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45096 | 445,097
39 | 104 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45098 | 445,099
39 | 104 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45100 | 445,101
39 | 104 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45102 | 445,103
39 | 104 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45104 | 445,105
39 | 105 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45110 | 445,111
39 | 105 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45112 | 445,113
39 | 105 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45116 | 445,117
39 | 105 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45118 | 445,119
39 | 105 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45120 | 445,121
39 | 105 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45122 | 445,123
39 | 105 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45124 | 445,125
39 | 105 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45126 | 445,127
39 | 105 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45128 | 445,129
39 | 105 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45130 | 445,131
39 | 106 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45136 | 445,137
39 | 106 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45138 | 445,139
39 | 106 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45142 | 445,143
39 | 106 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45144 | 445,145
39 | 106 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45146 | 445,147
39 | 106 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45148 | 445,149
39 | 106 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45150 | 445,151
39 | 106 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45152 | 445,153
39 | 106 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45154 | 445,155
39 | 106 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45156 | 445,157
39 | 107 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45162 | 445,163
39 | 107 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45164 | 445,165
39 | 107 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45168 | 445,169
39 | 107 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45170 | 445,171
39 | 107 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45172 | 445,173
39 | 107 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45174 | 445,175
39 | 107 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45176 | 445,177
39 | 107 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45178 | 445,179
39 | 107 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45180 | 445,181
39 | 107 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45182 | 445,183
39 | 108 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45188 | 445,189
39 | 108 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45190 | 445,191
39 | 108 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45194 | 445,195
39 | 108 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45196 | 445,197
39 | 108 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45198 | 445,199
39 | 108 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45200 | 445,201
39 | 108 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45202 | 445,203
39 | 108 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45204 | 445,205
39 | 108 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45206 | 445,207
39 | 108 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45208 | 445,209
39 | 109 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45214 | 445,215
39 | 109 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45216 | 445,217
39 | 109 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45220 | 445,221
39 | 109 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45222 | 445,223
39 | 109 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45224 | 445,225
39 | 109 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45226 | 445,227
39 | 109 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45228 | 445,229
39 | 109 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45230 | 445,231
39 | 109 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45232 | 445,233
39 | 109 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45234 | 445,235
39 | 110 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45240 | 445,241
39 | 110 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45242 | 445,243
39 | 110 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45246 | 445,247
39 | 110 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45248 | 445,249
39 | 110 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45250 | 445,251
39 | 110 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45252 | 445,253
39 | 110 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45254 | 445,255
39 | 110 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45256 | 445,257
39 | 110 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45258 | 445,259
39 | 110 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45260 | 445,261
39 | 111 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45266 | 445,267
39 | 111 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45268 | 445,269
39 | 111 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45272 | 445,273
39 | 111 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45274 | 445,275
39 | 111 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45276 | 445,277
39 | 111 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45278 | 445,279
39 | 111 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45280 | 445,281
39 | 111 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45282 | 445,283
39 | 111 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45284 | 445,285
39 | 111 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45286 | 445,287
39 | 112 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45292 | 445,293
39 | 112 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45294 | 445,295
39 | 112 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45298 | 445,299
39 | 112 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45300 | 445,301
39 | 112 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45302 | 445,303
39 | 112 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45304 | 445,305
39 | 112 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45306 | 445,307
39 | 112 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45308 | 445,309
39 | 112 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45310 | 445,311
39 | 112 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45312 | 445,313
39 | 113 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45318 | 445,319
39 | 113 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45320 | 445,321
39 | 113 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45324 | 445,325
39 | 113 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45326 | 445,327
39 | 113 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45328 | 445,329
39 | 113 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45330 | 445,331
39 | 113 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45332 | 445,333
39 | 113 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45334 | 445,335
39 | 113 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45336 | 445,337
39 | 113 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45338 | 445,339
39 | 114 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45344 | 445,345
39 | 114 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45346 | 445,347
39 | 114 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45350 | 445,351
39 | 114 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45352 | 445,353
39 | 114 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45354 | 445,355
39 | 114 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45356 | 445,357
39 | 114 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45358 | 445,359
39 | 114 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45360 | 445,361
39 | 114 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45362 | 445,363
39 | 114 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45364 | 445,365
39 | 115 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45370 | 445,371
39 | 115 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45372 | 445,373
39 | 115 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45376 | 445,377
39 | 115 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45378 | 445,379
39 | 115 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45380 | 445,381
39 | 115 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45382 | 445,383
39 | 115 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45384 | 445,385
39 | 115 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45386 | 445,387
39 | 115 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45388 | 445,389
39 | 115 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45390 | 445,391
39 | 116 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45396 | 445,397
39 | 116 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45398 | 445,399
39 | 116 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45402 | 445,403
39 | 116 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45404 | 445,405
39 | 116 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45406 | 445,407
39 | 116 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45408 | 445,409
39 | 116 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45410 | 445,411
39 | 116 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45412 | 445,413
39 | 116 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45414 | 445,415
39 | 116 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45416 | 445,417
39 | 117 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45422 | 445,423
39 | 117 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45424 | 445,425
39 | 117 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45428 | 445,429
39 | 117 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45430 | 445,431
39 | 117 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45432 | 445,433
39 | 117 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45434 | 445,435
39 | 117 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45436 | 445,437
39 | 117 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45438 | 445,439
39 | 117 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45440 | 445,441
39 | 117 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45442 | 445,443
39 | 118 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45448 | 445,449
39 | 118 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45450 | 445,451
39 | 118 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45454 | 445,455
39 | 118 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45456 | 445,457
39 | 118 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45458 | 445,459
39 | 118 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45460 | 445,461
39 | 118 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45462 | 445,463
39 | 118 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45464 | 445,465
39 | 118 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45466 | 445,467
39 | 118 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45468 | 445,469
39 | 119 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45474 | 445,475
39 | 119 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45476 | 445,477
39 | 119 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45480 | 445,481
39 | 119 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45482 | 445,483
39 | 119 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45484 | 445,485
39 | 119 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45486 | 445,487
39 | 119 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45488 | 445,489
39 | 119 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45490 | 445,491
39 | 119 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45492 | 445,493
39 | 119 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45494 | 445,495
39 | 120 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45500 | 445,501
39 | 120 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45502 | 445,503
39 | 120 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45506 | 445,507
39 | 120 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45508 | 445,509
39 | 120 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45510 | 445,511
39 | 120 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45512 | 445,513
39 | 120 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45514 | 445,515
39 | 120 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45516 | 445,517
39 | 120 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45518 | 445,519
39 | 120 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45520 | 445,521
39 | 121 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45526 | 445,527
39 | 121 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45528 | 445,529
39 | 121 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45532 | 445,533
39 | 121 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45534 | 445,535
39 | 121 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45536 | 445,537
39 | 121 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45538 | 445,539
39 | 121 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45540 | 445,541
39 | 121 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45542 | 445,543
39 | 121 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45544 | 445,545
39 | 121 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45546 | 445,547
39 | 122 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45552 | 445,553
39 | 122 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45554 | 445,555
39 | 122 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45558 | 445,559
39 | 122 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45560 | 445,561
39 | 122 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45562 | 445,563
39 | 122 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45564 | 445,565
39 | 122 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45566 | 445,567
39 | 122 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45568 | 445,569
39 | 122 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45570 | 445,571
39 | 122 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45572 | 445,573
39 | 123 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45578 | 445,579
39 | 123 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45580 | 445,581
39 | 123 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45584 | 445,585
39 | 123 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45586 | 445,587
39 | 123 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45588 | 445,589
39 | 123 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45590 | 445,591
39 | 123 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45592 | 445,593
39 | 123 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45594 | 445,595
39 | 123 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45596 | 445,597
39 | 123 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45598 | 445,599
39 | 124 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45604 | 445,605
39 | 124 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45606 | 445,607
39 | 124 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45610 | 445,611
39 | 124 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45612 | 445,613
39 | 124 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45614 | 445,615
39 | 124 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45616 | 445,617
39 | 124 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45618 | 445,619
39 | 124 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45620 | 445,621
39 | 124 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45622 | 445,623
39 | 124 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45624 | 445,625
39 | 125 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45630 | 445,631
39 | 125 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45632 | 445,633
39 | 125 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45636 | 445,637
39 | 125 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45638 | 445,639
39 | 125 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45640 | 445,641
39 | 125 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45642 | 445,643
39 | 125 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45644 | 445,645
39 | 125 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45646 | 445,647
39 | 125 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45648 | 445,649
39 | 125 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45650 | 445,651
39 | 126 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45656 | 445,657
39 | 126 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45658 | 445,659
39 | 126 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45662 | 445,663
39 | 126 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45664 | 445,665
39 | 126 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45666 | 445,667
39 | 126 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45668 | 445,669
39 | 126 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45670 | 445,671
39 | 126 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45672 | 445,673
39 | 126 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45674 | 445,675
39 | 126 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45676 | 445,677
39 | 127 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45682 | 445,683
39 | 127 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45684 | 445,685
39 | 127 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45688 | 445,689
39 | 127 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45690 | 445,691
39 | 127 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45692 | 445,693
39 | 127 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45694 | 445,695
39 | 127 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45696 | 445,697
39 | 127 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45698 | 445,699
39 | 127 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45700 | 445,701
39 | 127 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45702 | 445,703
39 | 128 | 1 | Logging Point | Base | Source Function A | Set the source of the data log point. | None (61), Analog Input (142), Active Set Point (72), Heat Power (160), Cool Power (161), Alarm (6), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Current (22), Current Read (179), Power (73), Limit (126), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778), Digital I/O (1142), Function Key (1001), Variable (245), Math (240), Process Value (241), Logic (239), Compare (230), Counter (231), Timer (244), Linearization (238), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Cascade Active Set Point (2125), Cascade Heat Power (1794), Cascade Cool Power (1795), Cascade Power (1796), Cascade Inner PV (2019), Cascade Outer PV (2020), Control Loop PV (2021), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 45708 | 445,709
39 | 128 | 2 | Logging Point | Base | Source Instance A | Set the instance of the data log point. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 45710 | 445,711
39 | 128 | 4 | Logging Point | Base | Source Value A | Monitor the value of the source being logged. | -1,999.000 to 9,999.000 |  | IEEE Float | R | 45714 | 445,715
39 | 128 | 5 | Logging Point | Base | Class | Set the class of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45716 | 445,717
39 | 128 | 6 | Logging Point | Base | Member | Set the member of the data log point. | 1 to 255 | 0 | Unsigned 8-bit | R/W | 45718 | 445,719
39 | 128 | 7 | Logging Point | Base | Display Precision | Set the precision applied to the data log point. | Source (1539), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Source (1539) | Enumeration | R/W | 45720 | 445,721
39 | 128 | 8 | Logging Point | Base | Error | Monitor the error status of the data log point. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 45722 | 445,723
39 | 128 | 9 | Logging Point | Base | Data Type | Monitor the data log point type. | 0 to 255 | 0 | Unsigned 8-bit | R | 45724 | 445,725
39 | 128 | 12 | Logging Point | Base | Log Enable | Set to enable data log point. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45726 | 445,727
39 | 128 | 13 | Logging Point | Base |  | Set to enable data point to be on trend plot. | Yes (106), No (59) | Yes (106) | Enumeration | R/W | 45728 | 445,729
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49340 | 449,341
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49341 | 449,342
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49342 | 449,343
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49343 | 449,344
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49344 | 449,345
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49345 | 449,346
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49346 | 449,347
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49347 | 449,348
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49348 | 449,349
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49349 | 449,350
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49350 | 449,351
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49351 | 449,352
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49352 | 449,353
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49353 | 449,354
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49354 | 449,355
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49355 | 449,356
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49356 | 449,357
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49357 | 449,358
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49358 | 449,359
44 | 1 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49359 | 449,360
44 | 1 | 4 | Cascade | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 4010 | 404,011
44 | 1 | 5 | Cascade | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | Enumeration | R | 4012 | 404,013
44 | 1 | 6 | Cascade | Base | Control Action | Set the heat/cool control method. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | Enumeration | R/W | 4014 | 404,015
44 | 1 | 7 | Cascade | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | Enumeration | R/W | 4016 | 404,017
44 | 1 | 8 | Cascade | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | IEEE Float | R/W | 4018 | 404,019
44 | 1 | 9 | Cascade | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4020 | 404,021
44 | 1 | 10 | Cascade | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | Enumeration | R | 4022 | 404,023
44 | 1 | 11 | Cascade | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4024 | 404,025
44 | 1 | 12 | Cascade | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | Unsigned 16-bit | R/W | 4026 | 404,027
44 | 1 | 13 | Cascade | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 4028 | 404,029
44 | 1 | 14 | Cascade | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | Enumeration | R | 4030 | 404,031
44 | 1 | 15 | Cascade | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 4032 | 404,033
44 | 1 | 16 | Cascade | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 4034 | 404,035
44 | 1 | 17 | Cascade | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 4036 | 404,037
44 | 1 | 18 | Cascade | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | IEEE Float | R/W | 4038 | 404,039
44 | 1 | 19 | Cascade | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | IEEE Float | R/W | 4040 | 404,041
44 | 1 | 20 | Cascade | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | IEEE Float | R/W | 4042 | 404,043
44 | 1 | 21 | Cascade | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | IEEE Float | R/W | 4044 | 404,045
44 | 1 | 22 | Cascade | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | IEEE Float | R/W | 4046 | 404,047
44 | 1 | 23 | Cascade | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 4048 | 404,049
44 | 1 | 24 | Cascade | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 4050 | 404,051
44 | 1 | 25 | Cascade | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | IEEE Float | R/W | 4052 | 404,053
44 | 1 | 26 | Cascade | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 4054 | 404,055
44 | 1 | 27 | Cascade | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | Enumeration | R/W | 4056 | 404,057
44 | 1 | 28 | Cascade | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 4058 | 404,059
44 | 1 | 29 | Cascade | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4060 | 404,061
44 | 1 | 30 | Cascade | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 4062 | 404,063
44 | 1 | 36 | Cascade | Base | Profile End Action | Set profile end action for control loop when end step is not specified. | User (100), Off (62), Hold (47) | User (100) | Enumeration | R/W | 4192 | 404,193
44 | 1 | 37 | Cascade | Base | Function | Set the type of cascade to implement. | Process (75), Deviation (1807) | Process (75) | Enumeration | R/W | 4194 | 404,195
44 | 1 | 40 | Cascade | Base | Range Low | Set the value represented for low power converted to a temperature set point for the inner loop. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4168 | 404,169
44 | 1 | 41 | Cascade | Base | Range High | Set the value represented for high power converted to a temperature set point for the inner loop. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 4170 | 404,171
44 | 1 | 43 | Cascade | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | Enumeration | R/W | 4064 | 404,065
44 | 1 | 50 | Cascade | Base | Inner Loop Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 4196 | 404,197
44 | 1 | 51 | Cascade | Base | Inner Loop Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 4198 | 404,199
44 | 1 | 57 | Cascade | Base | Inner Loop PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | Unsigned 8-bit | R | 4202 | 404,203
44 | 1 | 58 | Cascade | Base | Heat Proportional Band Inner Loop 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4066 | 404,067
44 | 1 | 59 | Cascade | Base | Cool Proportional Band Inner Loop 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4068 | 404,069
44 | 1 | 60 | Cascade | Base | Integral Inner Loop 1 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4070 | 404,071
44 | 1 | 61 | Cascade | Base | Derivative Inner Loop 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4072 | 404,073
44 | 1 | 62 | Cascade | Base | Heat Proportional Band Inner Loop 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4074 | 404,075
44 | 1 | 63 | Cascade | Base | Cool Proportional Band Inner Loop 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4076 | 404,077
44 | 1 | 64 | Cascade | Base | Integral Inner Loop 2 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4078 | 404,079
44 | 1 | 65 | Cascade | Base | Derivative Inner Loop 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4080 | 404,081
44 | 1 | 66 | Cascade | Base | Heat Proportional Band Inner Loop 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4082 | 404,083
44 | 1 | 67 | Cascade | Base | Cool Proportional Band Inner Loop 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4084 | 404,085
44 | 1 | 68 | Cascade | Base | Integral Inner Loop 3 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4086 | 404,087
44 | 1 | 69 | Cascade | Base | Derivative Inner Loop 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4088 | 404,089
44 | 1 | 70 | Cascade | Base | Heat Proportional Band Inner Loop 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4090 | 404,091
44 | 1 | 71 | Cascade | Base | Cool Proportional Band Inner Loop 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4092 | 404,093
44 | 1 | 72 | Cascade | Base | Integral Inner Loop 4 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4094 | 404,095
44 | 1 | 73 | Cascade | Base | Derivative Inner Loop 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4096 | 404,097
44 | 1 | 74 | Cascade | Base | Heat Proportional Band Inner Loop 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4098 | 404,099
44 | 1 | 75 | Cascade | Base | Cool Proportional Band Inner Loop 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4100 | 404,101
44 | 1 | 76 | Cascade | Base | Integral Inner Loop 5 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4102 | 404,103
44 | 1 | 77 | Cascade | Base | Derivative Inner Loop 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4104 | 404,105
44 | 1 | 78 | Cascade | Base | Inner Loop Deadband | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 4106 | 404,107
44 | 1 | 79 | Cascade | Base | Inner Loop On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 4108 | 404,109
44 | 1 | 80 | Cascade | Base | Inner Loop On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 4110 | 404,111
44 | 1 | 81 | Cascade | Base | Inner Loop Set Point Closed | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 4188 | 404,189
44 | 1 | 100 | Cascade | Base | Outer Loop Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 4112 | 404,113
44 | 1 | 101 | Cascade | Base | Outer Loop Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 4114 | 404,115
44 | 1 | 102 | Cascade | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | Enumeration | R/W | 4116 | 404,117
44 | 1 | 103 | Cascade | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. |  |  | IEEE Float | R/W | 4118 | 404,119
44 | 1 | 104 | Cascade | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. |  |  | IEEE Float | R/W | 4120 | 404,121
44 | 1 | 105 | Cascade | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. |  |  | IEEE Float | R/W | 4122 | 404,123
44 | 1 | 106 | Cascade | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. |  |  | IEEE Float | R/W | 4124 | 404,125
44 | 1 | 108 | Cascade | Base | Heat Proportional Band Outer Loop 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4126 | 404,127
44 | 1 | 109 | Cascade | Base | Cool Proportional Band Outer Loop 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4128 | 404,129
44 | 1 | 110 | Cascade | Base | Integral Outer Loop 1 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4130 | 404,131
44 | 1 | 111 | Cascade | Base | Derivative Outer Loop 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4132 | 404,133
44 | 1 | 112 | Cascade | Base | Heat Proportional Band Outer Loop 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4134 | 404,135
44 | 1 | 113 | Cascade | Base | Cool Proportional Band Outer Loop 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4136 | 404,137
44 | 1 | 114 | Cascade | Base | Integral Outer Loop 2 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4138 | 404,139
44 | 1 | 115 | Cascade | Base | Derivative Outer Loop 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4140 | 404,141
44 | 1 | 116 | Cascade | Base | Heat Proportional Band Outer Loop 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4142 | 404,143
44 | 1 | 117 | Cascade | Base | Cool Proportional Band Outer Loop 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4144 | 404,145
44 | 1 | 118 | Cascade | Base | Integral Outer Loop 3 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4146 | 404,147
44 | 1 | 119 | Cascade | Base | Derivative Outer Loop 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4148 | 404,149
44 | 1 | 120 | Cascade | Base | Heat Proportional Band Outer Loop 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4150 | 404,151
44 | 1 | 121 | Cascade | Base | Cool Proportional Band Outer Loop 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4152 | 404,153
44 | 1 | 122 | Cascade | Base | Integral Outer Loop 4 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4154 | 404,155
44 | 1 | 123 | Cascade | Base | Derivative Outer Loop 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4156 | 404,157
44 | 1 | 124 | Cascade | Base | Heat Proportional Band Outer Loop 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4158 | 404,159
44 | 1 | 125 | Cascade | Base | Cool Proportional Band Outer Loop 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4160 | 404,161
44 | 1 | 126 | Cascade | Base | Integral Outer Loop 5 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4162 | 404,163
44 | 1 | 127 | Cascade | Base | Derivative Outer Loop 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4164 | 404,165
44 | 1 | 128 | Cascade | Base | Outer Loop Deadband | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 4166 | 404,167
44 | 1 | 131 | Cascade | Base | Outer Loop Set Point Closed | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 4190 | 404,191
44 | 1 | 141 | Cascade | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | Unsigned 8-bit | R/W | 4172 | 404,173
44 | 1 | 150 | Cascade | Base | Cascade Heat Power | Monitor the requested PID heat power. | 0.0 to 100.0 |  | IEEE Float | R | 4174 | 404,175
44 | 1 | 152 | Cascade | Base | Cascade Cool Power | Monitor the requested PID cool power. | -100.0 to 0.0 |  | IEEE Float | R | 4176 | 404,177
44 | 1 | 154 | Cascade | Base | Cascade Power | Monitor the requested PID total power. | -100.0 to 100.0 |  | IEEE Float | R | 4178 | 404,179
44 | 1 | 163 | Cascade | Base | Source Value A | Monitor process value feedback for the outer loop while in auto mode. |  |  | IEEE Float | R | 4180 | 404,181
44 | 1 | 167 | Cascade | Base | Source Value B | Monitor the source input value used by the inner control loop while in auto mode. |  |  | IEEE Float | R | 4182 | 404,183
44 | 1 | 171 | Cascade | Base | Source Value C | Monitor the remote set point value. |  |  | IEEE Float | R | 4184 | 404,185
44 | 1 | 175 | Cascade | Base | Source Value D | Monitor set point from the profile engine when profiling is used. |  |  | IEEE Float | R | 4186 | 404,187
44 | 1 | 206 | Cascade | Base | Simple Set Point Enable | Set to switch off cascade feature. | On (63), Off (62) | Off (62) | Enumeration | R/W | 4200 | 404,201
44 | 1 | 207 | Cascade | Base | Cascade Control Mode Is Off | Monitor Cascade Control Mode is Off | On (63), Off (62) |  | Enumeration | R | 4204 | 404,205
44 | 1 | 208 | Cascade | Base | Set Point | Monitor Closed Loop Set Point |  |  | IEEE Float | R | 4206 | 404,207
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49360 | 449,361
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49361 | 449,362
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49362 | 449,363
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49363 | 449,364
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49364 | 449,365
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49365 | 449,366
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49366 | 449,367
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49367 | 449,368
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49368 | 449,369
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49369 | 449,370
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49370 | 449,371
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49371 | 449,372
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49372 | 449,373
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49373 | 449,374
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49374 | 449,375
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49375 | 449,376
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49376 | 449,377
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49377 | 449,378
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49378 | 449,379
44 | 2 | 3 | Cascade | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49379 | 449,380
44 | 2 | 4 | Cascade | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 4210 | 404,211
44 | 2 | 5 | Cascade | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | Enumeration | R | 4212 | 404,213
44 | 2 | 6 | Cascade | Base | Control Action | Set the heat/cool control method. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | Enumeration | R/W | 4214 | 404,215
44 | 2 | 7 | Cascade | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | Enumeration | R/W | 4216 | 404,217
44 | 2 | 8 | Cascade | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | IEEE Float | R/W | 4218 | 404,219
44 | 2 | 9 | Cascade | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4220 | 404,221
44 | 2 | 10 | Cascade | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | Enumeration | R | 4222 | 404,223
44 | 2 | 11 | Cascade | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4224 | 404,225
44 | 2 | 12 | Cascade | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | Unsigned 16-bit | R/W | 4226 | 404,227
44 | 2 | 13 | Cascade | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 4228 | 404,229
44 | 2 | 14 | Cascade | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | Enumeration | R | 4230 | 404,231
44 | 2 | 15 | Cascade | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 4232 | 404,233
44 | 2 | 16 | Cascade | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 4234 | 404,235
44 | 2 | 17 | Cascade | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 4236 | 404,237
44 | 2 | 18 | Cascade | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | IEEE Float | R/W | 4238 | 404,239
44 | 2 | 19 | Cascade | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | IEEE Float | R/W | 4240 | 404,241
44 | 2 | 20 | Cascade | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | IEEE Float | R/W | 4242 | 404,243
44 | 2 | 21 | Cascade | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | IEEE Float | R/W | 4244 | 404,245
44 | 2 | 22 | Cascade | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | IEEE Float | R/W | 4246 | 404,247
44 | 2 | 23 | Cascade | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 4248 | 404,249
44 | 2 | 24 | Cascade | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 4250 | 404,251
44 | 2 | 25 | Cascade | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | IEEE Float | R/W | 4252 | 404,253
44 | 2 | 26 | Cascade | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 4254 | 404,255
44 | 2 | 27 | Cascade | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | Enumeration | R/W | 4256 | 404,257
44 | 2 | 28 | Cascade | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 4258 | 404,259
44 | 2 | 29 | Cascade | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | Enumeration | R/W | 4260 | 404,261
44 | 2 | 30 | Cascade | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 4262 | 404,263
44 | 2 | 36 | Cascade | Base | Profile End Action | Set profile end action for control loop when end step is not specified. | User (100), Off (62), Hold (47) | User (100) | Enumeration | R/W | 4392 | 404,393
44 | 2 | 37 | Cascade | Base | Function | Set the type of cascade to implement. | Process (75), Deviation (1807) | Process (75) | Enumeration | R/W | 4394 | 404,395
44 | 2 | 40 | Cascade | Base | Range Low | Set the value represented for low power converted to a temperature set point for the inner loop. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4368 | 404,369
44 | 2 | 41 | Cascade | Base | Range High | Set the value represented for high power converted to a temperature set point for the inner loop. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 4370 | 404,371
44 | 2 | 43 | Cascade | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | Enumeration | R/W | 4264 | 404,265
44 | 2 | 50 | Cascade | Base | Inner Loop Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 4396 | 404,397
44 | 2 | 51 | Cascade | Base | Inner Loop Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 4398 | 404,399
44 | 2 | 57 | Cascade | Base | Inner Loop PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | Unsigned 8-bit | R | 4402 | 404,403
44 | 2 | 58 | Cascade | Base | Heat Proportional Band Inner Loop 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4266 | 404,267
44 | 2 | 59 | Cascade | Base | Cool Proportional Band Inner Loop 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4268 | 404,269
44 | 2 | 60 | Cascade | Base | Integral Inner Loop 1 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4270 | 404,271
44 | 2 | 61 | Cascade | Base | Derivative Inner Loop 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4272 | 404,273
44 | 2 | 62 | Cascade | Base | Heat Proportional Band Inner Loop 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4274 | 404,275
44 | 2 | 63 | Cascade | Base | Cool Proportional Band Inner Loop 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4276 | 404,277
44 | 2 | 64 | Cascade | Base | Integral Inner Loop 2 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4278 | 404,279
44 | 2 | 65 | Cascade | Base | Derivative Inner Loop 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4280 | 404,281
44 | 2 | 66 | Cascade | Base | Heat Proportional Band Inner Loop 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4282 | 404,283
44 | 2 | 67 | Cascade | Base | Cool Proportional Band Inner Loop 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4284 | 404,285
44 | 2 | 68 | Cascade | Base | Integral Inner Loop 3 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4286 | 404,287
44 | 2 | 69 | Cascade | Base | Derivative Inner Loop 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4288 | 404,289
44 | 2 | 70 | Cascade | Base | Heat Proportional Band Inner Loop 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4290 | 404,291
44 | 2 | 71 | Cascade | Base | Cool Proportional Band Inner Loop 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4292 | 404,293
44 | 2 | 72 | Cascade | Base | Integral Inner Loop 4 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4294 | 404,295
44 | 2 | 73 | Cascade | Base | Derivative Inner Loop 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4296 | 404,297
44 | 2 | 74 | Cascade | Base | Heat Proportional Band Inner Loop 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4298 | 404,299
44 | 2 | 75 | Cascade | Base | Cool Proportional Band Inner Loop 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4300 | 404,301
44 | 2 | 76 | Cascade | Base | Integral Inner Loop 5 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4302 | 404,303
44 | 2 | 77 | Cascade | Base | Derivative Inner Loop 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4304 | 404,305
44 | 2 | 78 | Cascade | Base | Inner Loop Deadband | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 4306 | 404,307
44 | 2 | 79 | Cascade | Base | Inner Loop On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 4308 | 404,309
44 | 2 | 80 | Cascade | Base | Inner Loop On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 4310 | 404,311
44 | 2 | 81 | Cascade | Base | Inner Loop Set Point Closed | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 4388 | 404,389
44 | 2 | 100 | Cascade | Base | Outer Loop Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 4312 | 404,313
44 | 2 | 101 | Cascade | Base | Outer Loop Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 4314 | 404,315
44 | 2 | 102 | Cascade | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | Enumeration | R/W | 4316 | 404,317
44 | 2 | 103 | Cascade | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. |  |  | IEEE Float | R/W | 4318 | 404,319
44 | 2 | 104 | Cascade | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. |  |  | IEEE Float | R/W | 4320 | 404,321
44 | 2 | 105 | Cascade | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. |  |  | IEEE Float | R/W | 4322 | 404,323
44 | 2 | 106 | Cascade | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. |  |  | IEEE Float | R/W | 4324 | 404,325
44 | 2 | 108 | Cascade | Base | Heat Proportional Band Outer Loop 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4326 | 404,327
44 | 2 | 109 | Cascade | Base | Cool Proportional Band Outer Loop 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4328 | 404,329
44 | 2 | 110 | Cascade | Base | Integral Outer Loop 1 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4330 | 404,331
44 | 2 | 111 | Cascade | Base | Derivative Outer Loop 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4332 | 404,333
44 | 2 | 112 | Cascade | Base | Heat Proportional Band Outer Loop 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4334 | 404,335
44 | 2 | 113 | Cascade | Base | Cool Proportional Band Outer Loop 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4336 | 404,337
44 | 2 | 114 | Cascade | Base | Integral Outer Loop 2 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4338 | 404,339
44 | 2 | 115 | Cascade | Base | Derivative Outer Loop 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4340 | 404,341
44 | 2 | 116 | Cascade | Base | Heat Proportional Band Outer Loop 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4342 | 404,343
44 | 2 | 117 | Cascade | Base | Cool Proportional Band Outer Loop 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4344 | 404,345
44 | 2 | 118 | Cascade | Base | Integral Outer Loop 3 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4346 | 404,347
44 | 2 | 119 | Cascade | Base | Derivative Outer Loop 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4348 | 404,349
44 | 2 | 120 | Cascade | Base | Heat Proportional Band Outer Loop 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4350 | 404,351
44 | 2 | 121 | Cascade | Base | Cool Proportional Band Outer Loop 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4352 | 404,353
44 | 2 | 122 | Cascade | Base | Integral Outer Loop 4 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4354 | 404,355
44 | 2 | 123 | Cascade | Base | Derivative Outer Loop 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4356 | 404,357
44 | 2 | 124 | Cascade | Base | Heat Proportional Band Outer Loop 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4358 | 404,359
44 | 2 | 125 | Cascade | Base | Cool Proportional Band Outer Loop 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 4360 | 404,361
44 | 2 | 126 | Cascade | Base | Integral Outer Loop 5 | Set the PID integral action for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 4362 | 404,363
44 | 2 | 127 | Cascade | Base | Derivative Outer Loop 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 4364 | 404,365
44 | 2 | 128 | Cascade | Base | Outer Loop Deadband | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 4366 | 404,367
44 | 2 | 131 | Cascade | Base | Outer Loop Set Point Closed | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 4390 | 404,391
44 | 2 | 141 | Cascade | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | Unsigned 8-bit | R/W | 4372 | 404,373
44 | 2 | 150 | Cascade | Base | Cascade Heat Power | Monitor the requested PID heat power. | 0.0 to 100.0 |  | IEEE Float | R | 4374 | 404,375
44 | 2 | 152 | Cascade | Base | Cascade Cool Power | Monitor the requested PID cool power. | -100.0 to 0.0 |  | IEEE Float | R | 4376 | 404,377
44 | 2 | 154 | Cascade | Base | Cascade Power | Monitor the requested PID total power. | -100.0 to 100.0 |  | IEEE Float | R | 4378 | 404,379
44 | 2 | 163 | Cascade | Base | Source Value A | Monitor process value feedback for the outer loop while in auto mode. |  |  | IEEE Float | R | 4380 | 404,381
44 | 2 | 167 | Cascade | Base | Source Value B | Monitor the source input value used by the inner control loop while in auto mode. |  |  | IEEE Float | R | 4382 | 404,383
44 | 2 | 171 | Cascade | Base | Source Value C | Monitor the remote set point value. |  |  | IEEE Float | R | 4384 | 404,385
44 | 2 | 175 | Cascade | Base | Source Value D | Monitor the set point used by the control loop while a profile is active. |  |  | IEEE Float | R | 4386 | 404,387
44 | 2 | 206 | Cascade | Base | Simple Set Point Enable | Set to switch off cascade feature. | On (63), Off (62) | Off (62) | Enumeration | R/W | 4400 | 404,401
44 | 2 | 207 | Cascade | Base | Cascade Control Mode Is Off | Monitor Cascade Control Mode is Off | On (63), Off (62) |  | Enumeration | R | 4404 | 404,405
44 | 2 | 208 | Cascade | Base | Set Point | Monitor Closed Loop Set Point |  |  | IEEE Float | R | 4406 | 404,407
46 | 1 | 1 | Function Key | Base | Function | Set the soft key action. | Momentary (1714), Toggle (1713), On Pulse (1471) | Momentary (1714) | Enumeration | R/W | 6840 | 406,841
46 | 1 | 2 | Function Key | Base | Time | Set the pulse time If function is On Pulse. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 6842 | 406,843
46 | 1 | 3 | Function Key | Base | Input State | Monitor the key state. | On (63), Off (62) |  | Enumeration | R | 6844 | 406,845
46 | 1 | 6 | Function Key | Base | Key Action | Set when the action occurs. | Down (1457), Up (1456) | Up (1456) | Enumeration | R/W | 6850 | 406,851
46 | 1 | 7 | Function Key | Base | Error | Monitor the error for key actions. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 6852 | 406,853
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49420 | 449,421
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49421 | 449,422
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49422 | 449,423
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49423 | 449,424
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49424 | 449,425
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49425 | 449,426
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49426 | 449,427
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49427 | 449,428
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49428 | 449,429
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49429 | 449,430
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49430 | 449,431
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49431 | 449,432
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49432 | 449,433
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49433 | 449,434
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49434 | 449,435
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49435 | 449,436
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49436 | 449,437
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49437 | 449,438
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49438 | 449,439
46 | 1 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49439 | 449,440
46 | 2 | 1 | Function Key | Base | Function | Set the soft key action. | Momentary (1714), Toggle (1713), On Pulse (1471) | Momentary (1714) | Enumeration | R/W | 6860 | 406,861
46 | 2 | 2 | Function Key | Base | Time | Set the pulse time If function is On Pulse. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 6862 | 406,863
46 | 2 | 3 | Function Key | Base | Input State | Monitor the key state. | On (63), Off (62) |  | Enumeration | R | 6864 | 406,865
46 | 2 | 6 | Function Key | Base | Key Action | Set when the action occurs. | Down (1457), Up (1456) | Up (1456) | Enumeration | R/W | 6870 | 406,871
46 | 2 | 7 | Function Key | Base | Error | Monitor the error for key actions. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 6872 | 406,873
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49440 | 449,441
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49441 | 449,442
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49442 | 449,443
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49443 | 449,444
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49444 | 449,445
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49445 | 449,446
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49446 | 449,447
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49447 | 449,448
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49448 | 449,449
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49449 | 449,450
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49450 | 449,451
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49451 | 449,452
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49452 | 449,453
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49453 | 449,454
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49454 | 449,455
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49455 | 449,456
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49456 | 449,457
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49457 | 449,458
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49458 | 449,459
46 | 2 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49459 | 449,460
46 | 3 | 1 | Function Key | Base | Function | Set the soft key action. | Momentary (1714), Toggle (1713), On Pulse (1471) | Momentary (1714) | Enumeration | R/W | 6880 | 406,881
46 | 3 | 2 | Function Key | Base | Time | Set the pulse time If function is On Pulse. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 6882 | 406,883
46 | 3 | 3 | Function Key | Base | Input State | Monitor the key state. | On (63), Off (62) |  | Enumeration | R | 6884 | 406,885
46 | 3 | 6 | Function Key | Base | Key Action | Set when the action occurs. | Down (1457), Up (1456) | Up (1456) | Enumeration | R/W | 6890 | 406,891
46 | 3 | 7 | Function Key | Base | Error | Monitor the error for key actions. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 6892 | 406,893
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49460 | 449,461
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49461 | 449,462
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49462 | 449,463
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49463 | 449,464
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49464 | 449,465
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49465 | 449,466
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49466 | 449,467
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49467 | 449,468
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49468 | 449,469
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49469 | 449,470
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49470 | 449,471
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49471 | 449,472
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49472 | 449,473
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49473 | 449,474
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49474 | 449,475
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49475 | 449,476
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49476 | 449,477
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49477 | 449,478
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49478 | 449,479
46 | 3 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49479 | 449,480
46 | 4 | 1 | Function Key | Base | Function | Set the soft key action. | Momentary (1714), Toggle (1713), On Pulse (1471) | Momentary (1714) | Enumeration | R/W | 6900 | 406,901
46 | 4 | 2 | Function Key | Base | Time | Set the pulse time If function is On Pulse. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 6902 | 406,903
46 | 4 | 3 | Function Key | Base | Input State | Monitor the key state. | On (63), Off (62) |  | Enumeration | R | 6904 | 406,905
46 | 4 | 6 | Function Key | Base | Key Action | Set when the action occurs. | Down (1457), Up (1456) | Up (1456) | Enumeration | R/W | 6910 | 406,911
46 | 4 | 7 | Function Key | Base | Error | Monitor the error for key actions. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 6912 | 406,913
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49480 | 449,481
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49481 | 449,482
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49482 | 449,483
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49483 | 449,484
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49484 | 449,485
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49485 | 449,486
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49486 | 449,487
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49487 | 449,488
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49488 | 449,489
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49489 | 449,490
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49490 | 449,491
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49491 | 449,492
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49492 | 449,493
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49493 | 449,494
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49494 | 449,495
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49495 | 449,496
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49496 | 449,497
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49497 | 449,498
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49498 | 449,499
46 | 4 | 8 | Function Key | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49499 | 449,500
55 | 1 | 1 | Universal Input | 1 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 27586 | 427,587
55 | 1 | 2 | Universal Input | 1 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 27588 | 427,589
55 | 1 | 3 | Universal Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 27590 | 427,591
55 | 1 | 4 | Universal Input | 1 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 27592 | 427,593
55 | 1 | 5 | Universal Input | 1 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 27594 | 427,595
55 | 1 | 6 | Universal Input | 1 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 27596 | 427,597
55 | 1 | 7 | Universal Input | 1 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 27598 | 427,599
55 | 1 | 8 | Universal Input | 1 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 27600 | 427,601
55 | 1 | 9 | Universal Input | 1 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 27602 | 427,603
55 | 1 | 10 | Universal Input | 1 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27604 | 427,605
55 | 1 | 11 | Universal Input | 1 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 27606 | 427,607
55 | 1 | 12 | Universal Input | 1 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 27608 | 427,609
55 | 1 | 13 | Universal Input | 1 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 27610 | 427,611
55 | 1 | 14 | Universal Input | 1 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 27612 | 427,613
55 | 1 | 15 | Universal Input | 1 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 27614 | 427,615
55 | 1 | 16 | Universal Input | 1 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27616 | 427,617
55 | 1 | 17 | Universal Input | 1 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 27618 | 427,619
55 | 1 | 18 | Universal Input | 1 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 27620 | 427,621
55 | 1 | 28 | Universal Input | 1 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 27640 | 427,641
55 | 1 | 29 | Universal Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 27642 | 427,643
55 | 1 | 30 | Universal Input | 1 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 27644 | 427,645
55 | 1 | 31 | Universal Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 27646 | 427,647
55 | 1 | 35 | Universal Input | 1 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27654 | 427,655
55 | 1 | 36 | Universal Input | 1 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27656 | 427,657
55 | 1 | 37 | Universal Input | 1 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 27658 | 427,659
55 | 1 | 38 | Universal Input | 1 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 27660 | 427,661
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49500 | 449,501
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49501 | 449,502
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49502 | 449,503
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49503 | 449,504
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49504 | 449,505
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49505 | 449,506
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49506 | 449,507
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49507 | 449,508
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49508 | 449,509
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49509 | 449,510
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49510 | 449,511
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49511 | 449,512
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49512 | 449,513
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49513 | 449,514
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49514 | 449,515
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49515 | 449,516
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49516 | 449,517
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49517 | 449,518
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49518 | 449,519
55 | 1 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49519 | 449,520
55 | 1 | 48 | Universal Input | 1 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 27680 | 427,681
55 | 2 | 1 | Universal Input | 1 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 27696 | 427,697
55 | 2 | 2 | Universal Input | 1 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 27698 | 427,699
55 | 2 | 3 | Universal Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 27700 | 427,701
55 | 2 | 4 | Universal Input | 1 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 27702 | 427,703
55 | 2 | 5 | Universal Input | 1 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 27704 | 427,705
55 | 2 | 6 | Universal Input | 1 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 27706 | 427,707
55 | 2 | 7 | Universal Input | 1 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 27708 | 427,709
55 | 2 | 8 | Universal Input | 1 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 27710 | 427,711
55 | 2 | 9 | Universal Input | 1 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 27712 | 427,713
55 | 2 | 10 | Universal Input | 1 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27714 | 427,715
55 | 2 | 11 | Universal Input | 1 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 27716 | 427,717
55 | 2 | 12 | Universal Input | 1 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 27718 | 427,719
55 | 2 | 13 | Universal Input | 1 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 27720 | 427,721
55 | 2 | 14 | Universal Input | 1 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 27722 | 427,723
55 | 2 | 15 | Universal Input | 1 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 27724 | 427,725
55 | 2 | 16 | Universal Input | 1 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27726 | 427,727
55 | 2 | 17 | Universal Input | 1 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 27728 | 427,729
55 | 2 | 18 | Universal Input | 1 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 27730 | 427,731
55 | 2 | 28 | Universal Input | 1 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 27750 | 427,751
55 | 2 | 29 | Universal Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 27752 | 427,753
55 | 2 | 30 | Universal Input | 1 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 27754 | 427,755
55 | 2 | 31 | Universal Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 27756 | 427,757
55 | 2 | 35 | Universal Input | 1 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27764 | 427,765
55 | 2 | 36 | Universal Input | 1 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27766 | 427,767
55 | 2 | 37 | Universal Input | 1 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 27768 | 427,769
55 | 2 | 38 | Universal Input | 1 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 27770 | 427,771
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49520 | 449,521
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49521 | 449,522
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49522 | 449,523
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49523 | 449,524
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49524 | 449,525
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49525 | 449,526
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49526 | 449,527
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49527 | 449,528
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49528 | 449,529
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49529 | 449,530
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49530 | 449,531
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49531 | 449,532
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49532 | 449,533
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49533 | 449,534
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49534 | 449,535
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49535 | 449,536
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49536 | 449,537
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49537 | 449,538
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49538 | 449,539
55 | 2 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49539 | 449,540
55 | 2 | 48 | Universal Input | 1 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 27790 | 427,791
55 | 3 | 1 | Universal Input | 1 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 27806 | 427,807
55 | 3 | 2 | Universal Input | 1 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 27808 | 427,809
55 | 3 | 3 | Universal Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 27810 | 427,811
55 | 3 | 4 | Universal Input | 1 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 27812 | 427,813
55 | 3 | 5 | Universal Input | 1 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 27814 | 427,815
55 | 3 | 6 | Universal Input | 1 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 27816 | 427,817
55 | 3 | 7 | Universal Input | 1 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 27818 | 427,819
55 | 3 | 8 | Universal Input | 1 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 27820 | 427,821
55 | 3 | 9 | Universal Input | 1 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 27822 | 427,823
55 | 3 | 10 | Universal Input | 1 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27824 | 427,825
55 | 3 | 11 | Universal Input | 1 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 27826 | 427,827
55 | 3 | 12 | Universal Input | 1 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 27828 | 427,829
55 | 3 | 13 | Universal Input | 1 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 27830 | 427,831
55 | 3 | 14 | Universal Input | 1 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 27832 | 427,833
55 | 3 | 15 | Universal Input | 1 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 27834 | 427,835
55 | 3 | 16 | Universal Input | 1 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27836 | 427,837
55 | 3 | 17 | Universal Input | 1 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 27838 | 427,839
55 | 3 | 18 | Universal Input | 1 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 27840 | 427,841
55 | 3 | 28 | Universal Input | 1 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 27860 | 427,861
55 | 3 | 29 | Universal Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 27862 | 427,863
55 | 3 | 30 | Universal Input | 1 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 27864 | 427,865
55 | 3 | 31 | Universal Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 27866 | 427,867
55 | 3 | 35 | Universal Input | 1 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27874 | 427,875
55 | 3 | 36 | Universal Input | 1 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27876 | 427,877
55 | 3 | 37 | Universal Input | 1 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 27878 | 427,879
55 | 3 | 38 | Universal Input | 1 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 27880 | 427,881
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49540 | 449,541
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49541 | 449,542
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49542 | 449,543
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49543 | 449,544
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49544 | 449,545
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49545 | 449,546
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49546 | 449,547
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49547 | 449,548
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49548 | 449,549
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49549 | 449,550
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49550 | 449,551
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49551 | 449,552
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49552 | 449,553
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49553 | 449,554
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49554 | 449,555
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49555 | 449,556
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49556 | 449,557
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49557 | 449,558
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49558 | 449,559
55 | 3 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49559 | 449,560
55 | 3 | 48 | Universal Input | 1 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 27900 | 427,901
55 | 4 | 1 | Universal Input | 1 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 27916 | 427,917
55 | 4 | 2 | Universal Input | 1 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 27918 | 427,919
55 | 4 | 3 | Universal Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 27920 | 427,921
55 | 4 | 4 | Universal Input | 1 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 27922 | 427,923
55 | 4 | 5 | Universal Input | 1 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 27924 | 427,925
55 | 4 | 6 | Universal Input | 1 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 27926 | 427,927
55 | 4 | 7 | Universal Input | 1 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 27928 | 427,929
55 | 4 | 8 | Universal Input | 1 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 27930 | 427,931
55 | 4 | 9 | Universal Input | 1 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 27932 | 427,933
55 | 4 | 10 | Universal Input | 1 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27934 | 427,935
55 | 4 | 11 | Universal Input | 1 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 27936 | 427,937
55 | 4 | 12 | Universal Input | 1 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 27938 | 427,939
55 | 4 | 13 | Universal Input | 1 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 27940 | 427,941
55 | 4 | 14 | Universal Input | 1 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 27942 | 427,943
55 | 4 | 15 | Universal Input | 1 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 27944 | 427,945
55 | 4 | 16 | Universal Input | 1 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27946 | 427,947
55 | 4 | 17 | Universal Input | 1 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 27948 | 427,949
55 | 4 | 18 | Universal Input | 1 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 27950 | 427,951
55 | 4 | 28 | Universal Input | 1 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 27970 | 427,971
55 | 4 | 29 | Universal Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 27972 | 427,973
55 | 4 | 30 | Universal Input | 1 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 27974 | 427,975
55 | 4 | 31 | Universal Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 27976 | 427,977
55 | 4 | 35 | Universal Input | 1 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27984 | 427,985
55 | 4 | 36 | Universal Input | 1 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27986 | 427,987
55 | 4 | 37 | Universal Input | 1 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 27988 | 427,989
55 | 4 | 38 | Universal Input | 1 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 27990 | 427,991
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49560 | 449,561
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49561 | 449,562
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49562 | 449,563
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49563 | 449,564
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49564 | 449,565
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49565 | 449,566
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49566 | 449,567
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49567 | 449,568
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49568 | 449,569
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49569 | 449,570
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49570 | 449,571
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49571 | 449,572
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49572 | 449,573
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49573 | 449,574
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49574 | 449,575
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49575 | 449,576
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49576 | 449,577
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49577 | 449,578
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49578 | 449,579
55 | 4 | 47 | Universal Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49579 | 449,580
55 | 4 | 48 | Universal Input | 1 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 28010 | 428,011
55 | 11 | 1 | Universal Input | 2 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28026 | 428,027
55 | 11 | 2 | Universal Input | 2 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 28028 | 428,029
55 | 11 | 3 | Universal Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 28030 | 428,031
55 | 11 | 4 | Universal Input | 2 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28032 | 428,033
55 | 11 | 5 | Universal Input | 2 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 28034 | 428,035
55 | 11 | 6 | Universal Input | 2 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 28036 | 428,037
55 | 11 | 7 | Universal Input | 2 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 28038 | 428,039
55 | 11 | 8 | Universal Input | 2 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28040 | 428,041
55 | 11 | 9 | Universal Input | 2 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 28042 | 428,043
55 | 11 | 10 | Universal Input | 2 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28044 | 428,045
55 | 11 | 11 | Universal Input | 2 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 28046 | 428,047
55 | 11 | 12 | Universal Input | 2 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 28048 | 428,049
55 | 11 | 13 | Universal Input | 2 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28050 | 428,051
55 | 11 | 14 | Universal Input | 2 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 28052 | 428,053
55 | 11 | 15 | Universal Input | 2 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 28054 | 428,055
55 | 11 | 16 | Universal Input | 2 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28056 | 428,057
55 | 11 | 17 | Universal Input | 2 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 28058 | 428,059
55 | 11 | 18 | Universal Input | 2 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 28060 | 428,061
55 | 11 | 28 | Universal Input | 2 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 28080 | 428,081
55 | 11 | 29 | Universal Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28082 | 428,083
55 | 11 | 30 | Universal Input | 2 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 28084 | 428,085
55 | 11 | 31 | Universal Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28086 | 428,087
55 | 11 | 35 | Universal Input | 2 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28094 | 428,095
55 | 11 | 36 | Universal Input | 2 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28096 | 428,097
55 | 11 | 37 | Universal Input | 2 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28098 | 428,099
55 | 11 | 38 | Universal Input | 2 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28100 | 428,101
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49580 | 449,581
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49581 | 449,582
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49582 | 449,583
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49583 | 449,584
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49584 | 449,585
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49585 | 449,586
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49586 | 449,587
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49587 | 449,588
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49588 | 449,589
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49589 | 449,590
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49590 | 449,591
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49591 | 449,592
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49592 | 449,593
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49593 | 449,594
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49594 | 449,595
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49595 | 449,596
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49596 | 449,597
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49597 | 449,598
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49598 | 449,599
55 | 11 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49599 | 449,600
55 | 11 | 48 | Universal Input | 2 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 28120 | 428,121
55 | 12 | 1 | Universal Input | 2 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28136 | 428,137
55 | 12 | 2 | Universal Input | 2 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 28138 | 428,139
55 | 12 | 3 | Universal Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 28140 | 428,141
55 | 12 | 4 | Universal Input | 2 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28142 | 428,143
55 | 12 | 5 | Universal Input | 2 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 28144 | 428,145
55 | 12 | 6 | Universal Input | 2 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 28146 | 428,147
55 | 12 | 7 | Universal Input | 2 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 28148 | 428,149
55 | 12 | 8 | Universal Input | 2 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28150 | 428,151
55 | 12 | 9 | Universal Input | 2 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 28152 | 428,153
55 | 12 | 10 | Universal Input | 2 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28154 | 428,155
55 | 12 | 11 | Universal Input | 2 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 28156 | 428,157
55 | 12 | 12 | Universal Input | 2 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 28158 | 428,159
55 | 12 | 13 | Universal Input | 2 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28160 | 428,161
55 | 12 | 14 | Universal Input | 2 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 28162 | 428,163
55 | 12 | 15 | Universal Input | 2 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 28164 | 428,165
55 | 12 | 16 | Universal Input | 2 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28166 | 428,167
55 | 12 | 17 | Universal Input | 2 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 28168 | 428,169
55 | 12 | 18 | Universal Input | 2 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 28170 | 428,171
55 | 12 | 28 | Universal Input | 2 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 28190 | 428,191
55 | 12 | 29 | Universal Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28192 | 428,193
55 | 12 | 30 | Universal Input | 2 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 28194 | 428,195
55 | 12 | 31 | Universal Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28196 | 428,197
55 | 12 | 35 | Universal Input | 2 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28204 | 428,205
55 | 12 | 36 | Universal Input | 2 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28206 | 428,207
55 | 12 | 37 | Universal Input | 2 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28208 | 428,209
55 | 12 | 38 | Universal Input | 2 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28210 | 428,211
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49600 | 449,601
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49601 | 449,602
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49602 | 449,603
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49603 | 449,604
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49604 | 449,605
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49605 | 449,606
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49606 | 449,607
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49607 | 449,608
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49608 | 449,609
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49609 | 449,610
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49610 | 449,611
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49611 | 449,612
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49612 | 449,613
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49613 | 449,614
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49614 | 449,615
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49615 | 449,616
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49616 | 449,617
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49617 | 449,618
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49618 | 449,619
55 | 12 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49619 | 449,620
55 | 12 | 48 | Universal Input | 2 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 28230 | 428,231
55 | 13 | 1 | Universal Input | 2 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28246 | 428,247
55 | 13 | 2 | Universal Input | 2 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 28248 | 428,249
55 | 13 | 3 | Universal Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 28250 | 428,251
55 | 13 | 4 | Universal Input | 2 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28252 | 428,253
55 | 13 | 5 | Universal Input | 2 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 28254 | 428,255
55 | 13 | 6 | Universal Input | 2 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 28256 | 428,257
55 | 13 | 7 | Universal Input | 2 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 28258 | 428,259
55 | 13 | 8 | Universal Input | 2 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28260 | 428,261
55 | 13 | 9 | Universal Input | 2 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 28262 | 428,263
55 | 13 | 10 | Universal Input | 2 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28264 | 428,265
55 | 13 | 11 | Universal Input | 2 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 28266 | 428,267
55 | 13 | 12 | Universal Input | 2 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 28268 | 428,269
55 | 13 | 13 | Universal Input | 2 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28270 | 428,271
55 | 13 | 14 | Universal Input | 2 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 28272 | 428,273
55 | 13 | 15 | Universal Input | 2 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 28274 | 428,275
55 | 13 | 16 | Universal Input | 2 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28276 | 428,277
55 | 13 | 17 | Universal Input | 2 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 28278 | 428,279
55 | 13 | 18 | Universal Input | 2 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 28280 | 428,281
55 | 13 | 28 | Universal Input | 2 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 28300 | 428,301
55 | 13 | 29 | Universal Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28302 | 428,303
55 | 13 | 30 | Universal Input | 2 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 28304 | 428,305
55 | 13 | 31 | Universal Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28306 | 428,307
55 | 13 | 35 | Universal Input | 2 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28314 | 428,315
55 | 13 | 36 | Universal Input | 2 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28316 | 428,317
55 | 13 | 37 | Universal Input | 2 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28318 | 428,319
55 | 13 | 38 | Universal Input | 2 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28320 | 428,321
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49620 | 449,621
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49621 | 449,622
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49622 | 449,623
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49623 | 449,624
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49624 | 449,625
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49625 | 449,626
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49626 | 449,627
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49627 | 449,628
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49628 | 449,629
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49629 | 449,630
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49630 | 449,631
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49631 | 449,632
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49632 | 449,633
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49633 | 449,634
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49634 | 449,635
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49635 | 449,636
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49636 | 449,637
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49637 | 449,638
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49638 | 449,639
55 | 13 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49639 | 449,640
55 | 13 | 48 | Universal Input | 2 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 28340 | 428,341
55 | 14 | 1 | Universal Input | 2 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28356 | 428,357
55 | 14 | 2 | Universal Input | 2 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 28358 | 428,359
55 | 14 | 3 | Universal Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 28360 | 428,361
55 | 14 | 4 | Universal Input | 2 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28362 | 428,363
55 | 14 | 5 | Universal Input | 2 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 28364 | 428,365
55 | 14 | 6 | Universal Input | 2 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 28366 | 428,367
55 | 14 | 7 | Universal Input | 2 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 28368 | 428,369
55 | 14 | 8 | Universal Input | 2 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28370 | 428,371
55 | 14 | 9 | Universal Input | 2 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 28372 | 428,373
55 | 14 | 10 | Universal Input | 2 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28374 | 428,375
55 | 14 | 11 | Universal Input | 2 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 28376 | 428,377
55 | 14 | 12 | Universal Input | 2 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 28378 | 428,379
55 | 14 | 13 | Universal Input | 2 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28380 | 428,381
55 | 14 | 14 | Universal Input | 2 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 28382 | 428,383
55 | 14 | 15 | Universal Input | 2 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 28384 | 428,385
55 | 14 | 16 | Universal Input | 2 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28386 | 428,387
55 | 14 | 17 | Universal Input | 2 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 28388 | 428,389
55 | 14 | 18 | Universal Input | 2 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 28390 | 428,391
55 | 14 | 28 | Universal Input | 2 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 28410 | 428,411
55 | 14 | 29 | Universal Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28412 | 428,413
55 | 14 | 30 | Universal Input | 2 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 28414 | 428,415
55 | 14 | 31 | Universal Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28416 | 428,417
55 | 14 | 35 | Universal Input | 2 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28424 | 428,425
55 | 14 | 36 | Universal Input | 2 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28426 | 428,427
55 | 14 | 37 | Universal Input | 2 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28428 | 428,429
55 | 14 | 38 | Universal Input | 2 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28430 | 428,431
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49640 | 449,641
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49641 | 449,642
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49642 | 449,643
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49643 | 449,644
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49644 | 449,645
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49645 | 449,646
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49646 | 449,647
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49647 | 449,648
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49648 | 449,649
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49649 | 449,650
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49650 | 449,651
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49651 | 449,652
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49652 | 449,653
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49653 | 449,654
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49654 | 449,655
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49655 | 449,656
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49656 | 449,657
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49657 | 449,658
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49658 | 449,659
55 | 14 | 47 | Universal Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49659 | 449,660
55 | 14 | 48 | Universal Input | 2 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 28450 | 428,451
55 | 21 | 1 | Universal Input | 3 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28466 | 428,467
55 | 21 | 2 | Universal Input | 3 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 28468 | 428,469
55 | 21 | 3 | Universal Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 28470 | 428,471
55 | 21 | 4 | Universal Input | 3 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28472 | 428,473
55 | 21 | 5 | Universal Input | 3 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 28474 | 428,475
55 | 21 | 6 | Universal Input | 3 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 28476 | 428,477
55 | 21 | 7 | Universal Input | 3 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 28478 | 428,479
55 | 21 | 8 | Universal Input | 3 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28480 | 428,481
55 | 21 | 9 | Universal Input | 3 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 28482 | 428,483
55 | 21 | 10 | Universal Input | 3 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28484 | 428,485
55 | 21 | 11 | Universal Input | 3 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 28486 | 428,487
55 | 21 | 12 | Universal Input | 3 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 28488 | 428,489
55 | 21 | 13 | Universal Input | 3 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28490 | 428,491
55 | 21 | 14 | Universal Input | 3 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 28492 | 428,493
55 | 21 | 15 | Universal Input | 3 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 28494 | 428,495
55 | 21 | 16 | Universal Input | 3 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28496 | 428,497
55 | 21 | 17 | Universal Input | 3 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 28498 | 428,499
55 | 21 | 18 | Universal Input | 3 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 28500 | 428,501
55 | 21 | 28 | Universal Input | 3 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 28520 | 428,521
55 | 21 | 29 | Universal Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28522 | 428,523
55 | 21 | 30 | Universal Input | 3 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 28524 | 428,525
55 | 21 | 31 | Universal Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28526 | 428,527
55 | 21 | 35 | Universal Input | 3 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28534 | 428,535
55 | 21 | 36 | Universal Input | 3 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28536 | 428,537
55 | 21 | 37 | Universal Input | 3 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28538 | 428,539
55 | 21 | 38 | Universal Input | 3 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28540 | 428,541
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49660 | 449,661
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49661 | 449,662
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49662 | 449,663
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49663 | 449,664
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49664 | 449,665
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49665 | 449,666
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49666 | 449,667
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49667 | 449,668
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49668 | 449,669
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49669 | 449,670
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49670 | 449,671
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49671 | 449,672
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49672 | 449,673
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49673 | 449,674
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49674 | 449,675
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49675 | 449,676
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49676 | 449,677
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49677 | 449,678
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49678 | 449,679
55 | 21 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49679 | 449,680
55 | 21 | 48 | Universal Input | 3 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 28560 | 428,561
55 | 22 | 1 | Universal Input | 3 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28576 | 428,577
55 | 22 | 2 | Universal Input | 3 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 28578 | 428,579
55 | 22 | 3 | Universal Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 28580 | 428,581
55 | 22 | 4 | Universal Input | 3 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28582 | 428,583
55 | 22 | 5 | Universal Input | 3 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 28584 | 428,585
55 | 22 | 6 | Universal Input | 3 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 28586 | 428,587
55 | 22 | 7 | Universal Input | 3 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 28588 | 428,589
55 | 22 | 8 | Universal Input | 3 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28590 | 428,591
55 | 22 | 9 | Universal Input | 3 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 28592 | 428,593
55 | 22 | 10 | Universal Input | 3 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28594 | 428,595
55 | 22 | 11 | Universal Input | 3 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 28596 | 428,597
55 | 22 | 12 | Universal Input | 3 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 28598 | 428,599
55 | 22 | 13 | Universal Input | 3 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28600 | 428,601
55 | 22 | 14 | Universal Input | 3 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 28602 | 428,603
55 | 22 | 15 | Universal Input | 3 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 28604 | 428,605
55 | 22 | 16 | Universal Input | 3 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28606 | 428,607
55 | 22 | 17 | Universal Input | 3 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 28608 | 428,609
55 | 22 | 18 | Universal Input | 3 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 28610 | 428,611
55 | 22 | 28 | Universal Input | 3 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 28630 | 428,631
55 | 22 | 29 | Universal Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28632 | 428,633
55 | 22 | 30 | Universal Input | 3 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 28634 | 428,635
55 | 22 | 31 | Universal Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28636 | 428,637
55 | 22 | 35 | Universal Input | 3 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28644 | 428,645
55 | 22 | 36 | Universal Input | 3 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28646 | 428,647
55 | 22 | 37 | Universal Input | 3 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28648 | 428,649
55 | 22 | 38 | Universal Input | 3 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28650 | 428,651
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49680 | 449,681
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49681 | 449,682
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49682 | 449,683
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49683 | 449,684
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49684 | 449,685
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49685 | 449,686
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49686 | 449,687
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49687 | 449,688
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49688 | 449,689
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49689 | 449,690
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49690 | 449,691
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49691 | 449,692
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49692 | 449,693
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49693 | 449,694
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49694 | 449,695
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49695 | 449,696
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49696 | 449,697
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49697 | 449,698
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49698 | 449,699
55 | 22 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49699 | 449,700
55 | 22 | 48 | Universal Input | 3 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 28670 | 428,671
55 | 23 | 1 | Universal Input | 3 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28686 | 428,687
55 | 23 | 2 | Universal Input | 3 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 28688 | 428,689
55 | 23 | 3 | Universal Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 28690 | 428,691
55 | 23 | 4 | Universal Input | 3 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28692 | 428,693
55 | 23 | 5 | Universal Input | 3 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 28694 | 428,695
55 | 23 | 6 | Universal Input | 3 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 28696 | 428,697
55 | 23 | 7 | Universal Input | 3 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 28698 | 428,699
55 | 23 | 8 | Universal Input | 3 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28700 | 428,701
55 | 23 | 9 | Universal Input | 3 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 28702 | 428,703
55 | 23 | 10 | Universal Input | 3 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28704 | 428,705
55 | 23 | 11 | Universal Input | 3 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 28706 | 428,707
55 | 23 | 12 | Universal Input | 3 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 28708 | 428,709
55 | 23 | 13 | Universal Input | 3 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28710 | 428,711
55 | 23 | 14 | Universal Input | 3 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 28712 | 428,713
55 | 23 | 15 | Universal Input | 3 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 28714 | 428,715
55 | 23 | 16 | Universal Input | 3 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28716 | 428,717
55 | 23 | 17 | Universal Input | 3 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 28718 | 428,719
55 | 23 | 18 | Universal Input | 3 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 28720 | 428,721
55 | 23 | 28 | Universal Input | 3 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 28740 | 428,741
55 | 23 | 29 | Universal Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28742 | 428,743
55 | 23 | 30 | Universal Input | 3 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 28744 | 428,745
55 | 23 | 31 | Universal Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28746 | 428,747
55 | 23 | 35 | Universal Input | 3 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28754 | 428,755
55 | 23 | 36 | Universal Input | 3 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28756 | 428,757
55 | 23 | 37 | Universal Input | 3 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28758 | 428,759
55 | 23 | 38 | Universal Input | 3 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28760 | 428,761
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49700 | 449,701
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49701 | 449,702
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49702 | 449,703
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49703 | 449,704
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49704 | 449,705
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49705 | 449,706
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49706 | 449,707
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49707 | 449,708
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49708 | 449,709
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49709 | 449,710
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49710 | 449,711
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49711 | 449,712
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49712 | 449,713
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49713 | 449,714
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49714 | 449,715
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49715 | 449,716
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49716 | 449,717
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49717 | 449,718
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49718 | 449,719
55 | 23 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49719 | 449,720
55 | 23 | 48 | Universal Input | 3 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 28780 | 428,781
55 | 24 | 1 | Universal Input | 3 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28796 | 428,797
55 | 24 | 2 | Universal Input | 3 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 28798 | 428,799
55 | 24 | 3 | Universal Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 28800 | 428,801
55 | 24 | 4 | Universal Input | 3 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28802 | 428,803
55 | 24 | 5 | Universal Input | 3 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 28804 | 428,805
55 | 24 | 6 | Universal Input | 3 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 28806 | 428,807
55 | 24 | 7 | Universal Input | 3 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 28808 | 428,809
55 | 24 | 8 | Universal Input | 3 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28810 | 428,811
55 | 24 | 9 | Universal Input | 3 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 28812 | 428,813
55 | 24 | 10 | Universal Input | 3 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28814 | 428,815
55 | 24 | 11 | Universal Input | 3 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 28816 | 428,817
55 | 24 | 12 | Universal Input | 3 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 28818 | 428,819
55 | 24 | 13 | Universal Input | 3 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28820 | 428,821
55 | 24 | 14 | Universal Input | 3 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 28822 | 428,823
55 | 24 | 15 | Universal Input | 3 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 28824 | 428,825
55 | 24 | 16 | Universal Input | 3 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28826 | 428,827
55 | 24 | 17 | Universal Input | 3 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 28828 | 428,829
55 | 24 | 18 | Universal Input | 3 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 28830 | 428,831
55 | 24 | 28 | Universal Input | 3 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 28850 | 428,851
55 | 24 | 29 | Universal Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28852 | 428,853
55 | 24 | 30 | Universal Input | 3 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 28854 | 428,855
55 | 24 | 31 | Universal Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28856 | 428,857
55 | 24 | 35 | Universal Input | 3 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28864 | 428,865
55 | 24 | 36 | Universal Input | 3 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28866 | 428,867
55 | 24 | 37 | Universal Input | 3 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28868 | 428,869
55 | 24 | 38 | Universal Input | 3 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28870 | 428,871
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49720 | 449,721
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49721 | 449,722
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49722 | 449,723
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49723 | 449,724
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49724 | 449,725
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49725 | 449,726
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49726 | 449,727
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49727 | 449,728
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49728 | 449,729
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49729 | 449,730
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49730 | 449,731
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49731 | 449,732
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49732 | 449,733
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49733 | 449,734
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49734 | 449,735
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49735 | 449,736
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49736 | 449,737
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49737 | 449,738
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49738 | 449,739
55 | 24 | 47 | Universal Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49739 | 449,740
55 | 24 | 48 | Universal Input | 3 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 28890 | 428,891
55 | 31 | 1 | Universal Input | 4 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28906 | 428,907
55 | 31 | 2 | Universal Input | 4 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 28908 | 428,909
55 | 31 | 3 | Universal Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 28910 | 428,911
55 | 31 | 4 | Universal Input | 4 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28912 | 428,913
55 | 31 | 5 | Universal Input | 4 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 28914 | 428,915
55 | 31 | 6 | Universal Input | 4 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 28916 | 428,917
55 | 31 | 7 | Universal Input | 4 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 28918 | 428,919
55 | 31 | 8 | Universal Input | 4 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28920 | 428,921
55 | 31 | 9 | Universal Input | 4 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 28922 | 428,923
55 | 31 | 10 | Universal Input | 4 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28924 | 428,925
55 | 31 | 11 | Universal Input | 4 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 28926 | 428,927
55 | 31 | 12 | Universal Input | 4 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 28928 | 428,929
55 | 31 | 13 | Universal Input | 4 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 28930 | 428,931
55 | 31 | 14 | Universal Input | 4 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 28932 | 428,933
55 | 31 | 15 | Universal Input | 4 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 28934 | 428,935
55 | 31 | 16 | Universal Input | 4 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28936 | 428,937
55 | 31 | 17 | Universal Input | 4 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 28938 | 428,939
55 | 31 | 18 | Universal Input | 4 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 28940 | 428,941
55 | 31 | 28 | Universal Input | 4 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 28960 | 428,961
55 | 31 | 29 | Universal Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28962 | 428,963
55 | 31 | 30 | Universal Input | 4 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 28964 | 428,965
55 | 31 | 31 | Universal Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 28966 | 428,967
55 | 31 | 35 | Universal Input | 4 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28974 | 428,975
55 | 31 | 36 | Universal Input | 4 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 28976 | 428,977
55 | 31 | 37 | Universal Input | 4 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28978 | 428,979
55 | 31 | 38 | Universal Input | 4 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 28980 | 428,981
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49740 | 449,741
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49741 | 449,742
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49742 | 449,743
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49743 | 449,744
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49744 | 449,745
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49745 | 449,746
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49746 | 449,747
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49747 | 449,748
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49748 | 449,749
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49749 | 449,750
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49750 | 449,751
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49751 | 449,752
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49752 | 449,753
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49753 | 449,754
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49754 | 449,755
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49755 | 449,756
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49756 | 449,757
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49757 | 449,758
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49758 | 449,759
55 | 31 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49759 | 449,760
55 | 31 | 48 | Universal Input | 4 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 29000 | 429,001
55 | 32 | 1 | Universal Input | 4 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29016 | 429,017
55 | 32 | 2 | Universal Input | 4 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 29018 | 429,019
55 | 32 | 3 | Universal Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 29020 | 429,021
55 | 32 | 4 | Universal Input | 4 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29022 | 429,023
55 | 32 | 5 | Universal Input | 4 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 29024 | 429,025
55 | 32 | 6 | Universal Input | 4 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 29026 | 429,027
55 | 32 | 7 | Universal Input | 4 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 29028 | 429,029
55 | 32 | 8 | Universal Input | 4 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29030 | 429,031
55 | 32 | 9 | Universal Input | 4 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 29032 | 429,033
55 | 32 | 10 | Universal Input | 4 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29034 | 429,035
55 | 32 | 11 | Universal Input | 4 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 29036 | 429,037
55 | 32 | 12 | Universal Input | 4 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 29038 | 429,039
55 | 32 | 13 | Universal Input | 4 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29040 | 429,041
55 | 32 | 14 | Universal Input | 4 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 29042 | 429,043
55 | 32 | 15 | Universal Input | 4 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 29044 | 429,045
55 | 32 | 16 | Universal Input | 4 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29046 | 429,047
55 | 32 | 17 | Universal Input | 4 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 29048 | 429,049
55 | 32 | 18 | Universal Input | 4 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 29050 | 429,051
55 | 32 | 28 | Universal Input | 4 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 29070 | 429,071
55 | 32 | 29 | Universal Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29072 | 429,073
55 | 32 | 30 | Universal Input | 4 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 29074 | 429,075
55 | 32 | 31 | Universal Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29076 | 429,077
55 | 32 | 35 | Universal Input | 4 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29084 | 429,085
55 | 32 | 36 | Universal Input | 4 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29086 | 429,087
55 | 32 | 37 | Universal Input | 4 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29088 | 429,089
55 | 32 | 38 | Universal Input | 4 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29090 | 429,091
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49760 | 449,761
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49761 | 449,762
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49762 | 449,763
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49763 | 449,764
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49764 | 449,765
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49765 | 449,766
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49766 | 449,767
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49767 | 449,768
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49768 | 449,769
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49769 | 449,770
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49770 | 449,771
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49771 | 449,772
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49772 | 449,773
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49773 | 449,774
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49774 | 449,775
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49775 | 449,776
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49776 | 449,777
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49777 | 449,778
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49778 | 449,779
55 | 32 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49779 | 449,780
55 | 32 | 48 | Universal Input | 4 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 29110 | 429,111
55 | 33 | 1 | Universal Input | 4 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29126 | 429,127
55 | 33 | 2 | Universal Input | 4 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 29128 | 429,129
55 | 33 | 3 | Universal Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 29130 | 429,131
55 | 33 | 4 | Universal Input | 4 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29132 | 429,133
55 | 33 | 5 | Universal Input | 4 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 29134 | 429,135
55 | 33 | 6 | Universal Input | 4 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 29136 | 429,137
55 | 33 | 7 | Universal Input | 4 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 29138 | 429,139
55 | 33 | 8 | Universal Input | 4 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29140 | 429,141
55 | 33 | 9 | Universal Input | 4 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 29142 | 429,143
55 | 33 | 10 | Universal Input | 4 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29144 | 429,145
55 | 33 | 11 | Universal Input | 4 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 29146 | 429,147
55 | 33 | 12 | Universal Input | 4 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 29148 | 429,149
55 | 33 | 13 | Universal Input | 4 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29150 | 429,151
55 | 33 | 14 | Universal Input | 4 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 29152 | 429,153
55 | 33 | 15 | Universal Input | 4 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 29154 | 429,155
55 | 33 | 16 | Universal Input | 4 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29156 | 429,157
55 | 33 | 17 | Universal Input | 4 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 29158 | 429,159
55 | 33 | 18 | Universal Input | 4 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 29160 | 429,161
55 | 33 | 28 | Universal Input | 4 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 29180 | 429,181
55 | 33 | 29 | Universal Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29182 | 429,183
55 | 33 | 30 | Universal Input | 4 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 29184 | 429,185
55 | 33 | 31 | Universal Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29186 | 429,187
55 | 33 | 35 | Universal Input | 4 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29194 | 429,195
55 | 33 | 36 | Universal Input | 4 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29196 | 429,197
55 | 33 | 37 | Universal Input | 4 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29198 | 429,199
55 | 33 | 38 | Universal Input | 4 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29200 | 429,201
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49780 | 449,781
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49781 | 449,782
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49782 | 449,783
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49783 | 449,784
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49784 | 449,785
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49785 | 449,786
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49786 | 449,787
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49787 | 449,788
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49788 | 449,789
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49789 | 449,790
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49790 | 449,791
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49791 | 449,792
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49792 | 449,793
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49793 | 449,794
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49794 | 449,795
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49795 | 449,796
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49796 | 449,797
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49797 | 449,798
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49798 | 449,799
55 | 33 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49799 | 449,800
55 | 33 | 48 | Universal Input | 4 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 29220 | 429,221
55 | 34 | 1 | Universal Input | 4 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29236 | 429,237
55 | 34 | 2 | Universal Input | 4 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 29238 | 429,239
55 | 34 | 3 | Universal Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 29240 | 429,241
55 | 34 | 4 | Universal Input | 4 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29242 | 429,243
55 | 34 | 5 | Universal Input | 4 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 29244 | 429,245
55 | 34 | 6 | Universal Input | 4 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 29246 | 429,247
55 | 34 | 7 | Universal Input | 4 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 29248 | 429,249
55 | 34 | 8 | Universal Input | 4 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29250 | 429,251
55 | 34 | 9 | Universal Input | 4 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 29252 | 429,253
55 | 34 | 10 | Universal Input | 4 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29254 | 429,255
55 | 34 | 11 | Universal Input | 4 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 29256 | 429,257
55 | 34 | 12 | Universal Input | 4 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 29258 | 429,259
55 | 34 | 13 | Universal Input | 4 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29260 | 429,261
55 | 34 | 14 | Universal Input | 4 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 29262 | 429,263
55 | 34 | 15 | Universal Input | 4 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 29264 | 429,265
55 | 34 | 16 | Universal Input | 4 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29266 | 429,267
55 | 34 | 17 | Universal Input | 4 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 29268 | 429,269
55 | 34 | 18 | Universal Input | 4 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 29270 | 429,271
55 | 34 | 28 | Universal Input | 4 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 29290 | 429,291
55 | 34 | 29 | Universal Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29292 | 429,293
55 | 34 | 30 | Universal Input | 4 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 29294 | 429,295
55 | 34 | 31 | Universal Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29296 | 429,297
55 | 34 | 35 | Universal Input | 4 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29304 | 429,305
55 | 34 | 36 | Universal Input | 4 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29306 | 429,307
55 | 34 | 37 | Universal Input | 4 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29308 | 429,309
55 | 34 | 38 | Universal Input | 4 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29310 | 429,311
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49800 | 449,801
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49801 | 449,802
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49802 | 449,803
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49803 | 449,804
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49804 | 449,805
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49805 | 449,806
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49806 | 449,807
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49807 | 449,808
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49808 | 449,809
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49809 | 449,810
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49810 | 449,811
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49811 | 449,812
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49812 | 449,813
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49813 | 449,814
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49814 | 449,815
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49815 | 449,816
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49816 | 449,817
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49817 | 449,818
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49818 | 449,819
55 | 34 | 47 | Universal Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49819 | 449,820
55 | 34 | 48 | Universal Input | 4 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 29330 | 429,331
55 | 41 | 1 | Universal Input | 5 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29346 | 429,347
55 | 41 | 2 | Universal Input | 5 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 29348 | 429,349
55 | 41 | 3 | Universal Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 29350 | 429,351
55 | 41 | 4 | Universal Input | 5 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29352 | 429,353
55 | 41 | 5 | Universal Input | 5 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 29354 | 429,355
55 | 41 | 6 | Universal Input | 5 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 29356 | 429,357
55 | 41 | 7 | Universal Input | 5 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 29358 | 429,359
55 | 41 | 8 | Universal Input | 5 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29360 | 429,361
55 | 41 | 9 | Universal Input | 5 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 29362 | 429,363
55 | 41 | 10 | Universal Input | 5 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29364 | 429,365
55 | 41 | 11 | Universal Input | 5 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 29366 | 429,367
55 | 41 | 12 | Universal Input | 5 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 29368 | 429,369
55 | 41 | 13 | Universal Input | 5 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29370 | 429,371
55 | 41 | 14 | Universal Input | 5 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 29372 | 429,373
55 | 41 | 15 | Universal Input | 5 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 29374 | 429,375
55 | 41 | 16 | Universal Input | 5 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29376 | 429,377
55 | 41 | 17 | Universal Input | 5 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 29378 | 429,379
55 | 41 | 18 | Universal Input | 5 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 29380 | 429,381
55 | 41 | 28 | Universal Input | 5 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 29400 | 429,401
55 | 41 | 29 | Universal Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29402 | 429,403
55 | 41 | 30 | Universal Input | 5 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 29404 | 429,405
55 | 41 | 31 | Universal Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29406 | 429,407
55 | 41 | 35 | Universal Input | 5 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29414 | 429,415
55 | 41 | 36 | Universal Input | 5 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29416 | 429,417
55 | 41 | 37 | Universal Input | 5 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29418 | 429,419
55 | 41 | 38 | Universal Input | 5 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29420 | 429,421
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49820 | 449,821
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49821 | 449,822
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49822 | 449,823
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49823 | 449,824
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49824 | 449,825
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49825 | 449,826
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49826 | 449,827
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49827 | 449,828
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49828 | 449,829
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49829 | 449,830
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49830 | 449,831
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49831 | 449,832
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49832 | 449,833
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49833 | 449,834
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49834 | 449,835
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49835 | 449,836
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49836 | 449,837
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49837 | 449,838
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49838 | 449,839
55 | 41 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49839 | 449,840
55 | 41 | 48 | Universal Input | 5 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 29440 | 429,441
55 | 42 | 1 | Universal Input | 5 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29456 | 429,457
55 | 42 | 2 | Universal Input | 5 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 29458 | 429,459
55 | 42 | 3 | Universal Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 29460 | 429,461
55 | 42 | 4 | Universal Input | 5 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29462 | 429,463
55 | 42 | 5 | Universal Input | 5 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 29464 | 429,465
55 | 42 | 6 | Universal Input | 5 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 29466 | 429,467
55 | 42 | 7 | Universal Input | 5 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 29468 | 429,469
55 | 42 | 8 | Universal Input | 5 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29470 | 429,471
55 | 42 | 9 | Universal Input | 5 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 29472 | 429,473
55 | 42 | 10 | Universal Input | 5 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29474 | 429,475
55 | 42 | 11 | Universal Input | 5 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 29476 | 429,477
55 | 42 | 12 | Universal Input | 5 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 29478 | 429,479
55 | 42 | 13 | Universal Input | 5 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29480 | 429,481
55 | 42 | 14 | Universal Input | 5 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 29482 | 429,483
55 | 42 | 15 | Universal Input | 5 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 29484 | 429,485
55 | 42 | 16 | Universal Input | 5 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29486 | 429,487
55 | 42 | 17 | Universal Input | 5 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 29488 | 429,489
55 | 42 | 18 | Universal Input | 5 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 29490 | 429,491
55 | 42 | 28 | Universal Input | 5 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 29510 | 429,511
55 | 42 | 29 | Universal Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29512 | 429,513
55 | 42 | 30 | Universal Input | 5 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 29514 | 429,515
55 | 42 | 31 | Universal Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29516 | 429,517
55 | 42 | 35 | Universal Input | 5 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29524 | 429,525
55 | 42 | 36 | Universal Input | 5 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29526 | 429,527
55 | 42 | 37 | Universal Input | 5 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29528 | 429,529
55 | 42 | 38 | Universal Input | 5 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29530 | 429,531
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49840 | 449,841
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49841 | 449,842
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49842 | 449,843
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49843 | 449,844
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49844 | 449,845
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49845 | 449,846
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49846 | 449,847
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49847 | 449,848
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49848 | 449,849
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49849 | 449,850
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49850 | 449,851
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49851 | 449,852
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49852 | 449,853
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49853 | 449,854
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49854 | 449,855
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49855 | 449,856
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49856 | 449,857
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49857 | 449,858
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49858 | 449,859
55 | 42 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49859 | 449,860
55 | 42 | 48 | Universal Input | 5 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 29550 | 429,551
55 | 43 | 1 | Universal Input | 5 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29566 | 429,567
55 | 43 | 2 | Universal Input | 5 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 29568 | 429,569
55 | 43 | 3 | Universal Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 29570 | 429,571
55 | 43 | 4 | Universal Input | 5 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29572 | 429,573
55 | 43 | 5 | Universal Input | 5 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 29574 | 429,575
55 | 43 | 6 | Universal Input | 5 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 29576 | 429,577
55 | 43 | 7 | Universal Input | 5 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 29578 | 429,579
55 | 43 | 8 | Universal Input | 5 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29580 | 429,581
55 | 43 | 9 | Universal Input | 5 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 29582 | 429,583
55 | 43 | 10 | Universal Input | 5 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29584 | 429,585
55 | 43 | 11 | Universal Input | 5 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 29586 | 429,587
55 | 43 | 12 | Universal Input | 5 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 29588 | 429,589
55 | 43 | 13 | Universal Input | 5 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29590 | 429,591
55 | 43 | 14 | Universal Input | 5 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 29592 | 429,593
55 | 43 | 15 | Universal Input | 5 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 29594 | 429,595
55 | 43 | 16 | Universal Input | 5 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29596 | 429,597
55 | 43 | 17 | Universal Input | 5 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 29598 | 429,599
55 | 43 | 18 | Universal Input | 5 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 29600 | 429,601
55 | 43 | 28 | Universal Input | 5 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 29620 | 429,621
55 | 43 | 29 | Universal Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29622 | 429,623
55 | 43 | 30 | Universal Input | 5 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 29624 | 429,625
55 | 43 | 31 | Universal Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29626 | 429,627
55 | 43 | 35 | Universal Input | 5 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29634 | 429,635
55 | 43 | 36 | Universal Input | 5 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29636 | 429,637
55 | 43 | 37 | Universal Input | 5 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29638 | 429,639
55 | 43 | 38 | Universal Input | 5 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29640 | 429,641
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49860 | 449,861
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49861 | 449,862
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49862 | 449,863
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49863 | 449,864
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49864 | 449,865
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49865 | 449,866
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49866 | 449,867
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49867 | 449,868
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49868 | 449,869
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49869 | 449,870
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49870 | 449,871
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49871 | 449,872
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49872 | 449,873
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49873 | 449,874
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49874 | 449,875
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49875 | 449,876
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49876 | 449,877
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49877 | 449,878
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49878 | 449,879
55 | 43 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49879 | 449,880
55 | 43 | 48 | Universal Input | 5 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 29660 | 429,661
55 | 44 | 1 | Universal Input | 5 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29676 | 429,677
55 | 44 | 2 | Universal Input | 5 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 29678 | 429,679
55 | 44 | 3 | Universal Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 29680 | 429,681
55 | 44 | 4 | Universal Input | 5 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29682 | 429,683
55 | 44 | 5 | Universal Input | 5 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 29684 | 429,685
55 | 44 | 6 | Universal Input | 5 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 29686 | 429,687
55 | 44 | 7 | Universal Input | 5 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 29688 | 429,689
55 | 44 | 8 | Universal Input | 5 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29690 | 429,691
55 | 44 | 9 | Universal Input | 5 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 29692 | 429,693
55 | 44 | 10 | Universal Input | 5 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29694 | 429,695
55 | 44 | 11 | Universal Input | 5 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 29696 | 429,697
55 | 44 | 12 | Universal Input | 5 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 29698 | 429,699
55 | 44 | 13 | Universal Input | 5 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29700 | 429,701
55 | 44 | 14 | Universal Input | 5 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 29702 | 429,703
55 | 44 | 15 | Universal Input | 5 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 29704 | 429,705
55 | 44 | 16 | Universal Input | 5 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29706 | 429,707
55 | 44 | 17 | Universal Input | 5 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 29708 | 429,709
55 | 44 | 18 | Universal Input | 5 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 29710 | 429,711
55 | 44 | 28 | Universal Input | 5 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 29730 | 429,731
55 | 44 | 29 | Universal Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29732 | 429,733
55 | 44 | 30 | Universal Input | 5 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 29734 | 429,735
55 | 44 | 31 | Universal Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29736 | 429,737
55 | 44 | 35 | Universal Input | 5 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29744 | 429,745
55 | 44 | 36 | Universal Input | 5 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29746 | 429,747
55 | 44 | 37 | Universal Input | 5 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29748 | 429,749
55 | 44 | 38 | Universal Input | 5 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29750 | 429,751
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49880 | 449,881
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49881 | 449,882
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49882 | 449,883
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49883 | 449,884
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49884 | 449,885
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49885 | 449,886
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49886 | 449,887
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49887 | 449,888
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49888 | 449,889
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49889 | 449,890
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49890 | 449,891
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49891 | 449,892
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49892 | 449,893
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49893 | 449,894
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49894 | 449,895
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49895 | 449,896
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49896 | 449,897
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49897 | 449,898
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49898 | 449,899
55 | 44 | 47 | Universal Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49899 | 449,900
55 | 44 | 48 | Universal Input | 5 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 29770 | 429,771
55 | 51 | 1 | Universal Input | 6 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29786 | 429,787
55 | 51 | 2 | Universal Input | 6 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 29788 | 429,789
55 | 51 | 3 | Universal Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 29790 | 429,791
55 | 51 | 4 | Universal Input | 6 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29792 | 429,793
55 | 51 | 5 | Universal Input | 6 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 29794 | 429,795
55 | 51 | 6 | Universal Input | 6 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 29796 | 429,797
55 | 51 | 7 | Universal Input | 6 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 29798 | 429,799
55 | 51 | 8 | Universal Input | 6 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29800 | 429,801
55 | 51 | 9 | Universal Input | 6 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 29802 | 429,803
55 | 51 | 10 | Universal Input | 6 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29804 | 429,805
55 | 51 | 11 | Universal Input | 6 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 29806 | 429,807
55 | 51 | 12 | Universal Input | 6 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 29808 | 429,809
55 | 51 | 13 | Universal Input | 6 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29810 | 429,811
55 | 51 | 14 | Universal Input | 6 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 29812 | 429,813
55 | 51 | 15 | Universal Input | 6 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 29814 | 429,815
55 | 51 | 16 | Universal Input | 6 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29816 | 429,817
55 | 51 | 17 | Universal Input | 6 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 29818 | 429,819
55 | 51 | 18 | Universal Input | 6 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 29820 | 429,821
55 | 51 | 28 | Universal Input | 6 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 29840 | 429,841
55 | 51 | 29 | Universal Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29842 | 429,843
55 | 51 | 30 | Universal Input | 6 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 29844 | 429,845
55 | 51 | 31 | Universal Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29846 | 429,847
55 | 51 | 35 | Universal Input | 6 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29854 | 429,855
55 | 51 | 36 | Universal Input | 6 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29856 | 429,857
55 | 51 | 37 | Universal Input | 6 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29858 | 429,859
55 | 51 | 38 | Universal Input | 6 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29860 | 429,861
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49900 | 449,901
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49901 | 449,902
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49902 | 449,903
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49903 | 449,904
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49904 | 449,905
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49905 | 449,906
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49906 | 449,907
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49907 | 449,908
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49908 | 449,909
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49909 | 449,910
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49910 | 449,911
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49911 | 449,912
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49912 | 449,913
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49913 | 449,914
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49914 | 449,915
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49915 | 449,916
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49916 | 449,917
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49917 | 449,918
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49918 | 449,919
55 | 51 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49919 | 449,920
55 | 51 | 48 | Universal Input | 6 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 29880 | 429,881
55 | 52 | 1 | Universal Input | 6 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29896 | 429,897
55 | 52 | 2 | Universal Input | 6 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 29898 | 429,899
55 | 52 | 3 | Universal Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 29900 | 429,901
55 | 52 | 4 | Universal Input | 6 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29902 | 429,903
55 | 52 | 5 | Universal Input | 6 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 29904 | 429,905
55 | 52 | 6 | Universal Input | 6 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 29906 | 429,907
55 | 52 | 7 | Universal Input | 6 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 29908 | 429,909
55 | 52 | 8 | Universal Input | 6 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29910 | 429,911
55 | 52 | 9 | Universal Input | 6 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 29912 | 429,913
55 | 52 | 10 | Universal Input | 6 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29914 | 429,915
55 | 52 | 11 | Universal Input | 6 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 29916 | 429,917
55 | 52 | 12 | Universal Input | 6 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 29918 | 429,919
55 | 52 | 13 | Universal Input | 6 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 29920 | 429,921
55 | 52 | 14 | Universal Input | 6 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 29922 | 429,923
55 | 52 | 15 | Universal Input | 6 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 29924 | 429,925
55 | 52 | 16 | Universal Input | 6 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29926 | 429,927
55 | 52 | 17 | Universal Input | 6 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 29928 | 429,929
55 | 52 | 18 | Universal Input | 6 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 29930 | 429,931
55 | 52 | 28 | Universal Input | 6 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 29950 | 429,951
55 | 52 | 29 | Universal Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29952 | 429,953
55 | 52 | 30 | Universal Input | 6 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 29954 | 429,955
55 | 52 | 31 | Universal Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 29956 | 429,957
55 | 52 | 35 | Universal Input | 6 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29964 | 429,965
55 | 52 | 36 | Universal Input | 6 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 29966 | 429,967
55 | 52 | 37 | Universal Input | 6 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29968 | 429,969
55 | 52 | 38 | Universal Input | 6 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 29970 | 429,971
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49920 | 449,921
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49921 | 449,922
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49922 | 449,923
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49923 | 449,924
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49924 | 449,925
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49925 | 449,926
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49926 | 449,927
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49927 | 449,928
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49928 | 449,929
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49929 | 449,930
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49930 | 449,931
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49931 | 449,932
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49932 | 449,933
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49933 | 449,934
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49934 | 449,935
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49935 | 449,936
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49936 | 449,937
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49937 | 449,938
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49938 | 449,939
55 | 52 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49939 | 449,940
55 | 52 | 48 | Universal Input | 6 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 29990 | 429,991
55 | 53 | 1 | Universal Input | 6 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30006 | 430,007
55 | 53 | 2 | Universal Input | 6 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 30008 | 430,009
55 | 53 | 3 | Universal Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 30010 | 430,011
55 | 53 | 4 | Universal Input | 6 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30012 | 430,013
55 | 53 | 5 | Universal Input | 6 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 30014 | 430,015
55 | 53 | 6 | Universal Input | 6 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 30016 | 430,017
55 | 53 | 7 | Universal Input | 6 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 30018 | 430,019
55 | 53 | 8 | Universal Input | 6 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 30020 | 430,021
55 | 53 | 9 | Universal Input | 6 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 30022 | 430,023
55 | 53 | 10 | Universal Input | 6 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30024 | 430,025
55 | 53 | 11 | Universal Input | 6 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 30026 | 430,027
55 | 53 | 12 | Universal Input | 6 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 30028 | 430,029
55 | 53 | 13 | Universal Input | 6 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 30030 | 430,031
55 | 53 | 14 | Universal Input | 6 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 30032 | 430,033
55 | 53 | 15 | Universal Input | 6 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 30034 | 430,035
55 | 53 | 16 | Universal Input | 6 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30036 | 430,037
55 | 53 | 17 | Universal Input | 6 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 30038 | 430,039
55 | 53 | 18 | Universal Input | 6 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 30040 | 430,041
55 | 53 | 28 | Universal Input | 6 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 30060 | 430,061
55 | 53 | 29 | Universal Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30062 | 430,063
55 | 53 | 30 | Universal Input | 6 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 30064 | 430,065
55 | 53 | 31 | Universal Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30066 | 430,067
55 | 53 | 35 | Universal Input | 6 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30074 | 430,075
55 | 53 | 36 | Universal Input | 6 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30076 | 430,077
55 | 53 | 37 | Universal Input | 6 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30078 | 430,079
55 | 53 | 38 | Universal Input | 6 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30080 | 430,081
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49940 | 449,941
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49941 | 449,942
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49942 | 449,943
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49943 | 449,944
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49944 | 449,945
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49945 | 449,946
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49946 | 449,947
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49947 | 449,948
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49948 | 449,949
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49949 | 449,950
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49950 | 449,951
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49951 | 449,952
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49952 | 449,953
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49953 | 449,954
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49954 | 449,955
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49955 | 449,956
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49956 | 449,957
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49957 | 449,958
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49958 | 449,959
55 | 53 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49959 | 449,960
55 | 53 | 48 | Universal Input | 6 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 30100 | 430,101
55 | 54 | 1 | Universal Input | 6 | Analog Input Value | Monitor the unfiltered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30116 | 430,117
55 | 54 | 2 | Universal Input | 6 | Input Error | Monitor for errors on the analog input. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 30118 | 430,119
55 | 54 | 3 | Universal Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 30120 | 430,121
55 | 54 | 4 | Universal Input | 6 | Filtered Process Value | Monitor the filtered analog input value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30122 | 430,123
55 | 54 | 5 | Universal Input | 6 | Sensor Type | Set the analog sensor type to match the device wired to this input. | Off (62), Thermocouple (95), Millivolts (56), Volts (104), Milliamps (112), RTD 100 Ohm (113), RTD 1000 Ohm (114), 1K Potentiometer (155) | Thermocouple (95) | Enumeration | R/W | 30124 | 430,125
55 | 54 | 6 | Universal Input | 6 | TC Linearization | Set the linearization to match the thermocouple wired to this input. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 30126 | 430,127
55 | 54 | 7 | Universal Input | 6 | RTD Leads | Set to match the number of leads on the RTD wired to this input. | 2 (1), 3 (2) | 2 (1) | Enumeration | R/W | 30128 | 430,129
55 | 54 | 8 | Universal Input | 6 | Scale Low | Set the low scale for process inputs. This value, in millivolts, volts or milliamps, will correspond to the Range Low output of this function block. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 30130 | 430,131
55 | 54 | 9 | Universal Input | 6 | Scale High | Set the high scale for process inputs. This value, in millivolts, volts or milliamperes, will correspond to the Range High output of this function block. | -100.0 to 1,000.0 | 20.0 | IEEE Float | R/W | 30132 | 430,133
55 | 54 | 10 | Universal Input | 6 | Range Low | Set the low range for this function block's output. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30134 | 430,135
55 | 54 | 11 | Universal Input | 6 | Range High | Set the high range for this function block's output. | -99,999.0 to 99,999.0 | 9,999.0 | IEEE Float | R/W | 30136 | 430,137
55 | 54 | 12 | Universal Input | 6 | Process Error Enable | Set the Process Error Low feature to Low to detect low analog input values. | Off (62), Low (53) | Off (62) | Enumeration | R/W | 30138 | 430,139
55 | 54 | 13 | Universal Input | 6 | Process Error Low Value | Set the value that generates a low analog input error when Process Error Enable is set to low. | -100.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 30140 | 430,141
55 | 54 | 14 | Universal Input | 6 | Display Precision | Set display precision used by the screen. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 30142 | 430,143
55 | 54 | 15 | Universal Input | 6 | Units | Set the type of units the sensor will measure. | Absolute Temperature (1540), Power (73), Process (75), Relative Humidity (1538) | Process (75) | Enumeration | R/W | 30144 | 430,145
55 | 54 | 16 | Universal Input | 6 | Calibration Offset | Set an offset of the input reading to compensate for lead wire resistance or other factors that cause the input reading to vary from the actual process value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30146 | 430,147
55 | 54 | 17 | Universal Input | 6 | Input Error Latching | Set to latch intermittent analog input errors. | Off (62), On (63) | Off (62) | Enumeration | R/W | 30148 | 430,149
55 | 54 | 18 | Universal Input | 6 | Clear Error | Request to clear latched analog input error. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 30150 | 430,151
55 | 54 | 28 | Universal Input | 6 | Electrical Measurement | Monitor the electrical value produced by the analog input. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 30170 | 430,171
55 | 54 | 29 | Universal Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30172 | 430,173
55 | 54 | 30 | Universal Input | 6 | Measure CJC | Set to enable the cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 30174 | 430,175
55 | 54 | 31 | Universal Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30176 | 430,177
55 | 54 | 35 | Universal Input | 6 | Ambient Offset | Set an offset for the ambient temperature measurement. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30184 | 430,185
55 | 54 | 36 | Universal Input | 6 | Electrical Input Offset | Set an electrical offset value for an analog input. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30186 | 430,187
55 | 54 | 37 | Universal Input | 6 | Electrical Input Slope | Set an electrical slope value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30188 | 430,189
55 | 54 | 38 | Universal Input | 6 | Calibration Slope | Set an calibration value for an analog input. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30190 | 430,191
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49960 | 449,961
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49961 | 449,962
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49962 | 449,963
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49963 | 449,964
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49964 | 449,965
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49965 | 449,966
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49966 | 449,967
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49967 | 449,968
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49968 | 449,969
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49969 | 449,970
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49970 | 449,971
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49971 | 449,972
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49972 | 449,973
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49973 | 449,974
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49974 | 449,975
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49975 | 449,976
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49976 | 449,977
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49977 | 449,978
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49978 | 449,979
55 | 54 | 47 | Universal Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49979 | 449,980
55 | 54 | 48 | Universal Input | 6 | Terminate | Set a first order number of to apply 3 the analog input value. | 2 (1), 3 (2) |  | Enumeration | R | 30210 | 430,211
56 | 1 | 1 | Thermistor Input | 1 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30226 | 430,227
56 | 1 | 2 | Thermistor Input | 1 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 30228 | 430,229
56 | 1 | 3 | Thermistor Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 30230 | 430,231
56 | 1 | 4 | Thermistor Input | 1 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30232 | 430,233
56 | 1 | 5 | Thermistor Input | 1 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 30234 | 430,235
56 | 1 | 6 | Thermistor Input | 1 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 30236 | 430,237
56 | 1 | 7 | Thermistor Input | 1 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 30238 | 430,239
56 | 1 | 8 | Thermistor Input | 1 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 30240 | 430,241
56 | 1 | 9 | Thermistor Input | 1 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 30242 | 430,243
56 | 1 | 10 | Thermistor Input | 1 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 30244 | 430,245
56 | 1 | 14 | Thermistor Input | 1 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 30252 | 430,253
56 | 1 | 16 | Thermistor Input | 1 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30256 | 430,257
56 | 1 | 17 | Thermistor Input | 1 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 30258 | 430,259
56 | 1 | 18 | Thermistor Input | 1 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 30260 | 430,261
56 | 1 | 28 | Thermistor Input | 1 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 30280 | 430,281
56 | 1 | 29 | Thermistor Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30282 | 430,283
56 | 1 | 30 | Thermistor Input | 1 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 30284 | 430,285
56 | 1 | 31 | Thermistor Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30286 | 430,287
56 | 1 | 35 | Thermistor Input | 1 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30294 | 430,295
56 | 1 | 36 | Thermistor Input | 1 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30296 | 430,297
56 | 1 | 37 | Thermistor Input | 1 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30298 | 430,299
56 | 1 | 38 | Thermistor Input | 1 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30300 | 430,301
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49980 | 449,981
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49981 | 449,982
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49982 | 449,983
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49983 | 449,984
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49984 | 449,985
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49985 | 449,986
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49986 | 449,987
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49987 | 449,988
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49988 | 449,989
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49989 | 449,990
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49990 | 449,991
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49991 | 449,992
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49992 | 449,993
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49993 | 449,994
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49994 | 449,995
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49995 | 449,996
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49996 | 449,997
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49997 | 449,998
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49998 | 449,999
56 | 1 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 49999 | 450,000
56 | 2 | 1 | Thermistor Input | 1 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30306 | 430,307
56 | 2 | 2 | Thermistor Input | 1 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 30308 | 430,309
56 | 2 | 3 | Thermistor Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 30310 | 430,311
56 | 2 | 4 | Thermistor Input | 1 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30312 | 430,313
56 | 2 | 5 | Thermistor Input | 1 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 30314 | 430,315
56 | 2 | 6 | Thermistor Input | 1 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 30316 | 430,317
56 | 2 | 7 | Thermistor Input | 1 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 30318 | 430,319
56 | 2 | 8 | Thermistor Input | 1 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 30320 | 430,321
56 | 2 | 9 | Thermistor Input | 1 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 30322 | 430,323
56 | 2 | 10 | Thermistor Input | 1 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 30324 | 430,325
56 | 2 | 14 | Thermistor Input | 1 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 30332 | 430,333
56 | 2 | 16 | Thermistor Input | 1 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30336 | 430,337
56 | 2 | 17 | Thermistor Input | 1 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 30338 | 430,339
56 | 2 | 18 | Thermistor Input | 1 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 30340 | 430,341
56 | 2 | 28 | Thermistor Input | 1 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 30360 | 430,361
56 | 2 | 29 | Thermistor Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30362 | 430,363
56 | 2 | 30 | Thermistor Input | 1 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 30364 | 430,365
56 | 2 | 31 | Thermistor Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30366 | 430,367
56 | 2 | 35 | Thermistor Input | 1 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30374 | 430,375
56 | 2 | 36 | Thermistor Input | 1 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30376 | 430,377
56 | 2 | 37 | Thermistor Input | 1 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30378 | 430,379
56 | 2 | 38 | Thermistor Input | 1 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30380 | 430,381
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50000 | 450,001
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50001 | 450,002
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50002 | 450,003
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50003 | 450,004
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50004 | 450,005
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50005 | 450,006
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50006 | 450,007
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50007 | 450,008
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50008 | 450,009
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50009 | 450,010
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50010 | 450,011
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50011 | 450,012
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50012 | 450,013
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50013 | 450,014
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50014 | 450,015
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50015 | 450,016
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50016 | 450,017
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50017 | 450,018
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50018 | 450,019
56 | 2 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50019 | 450,020
56 | 3 | 1 | Thermistor Input | 1 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30386 | 430,387
56 | 3 | 2 | Thermistor Input | 1 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 30388 | 430,389
56 | 3 | 3 | Thermistor Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 30390 | 430,391
56 | 3 | 4 | Thermistor Input | 1 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30392 | 430,393
56 | 3 | 5 | Thermistor Input | 1 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 30394 | 430,395
56 | 3 | 6 | Thermistor Input | 1 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 30396 | 430,397
56 | 3 | 7 | Thermistor Input | 1 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 30398 | 430,399
56 | 3 | 8 | Thermistor Input | 1 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 30400 | 430,401
56 | 3 | 9 | Thermistor Input | 1 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 30402 | 430,403
56 | 3 | 10 | Thermistor Input | 1 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 30404 | 430,405
56 | 3 | 14 | Thermistor Input | 1 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 30412 | 430,413
56 | 3 | 16 | Thermistor Input | 1 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30416 | 430,417
56 | 3 | 17 | Thermistor Input | 1 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 30418 | 430,419
56 | 3 | 18 | Thermistor Input | 1 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 30420 | 430,421
56 | 3 | 28 | Thermistor Input | 1 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 30440 | 430,441
56 | 3 | 29 | Thermistor Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30442 | 430,443
56 | 3 | 30 | Thermistor Input | 1 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 30444 | 430,445
56 | 3 | 31 | Thermistor Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30446 | 430,447
56 | 3 | 35 | Thermistor Input | 1 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30454 | 430,455
56 | 3 | 36 | Thermistor Input | 1 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30456 | 430,457
56 | 3 | 37 | Thermistor Input | 1 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30458 | 430,459
56 | 3 | 38 | Thermistor Input | 1 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30460 | 430,461
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50020 | 450,021
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50021 | 450,022
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50022 | 450,023
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50023 | 450,024
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50024 | 450,025
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50025 | 450,026
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50026 | 450,027
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50027 | 450,028
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50028 | 450,029
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50029 | 450,030
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50030 | 450,031
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50031 | 450,032
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50032 | 450,033
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50033 | 450,034
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50034 | 450,035
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50035 | 450,036
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50036 | 450,037
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50037 | 450,038
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50038 | 450,039
56 | 3 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50039 | 450,040
56 | 4 | 1 | Thermistor Input | 1 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30466 | 430,467
56 | 4 | 2 | Thermistor Input | 1 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 30468 | 430,469
56 | 4 | 3 | Thermistor Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 30470 | 430,471
56 | 4 | 4 | Thermistor Input | 1 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30472 | 430,473
56 | 4 | 5 | Thermistor Input | 1 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 30474 | 430,475
56 | 4 | 6 | Thermistor Input | 1 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 30476 | 430,477
56 | 4 | 7 | Thermistor Input | 1 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 30478 | 430,479
56 | 4 | 8 | Thermistor Input | 1 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 30480 | 430,481
56 | 4 | 9 | Thermistor Input | 1 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 30482 | 430,483
56 | 4 | 10 | Thermistor Input | 1 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 30484 | 430,485
56 | 4 | 14 | Thermistor Input | 1 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 30492 | 430,493
56 | 4 | 16 | Thermistor Input | 1 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30496 | 430,497
56 | 4 | 17 | Thermistor Input | 1 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 30498 | 430,499
56 | 4 | 18 | Thermistor Input | 1 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 30500 | 430,501
56 | 4 | 28 | Thermistor Input | 1 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 30520 | 430,521
56 | 4 | 29 | Thermistor Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30522 | 430,523
56 | 4 | 30 | Thermistor Input | 1 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 30524 | 430,525
56 | 4 | 31 | Thermistor Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30526 | 430,527
56 | 4 | 35 | Thermistor Input | 1 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30534 | 430,535
56 | 4 | 36 | Thermistor Input | 1 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30536 | 430,537
56 | 4 | 37 | Thermistor Input | 1 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30538 | 430,539
56 | 4 | 38 | Thermistor Input | 1 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30540 | 430,541
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50040 | 450,041
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50041 | 450,042
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50042 | 450,043
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50043 | 450,044
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50044 | 450,045
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50045 | 450,046
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50046 | 450,047
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50047 | 450,048
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50048 | 450,049
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50049 | 450,050
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50050 | 450,051
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50051 | 450,052
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50052 | 450,053
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50053 | 450,054
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50054 | 450,055
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50055 | 450,056
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50056 | 450,057
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50057 | 450,058
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50058 | 450,059
56 | 4 | 47 | Thermistor Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50059 | 450,060
56 | 11 | 1 | Thermistor Input | 2 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30546 | 430,547
56 | 11 | 2 | Thermistor Input | 2 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 30548 | 430,549
56 | 11 | 3 | Thermistor Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 30550 | 430,551
56 | 11 | 4 | Thermistor Input | 2 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30552 | 430,553
56 | 11 | 5 | Thermistor Input | 2 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 30554 | 430,555
56 | 11 | 6 | Thermistor Input | 2 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 30556 | 430,557
56 | 11 | 7 | Thermistor Input | 2 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 30558 | 430,559
56 | 11 | 8 | Thermistor Input | 2 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 30560 | 430,561
56 | 11 | 9 | Thermistor Input | 2 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 30562 | 430,563
56 | 11 | 10 | Thermistor Input | 2 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 30564 | 430,565
56 | 11 | 14 | Thermistor Input | 2 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 30572 | 430,573
56 | 11 | 16 | Thermistor Input | 2 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30576 | 430,577
56 | 11 | 17 | Thermistor Input | 2 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 30578 | 430,579
56 | 11 | 18 | Thermistor Input | 2 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 30580 | 430,581
56 | 11 | 28 | Thermistor Input | 2 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 30600 | 430,601
56 | 11 | 29 | Thermistor Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30602 | 430,603
56 | 11 | 30 | Thermistor Input | 2 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 30604 | 430,605
56 | 11 | 31 | Thermistor Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30606 | 430,607
56 | 11 | 35 | Thermistor Input | 2 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30614 | 430,615
56 | 11 | 36 | Thermistor Input | 2 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30616 | 430,617
56 | 11 | 37 | Thermistor Input | 2 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30618 | 430,619
56 | 11 | 38 | Thermistor Input | 2 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30620 | 430,621
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50060 | 450,061
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50061 | 450,062
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50062 | 450,063
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50063 | 450,064
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50064 | 450,065
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50065 | 450,066
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50066 | 450,067
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50067 | 450,068
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50068 | 450,069
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50069 | 450,070
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50070 | 450,071
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50071 | 450,072
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50072 | 450,073
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50073 | 450,074
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50074 | 450,075
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50075 | 450,076
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50076 | 450,077
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50077 | 450,078
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50078 | 450,079
56 | 11 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50079 | 450,080
56 | 12 | 1 | Thermistor Input | 2 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30626 | 430,627
56 | 12 | 2 | Thermistor Input | 2 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 30628 | 430,629
56 | 12 | 3 | Thermistor Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 30630 | 430,631
56 | 12 | 4 | Thermistor Input | 2 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30632 | 430,633
56 | 12 | 5 | Thermistor Input | 2 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 30634 | 430,635
56 | 12 | 6 | Thermistor Input | 2 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 30636 | 430,637
56 | 12 | 7 | Thermistor Input | 2 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 30638 | 430,639
56 | 12 | 8 | Thermistor Input | 2 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 30640 | 430,641
56 | 12 | 9 | Thermistor Input | 2 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 30642 | 430,643
56 | 12 | 10 | Thermistor Input | 2 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 30644 | 430,645
56 | 12 | 14 | Thermistor Input | 2 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 30652 | 430,653
56 | 12 | 16 | Thermistor Input | 2 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30656 | 430,657
56 | 12 | 17 | Thermistor Input | 2 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 30658 | 430,659
56 | 12 | 18 | Thermistor Input | 2 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 30660 | 430,661
56 | 12 | 28 | Thermistor Input | 2 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 30680 | 430,681
56 | 12 | 29 | Thermistor Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30682 | 430,683
56 | 12 | 30 | Thermistor Input | 2 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 30684 | 430,685
56 | 12 | 31 | Thermistor Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30686 | 430,687
56 | 12 | 35 | Thermistor Input | 2 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30694 | 430,695
56 | 12 | 36 | Thermistor Input | 2 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30696 | 430,697
56 | 12 | 37 | Thermistor Input | 2 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30698 | 430,699
56 | 12 | 38 | Thermistor Input | 2 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30700 | 430,701
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50080 | 450,081
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50081 | 450,082
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50082 | 450,083
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50083 | 450,084
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50084 | 450,085
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50085 | 450,086
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50086 | 450,087
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50087 | 450,088
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50088 | 450,089
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50089 | 450,090
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50090 | 450,091
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50091 | 450,092
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50092 | 450,093
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50093 | 450,094
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50094 | 450,095
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50095 | 450,096
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50096 | 450,097
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50097 | 450,098
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50098 | 450,099
56 | 12 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50099 | 450,100
56 | 13 | 1 | Thermistor Input | 2 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30706 | 430,707
56 | 13 | 2 | Thermistor Input | 2 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 30708 | 430,709
56 | 13 | 3 | Thermistor Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 30710 | 430,711
56 | 13 | 4 | Thermistor Input | 2 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30712 | 430,713
56 | 13 | 5 | Thermistor Input | 2 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 30714 | 430,715
56 | 13 | 6 | Thermistor Input | 2 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 30716 | 430,717
56 | 13 | 7 | Thermistor Input | 2 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 30718 | 430,719
56 | 13 | 8 | Thermistor Input | 2 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 30720 | 430,721
56 | 13 | 9 | Thermistor Input | 2 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 30722 | 430,723
56 | 13 | 10 | Thermistor Input | 2 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 30724 | 430,725
56 | 13 | 14 | Thermistor Input | 2 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 30732 | 430,733
56 | 13 | 16 | Thermistor Input | 2 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30736 | 430,737
56 | 13 | 17 | Thermistor Input | 2 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 30738 | 430,739
56 | 13 | 18 | Thermistor Input | 2 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 30740 | 430,741
56 | 13 | 28 | Thermistor Input | 2 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 30760 | 430,761
56 | 13 | 29 | Thermistor Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30762 | 430,763
56 | 13 | 30 | Thermistor Input | 2 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 30764 | 430,765
56 | 13 | 31 | Thermistor Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30766 | 430,767
56 | 13 | 35 | Thermistor Input | 2 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30774 | 430,775
56 | 13 | 36 | Thermistor Input | 2 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30776 | 430,777
56 | 13 | 37 | Thermistor Input | 2 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30778 | 430,779
56 | 13 | 38 | Thermistor Input | 2 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30780 | 430,781
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50100 | 450,101
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50101 | 450,102
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50102 | 450,103
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50103 | 450,104
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50104 | 450,105
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50105 | 450,106
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50106 | 450,107
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50107 | 450,108
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50108 | 450,109
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50109 | 450,110
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50110 | 450,111
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50111 | 450,112
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50112 | 450,113
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50113 | 450,114
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50114 | 450,115
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50115 | 450,116
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50116 | 450,117
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50117 | 450,118
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50118 | 450,119
56 | 13 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50119 | 450,120
56 | 14 | 1 | Thermistor Input | 2 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30786 | 430,787
56 | 14 | 2 | Thermistor Input | 2 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 30788 | 430,789
56 | 14 | 3 | Thermistor Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 30790 | 430,791
56 | 14 | 4 | Thermistor Input | 2 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30792 | 430,793
56 | 14 | 5 | Thermistor Input | 2 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 30794 | 430,795
56 | 14 | 6 | Thermistor Input | 2 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 30796 | 430,797
56 | 14 | 7 | Thermistor Input | 2 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 30798 | 430,799
56 | 14 | 8 | Thermistor Input | 2 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 30800 | 430,801
56 | 14 | 9 | Thermistor Input | 2 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 30802 | 430,803
56 | 14 | 10 | Thermistor Input | 2 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 30804 | 430,805
56 | 14 | 14 | Thermistor Input | 2 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 30812 | 430,813
56 | 14 | 16 | Thermistor Input | 2 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30816 | 430,817
56 | 14 | 17 | Thermistor Input | 2 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 30818 | 430,819
56 | 14 | 18 | Thermistor Input | 2 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 30820 | 430,821
56 | 14 | 28 | Thermistor Input | 2 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 30840 | 430,841
56 | 14 | 29 | Thermistor Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30842 | 430,843
56 | 14 | 30 | Thermistor Input | 2 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 30844 | 430,845
56 | 14 | 31 | Thermistor Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30846 | 430,847
56 | 14 | 35 | Thermistor Input | 2 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30854 | 430,855
56 | 14 | 36 | Thermistor Input | 2 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30856 | 430,857
56 | 14 | 37 | Thermistor Input | 2 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30858 | 430,859
56 | 14 | 38 | Thermistor Input | 2 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30860 | 430,861
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50120 | 450,121
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50121 | 450,122
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50122 | 450,123
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50123 | 450,124
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50124 | 450,125
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50125 | 450,126
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50126 | 450,127
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50127 | 450,128
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50128 | 450,129
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50129 | 450,130
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50130 | 450,131
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50131 | 450,132
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50132 | 450,133
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50133 | 450,134
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50134 | 450,135
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50135 | 450,136
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50136 | 450,137
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50137 | 450,138
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50138 | 450,139
56 | 14 | 47 | Thermistor Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50139 | 450,140
56 | 21 | 1 | Thermistor Input | 3 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30866 | 430,867
56 | 21 | 2 | Thermistor Input | 3 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 30868 | 430,869
56 | 21 | 3 | Thermistor Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 30870 | 430,871
56 | 21 | 4 | Thermistor Input | 3 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30872 | 430,873
56 | 21 | 5 | Thermistor Input | 3 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 30874 | 430,875
56 | 21 | 6 | Thermistor Input | 3 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 30876 | 430,877
56 | 21 | 7 | Thermistor Input | 3 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 30878 | 430,879
56 | 21 | 8 | Thermistor Input | 3 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 30880 | 430,881
56 | 21 | 9 | Thermistor Input | 3 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 30882 | 430,883
56 | 21 | 10 | Thermistor Input | 3 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 30884 | 430,885
56 | 21 | 14 | Thermistor Input | 3 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 30892 | 430,893
56 | 21 | 16 | Thermistor Input | 3 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30896 | 430,897
56 | 21 | 17 | Thermistor Input | 3 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 30898 | 430,899
56 | 21 | 18 | Thermistor Input | 3 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 30900 | 430,901
56 | 21 | 28 | Thermistor Input | 3 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 30920 | 430,921
56 | 21 | 29 | Thermistor Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30922 | 430,923
56 | 21 | 30 | Thermistor Input | 3 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 30924 | 430,925
56 | 21 | 31 | Thermistor Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30926 | 430,927
56 | 21 | 35 | Thermistor Input | 3 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30934 | 430,935
56 | 21 | 36 | Thermistor Input | 3 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30936 | 430,937
56 | 21 | 37 | Thermistor Input | 3 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30938 | 430,939
56 | 21 | 38 | Thermistor Input | 3 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 30940 | 430,941
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50140 | 450,141
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50141 | 450,142
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50142 | 450,143
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50143 | 450,144
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50144 | 450,145
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50145 | 450,146
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50146 | 450,147
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50147 | 450,148
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50148 | 450,149
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50149 | 450,150
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50150 | 450,151
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50151 | 450,152
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50152 | 450,153
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50153 | 450,154
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50154 | 450,155
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50155 | 450,156
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50156 | 450,157
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50157 | 450,158
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50158 | 450,159
56 | 21 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50159 | 450,160
56 | 22 | 1 | Thermistor Input | 3 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30946 | 430,947
56 | 22 | 2 | Thermistor Input | 3 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 30948 | 430,949
56 | 22 | 3 | Thermistor Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 30950 | 430,951
56 | 22 | 4 | Thermistor Input | 3 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 30952 | 430,953
56 | 22 | 5 | Thermistor Input | 3 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 30954 | 430,955
56 | 22 | 6 | Thermistor Input | 3 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 30956 | 430,957
56 | 22 | 7 | Thermistor Input | 3 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 30958 | 430,959
56 | 22 | 8 | Thermistor Input | 3 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 30960 | 430,961
56 | 22 | 9 | Thermistor Input | 3 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 30962 | 430,963
56 | 22 | 10 | Thermistor Input | 3 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 30964 | 430,965
56 | 22 | 14 | Thermistor Input | 3 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 30972 | 430,973
56 | 22 | 16 | Thermistor Input | 3 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 30976 | 430,977
56 | 22 | 17 | Thermistor Input | 3 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 30978 | 430,979
56 | 22 | 18 | Thermistor Input | 3 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 30980 | 430,981
56 | 22 | 28 | Thermistor Input | 3 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 31000 | 431,001
56 | 22 | 29 | Thermistor Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31002 | 431,003
56 | 22 | 30 | Thermistor Input | 3 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 31004 | 431,005
56 | 22 | 31 | Thermistor Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31006 | 431,007
56 | 22 | 35 | Thermistor Input | 3 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31014 | 431,015
56 | 22 | 36 | Thermistor Input | 3 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31016 | 431,017
56 | 22 | 37 | Thermistor Input | 3 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31018 | 431,019
56 | 22 | 38 | Thermistor Input | 3 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31020 | 431,021
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50160 | 450,161
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50161 | 450,162
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50162 | 450,163
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50163 | 450,164
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50164 | 450,165
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50165 | 450,166
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50166 | 450,167
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50167 | 450,168
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50168 | 450,169
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50169 | 450,170
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50170 | 450,171
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50171 | 450,172
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50172 | 450,173
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50173 | 450,174
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50174 | 450,175
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50175 | 450,176
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50176 | 450,177
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50177 | 450,178
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50178 | 450,179
56 | 22 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50179 | 450,180
56 | 23 | 1 | Thermistor Input | 3 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31026 | 431,027
56 | 23 | 2 | Thermistor Input | 3 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 31028 | 431,029
56 | 23 | 3 | Thermistor Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 31030 | 431,031
56 | 23 | 4 | Thermistor Input | 3 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31032 | 431,033
56 | 23 | 5 | Thermistor Input | 3 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 31034 | 431,035
56 | 23 | 6 | Thermistor Input | 3 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 31036 | 431,037
56 | 23 | 7 | Thermistor Input | 3 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 31038 | 431,039
56 | 23 | 8 | Thermistor Input | 3 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 31040 | 431,041
56 | 23 | 9 | Thermistor Input | 3 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 31042 | 431,043
56 | 23 | 10 | Thermistor Input | 3 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 31044 | 431,045
56 | 23 | 14 | Thermistor Input | 3 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 31052 | 431,053
56 | 23 | 16 | Thermistor Input | 3 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31056 | 431,057
56 | 23 | 17 | Thermistor Input | 3 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 31058 | 431,059
56 | 23 | 18 | Thermistor Input | 3 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 31060 | 431,061
56 | 23 | 28 | Thermistor Input | 3 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 31080 | 431,081
56 | 23 | 29 | Thermistor Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31082 | 431,083
56 | 23 | 30 | Thermistor Input | 3 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 31084 | 431,085
56 | 23 | 31 | Thermistor Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31086 | 431,087
56 | 23 | 35 | Thermistor Input | 3 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31094 | 431,095
56 | 23 | 36 | Thermistor Input | 3 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31096 | 431,097
56 | 23 | 37 | Thermistor Input | 3 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31098 | 431,099
56 | 23 | 38 | Thermistor Input | 3 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31100 | 431,101
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50180 | 450,181
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50181 | 450,182
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50182 | 450,183
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50183 | 450,184
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50184 | 450,185
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50185 | 450,186
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50186 | 450,187
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50187 | 450,188
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50188 | 450,189
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50189 | 450,190
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50190 | 450,191
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50191 | 450,192
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50192 | 450,193
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50193 | 450,194
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50194 | 450,195
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50195 | 450,196
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50196 | 450,197
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50197 | 450,198
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50198 | 450,199
56 | 23 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50199 | 450,200
56 | 24 | 1 | Thermistor Input | 3 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31106 | 431,107
56 | 24 | 2 | Thermistor Input | 3 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 31108 | 431,109
56 | 24 | 3 | Thermistor Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 31110 | 431,111
56 | 24 | 4 | Thermistor Input | 3 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31112 | 431,113
56 | 24 | 5 | Thermistor Input | 3 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 31114 | 431,115
56 | 24 | 6 | Thermistor Input | 3 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 31116 | 431,117
56 | 24 | 7 | Thermistor Input | 3 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 31118 | 431,119
56 | 24 | 8 | Thermistor Input | 3 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 31120 | 431,121
56 | 24 | 9 | Thermistor Input | 3 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 31122 | 431,123
56 | 24 | 10 | Thermistor Input | 3 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 31124 | 431,125
56 | 24 | 14 | Thermistor Input | 3 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 31132 | 431,133
56 | 24 | 16 | Thermistor Input | 3 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31136 | 431,137
56 | 24 | 17 | Thermistor Input | 3 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 31138 | 431,139
56 | 24 | 18 | Thermistor Input | 3 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 31140 | 431,141
56 | 24 | 28 | Thermistor Input | 3 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 31160 | 431,161
56 | 24 | 29 | Thermistor Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31162 | 431,163
56 | 24 | 30 | Thermistor Input | 3 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 31164 | 431,165
56 | 24 | 31 | Thermistor Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31166 | 431,167
56 | 24 | 35 | Thermistor Input | 3 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31174 | 431,175
56 | 24 | 36 | Thermistor Input | 3 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31176 | 431,177
56 | 24 | 37 | Thermistor Input | 3 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31178 | 431,179
56 | 24 | 38 | Thermistor Input | 3 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31180 | 431,181
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50200 | 450,201
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50201 | 450,202
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50202 | 450,203
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50203 | 450,204
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50204 | 450,205
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50205 | 450,206
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50206 | 450,207
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50207 | 450,208
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50208 | 450,209
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50209 | 450,210
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50210 | 450,211
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50211 | 450,212
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50212 | 450,213
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50213 | 450,214
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50214 | 450,215
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50215 | 450,216
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50216 | 450,217
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50217 | 450,218
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50218 | 450,219
56 | 24 | 47 | Thermistor Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50219 | 450,220
56 | 31 | 1 | Thermistor Input | 4 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31186 | 431,187
56 | 31 | 2 | Thermistor Input | 4 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 31188 | 431,189
56 | 31 | 3 | Thermistor Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 31190 | 431,191
56 | 31 | 4 | Thermistor Input | 4 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31192 | 431,193
56 | 31 | 5 | Thermistor Input | 4 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 31194 | 431,195
56 | 31 | 6 | Thermistor Input | 4 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 31196 | 431,197
56 | 31 | 7 | Thermistor Input | 4 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 31198 | 431,199
56 | 31 | 8 | Thermistor Input | 4 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 31200 | 431,201
56 | 31 | 9 | Thermistor Input | 4 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 31202 | 431,203
56 | 31 | 10 | Thermistor Input | 4 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 31204 | 431,205
56 | 31 | 14 | Thermistor Input | 4 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 31212 | 431,213
56 | 31 | 16 | Thermistor Input | 4 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31216 | 431,217
56 | 31 | 17 | Thermistor Input | 4 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 31218 | 431,219
56 | 31 | 18 | Thermistor Input | 4 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 31220 | 431,221
56 | 31 | 28 | Thermistor Input | 4 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 31240 | 431,241
56 | 31 | 29 | Thermistor Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31242 | 431,243
56 | 31 | 30 | Thermistor Input | 4 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 31244 | 431,245
56 | 31 | 31 | Thermistor Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31246 | 431,247
56 | 31 | 35 | Thermistor Input | 4 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31254 | 431,255
56 | 31 | 36 | Thermistor Input | 4 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31256 | 431,257
56 | 31 | 37 | Thermistor Input | 4 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31258 | 431,259
56 | 31 | 38 | Thermistor Input | 4 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31260 | 431,261
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50220 | 450,221
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50221 | 450,222
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50222 | 450,223
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50223 | 450,224
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50224 | 450,225
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50225 | 450,226
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50226 | 450,227
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50227 | 450,228
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50228 | 450,229
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50229 | 450,230
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50230 | 450,231
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50231 | 450,232
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50232 | 450,233
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50233 | 450,234
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50234 | 450,235
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50235 | 450,236
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50236 | 450,237
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50237 | 450,238
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50238 | 450,239
56 | 31 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50239 | 450,240
56 | 32 | 1 | Thermistor Input | 4 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31266 | 431,267
56 | 32 | 2 | Thermistor Input | 4 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 31268 | 431,269
56 | 32 | 3 | Thermistor Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 31270 | 431,271
56 | 32 | 4 | Thermistor Input | 4 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31272 | 431,273
56 | 32 | 5 | Thermistor Input | 4 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 31274 | 431,275
56 | 32 | 6 | Thermistor Input | 4 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 31276 | 431,277
56 | 32 | 7 | Thermistor Input | 4 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 31278 | 431,279
56 | 32 | 8 | Thermistor Input | 4 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 31280 | 431,281
56 | 32 | 9 | Thermistor Input | 4 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 31282 | 431,283
56 | 32 | 10 | Thermistor Input | 4 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 31284 | 431,285
56 | 32 | 14 | Thermistor Input | 4 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 31292 | 431,293
56 | 32 | 16 | Thermistor Input | 4 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31296 | 431,297
56 | 32 | 17 | Thermistor Input | 4 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 31298 | 431,299
56 | 32 | 18 | Thermistor Input | 4 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 31300 | 431,301
56 | 32 | 28 | Thermistor Input | 4 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 31320 | 431,321
56 | 32 | 29 | Thermistor Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31322 | 431,323
56 | 32 | 30 | Thermistor Input | 4 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 31324 | 431,325
56 | 32 | 31 | Thermistor Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31326 | 431,327
56 | 32 | 35 | Thermistor Input | 4 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31334 | 431,335
56 | 32 | 36 | Thermistor Input | 4 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31336 | 431,337
56 | 32 | 37 | Thermistor Input | 4 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31338 | 431,339
56 | 32 | 38 | Thermistor Input | 4 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31340 | 431,341
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50240 | 450,241
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50241 | 450,242
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50242 | 450,243
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50243 | 450,244
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50244 | 450,245
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50245 | 450,246
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50246 | 450,247
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50247 | 450,248
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50248 | 450,249
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50249 | 450,250
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50250 | 450,251
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50251 | 450,252
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50252 | 450,253
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50253 | 450,254
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50254 | 450,255
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50255 | 450,256
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50256 | 450,257
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50257 | 450,258
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50258 | 450,259
56 | 32 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50259 | 450,260
56 | 33 | 1 | Thermistor Input | 4 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31346 | 431,347
56 | 33 | 2 | Thermistor Input | 4 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 31348 | 431,349
56 | 33 | 3 | Thermistor Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 31350 | 431,351
56 | 33 | 4 | Thermistor Input | 4 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31352 | 431,353
56 | 33 | 5 | Thermistor Input | 4 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 31354 | 431,355
56 | 33 | 6 | Thermistor Input | 4 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 31356 | 431,357
56 | 33 | 7 | Thermistor Input | 4 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 31358 | 431,359
56 | 33 | 8 | Thermistor Input | 4 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 31360 | 431,361
56 | 33 | 9 | Thermistor Input | 4 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 31362 | 431,363
56 | 33 | 10 | Thermistor Input | 4 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 31364 | 431,365
56 | 33 | 14 | Thermistor Input | 4 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 31372 | 431,373
56 | 33 | 16 | Thermistor Input | 4 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31376 | 431,377
56 | 33 | 17 | Thermistor Input | 4 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 31378 | 431,379
56 | 33 | 18 | Thermistor Input | 4 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 31380 | 431,381
56 | 33 | 28 | Thermistor Input | 4 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 31400 | 431,401
56 | 33 | 29 | Thermistor Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31402 | 431,403
56 | 33 | 30 | Thermistor Input | 4 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 31404 | 431,405
56 | 33 | 31 | Thermistor Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31406 | 431,407
56 | 33 | 35 | Thermistor Input | 4 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31414 | 431,415
56 | 33 | 36 | Thermistor Input | 4 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31416 | 431,417
56 | 33 | 37 | Thermistor Input | 4 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31418 | 431,419
56 | 33 | 38 | Thermistor Input | 4 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31420 | 431,421
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50260 | 450,261
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50261 | 450,262
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50262 | 450,263
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50263 | 450,264
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50264 | 450,265
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50265 | 450,266
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50266 | 450,267
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50267 | 450,268
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50268 | 450,269
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50269 | 450,270
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50270 | 450,271
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50271 | 450,272
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50272 | 450,273
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50273 | 450,274
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50274 | 450,275
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50275 | 450,276
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50276 | 450,277
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50277 | 450,278
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50278 | 450,279
56 | 33 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50279 | 450,280
56 | 34 | 1 | Thermistor Input | 4 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31426 | 431,427
56 | 34 | 2 | Thermistor Input | 4 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 31428 | 431,429
56 | 34 | 3 | Thermistor Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 31430 | 431,431
56 | 34 | 4 | Thermistor Input | 4 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31432 | 431,433
56 | 34 | 5 | Thermistor Input | 4 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 31434 | 431,435
56 | 34 | 6 | Thermistor Input | 4 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 31436 | 431,437
56 | 34 | 7 | Thermistor Input | 4 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 31438 | 431,439
56 | 34 | 8 | Thermistor Input | 4 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 31440 | 431,441
56 | 34 | 9 | Thermistor Input | 4 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 31442 | 431,443
56 | 34 | 10 | Thermistor Input | 4 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 31444 | 431,445
56 | 34 | 14 | Thermistor Input | 4 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 31452 | 431,453
56 | 34 | 16 | Thermistor Input | 4 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31456 | 431,457
56 | 34 | 17 | Thermistor Input | 4 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 31458 | 431,459
56 | 34 | 18 | Thermistor Input | 4 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 31460 | 431,461
56 | 34 | 28 | Thermistor Input | 4 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 31480 | 431,481
56 | 34 | 29 | Thermistor Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31482 | 431,483
56 | 34 | 30 | Thermistor Input | 4 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 31484 | 431,485
56 | 34 | 31 | Thermistor Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31486 | 431,487
56 | 34 | 35 | Thermistor Input | 4 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31494 | 431,495
56 | 34 | 36 | Thermistor Input | 4 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31496 | 431,497
56 | 34 | 37 | Thermistor Input | 4 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31498 | 431,499
56 | 34 | 38 | Thermistor Input | 4 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31500 | 431,501
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50280 | 450,281
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50281 | 450,282
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50282 | 450,283
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50283 | 450,284
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50284 | 450,285
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50285 | 450,286
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50286 | 450,287
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50287 | 450,288
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50288 | 450,289
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50289 | 450,290
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50290 | 450,291
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50291 | 450,292
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50292 | 450,293
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50293 | 450,294
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50294 | 450,295
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50295 | 450,296
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50296 | 450,297
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50297 | 450,298
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50298 | 450,299
56 | 34 | 47 | Thermistor Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50299 | 450,300
56 | 41 | 1 | Thermistor Input | 5 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31506 | 431,507
56 | 41 | 2 | Thermistor Input | 5 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 31508 | 431,509
56 | 41 | 3 | Thermistor Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 31510 | 431,511
56 | 41 | 4 | Thermistor Input | 5 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31512 | 431,513
56 | 41 | 5 | Thermistor Input | 5 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 31514 | 431,515
56 | 41 | 6 | Thermistor Input | 5 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 31516 | 431,517
56 | 41 | 7 | Thermistor Input | 5 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 31518 | 431,519
56 | 41 | 8 | Thermistor Input | 5 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 31520 | 431,521
56 | 41 | 9 | Thermistor Input | 5 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 31522 | 431,523
56 | 41 | 10 | Thermistor Input | 5 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 31524 | 431,525
56 | 41 | 14 | Thermistor Input | 5 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 31532 | 431,533
56 | 41 | 16 | Thermistor Input | 5 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31536 | 431,537
56 | 41 | 17 | Thermistor Input | 5 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 31538 | 431,539
56 | 41 | 18 | Thermistor Input | 5 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 31540 | 431,541
56 | 41 | 28 | Thermistor Input | 5 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 31560 | 431,561
56 | 41 | 29 | Thermistor Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31562 | 431,563
56 | 41 | 30 | Thermistor Input | 5 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 31564 | 431,565
56 | 41 | 31 | Thermistor Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31566 | 431,567
56 | 41 | 35 | Thermistor Input | 5 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31574 | 431,575
56 | 41 | 36 | Thermistor Input | 5 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31576 | 431,577
56 | 41 | 37 | Thermistor Input | 5 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31578 | 431,579
56 | 41 | 38 | Thermistor Input | 5 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31580 | 431,581
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50300 | 450,301
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50301 | 450,302
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50302 | 450,303
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50303 | 450,304
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50304 | 450,305
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50305 | 450,306
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50306 | 450,307
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50307 | 450,308
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50308 | 450,309
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50309 | 450,310
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50310 | 450,311
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50311 | 450,312
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50312 | 450,313
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50313 | 450,314
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50314 | 450,315
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50315 | 450,316
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50316 | 450,317
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50317 | 450,318
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50318 | 450,319
56 | 41 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50319 | 450,320
56 | 42 | 1 | Thermistor Input | 5 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31586 | 431,587
56 | 42 | 2 | Thermistor Input | 5 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 31588 | 431,589
56 | 42 | 3 | Thermistor Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 31590 | 431,591
56 | 42 | 4 | Thermistor Input | 5 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31592 | 431,593
56 | 42 | 5 | Thermistor Input | 5 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 31594 | 431,595
56 | 42 | 6 | Thermistor Input | 5 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 31596 | 431,597
56 | 42 | 7 | Thermistor Input | 5 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 31598 | 431,599
56 | 42 | 8 | Thermistor Input | 5 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 31600 | 431,601
56 | 42 | 9 | Thermistor Input | 5 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 31602 | 431,603
56 | 42 | 10 | Thermistor Input | 5 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 31604 | 431,605
56 | 42 | 14 | Thermistor Input | 5 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 31612 | 431,613
56 | 42 | 16 | Thermistor Input | 5 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31616 | 431,617
56 | 42 | 17 | Thermistor Input | 5 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 31618 | 431,619
56 | 42 | 18 | Thermistor Input | 5 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 31620 | 431,621
56 | 42 | 28 | Thermistor Input | 5 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 31640 | 431,641
56 | 42 | 29 | Thermistor Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31642 | 431,643
56 | 42 | 30 | Thermistor Input | 5 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 31644 | 431,645
56 | 42 | 31 | Thermistor Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31646 | 431,647
56 | 42 | 35 | Thermistor Input | 5 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31654 | 431,655
56 | 42 | 36 | Thermistor Input | 5 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31656 | 431,657
56 | 42 | 37 | Thermistor Input | 5 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31658 | 431,659
56 | 42 | 38 | Thermistor Input | 5 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31660 | 431,661
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50320 | 450,321
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50321 | 450,322
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50322 | 450,323
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50323 | 450,324
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50324 | 450,325
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50325 | 450,326
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50326 | 450,327
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50327 | 450,328
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50328 | 450,329
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50329 | 450,330
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50330 | 450,331
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50331 | 450,332
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50332 | 450,333
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50333 | 450,334
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50334 | 450,335
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50335 | 450,336
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50336 | 450,337
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50337 | 450,338
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50338 | 450,339
56 | 42 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50339 | 450,340
56 | 43 | 1 | Thermistor Input | 5 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31666 | 431,667
56 | 43 | 2 | Thermistor Input | 5 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 31668 | 431,669
56 | 43 | 3 | Thermistor Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 31670 | 431,671
56 | 43 | 4 | Thermistor Input | 5 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31672 | 431,673
56 | 43 | 5 | Thermistor Input | 5 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 31674 | 431,675
56 | 43 | 6 | Thermistor Input | 5 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 31676 | 431,677
56 | 43 | 7 | Thermistor Input | 5 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 31678 | 431,679
56 | 43 | 8 | Thermistor Input | 5 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 31680 | 431,681
56 | 43 | 9 | Thermistor Input | 5 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 31682 | 431,683
56 | 43 | 10 | Thermistor Input | 5 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 31684 | 431,685
56 | 43 | 14 | Thermistor Input | 5 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 31692 | 431,693
56 | 43 | 16 | Thermistor Input | 5 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31696 | 431,697
56 | 43 | 17 | Thermistor Input | 5 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 31698 | 431,699
56 | 43 | 18 | Thermistor Input | 5 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 31700 | 431,701
56 | 43 | 28 | Thermistor Input | 5 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 31720 | 431,721
56 | 43 | 29 | Thermistor Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31722 | 431,723
56 | 43 | 30 | Thermistor Input | 5 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 31724 | 431,725
56 | 43 | 31 | Thermistor Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31726 | 431,727
56 | 43 | 35 | Thermistor Input | 5 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31734 | 431,735
56 | 43 | 36 | Thermistor Input | 5 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31736 | 431,737
56 | 43 | 37 | Thermistor Input | 5 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31738 | 431,739
56 | 43 | 38 | Thermistor Input | 5 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31740 | 431,741
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50340 | 450,341
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50341 | 450,342
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50342 | 450,343
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50343 | 450,344
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50344 | 450,345
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50345 | 450,346
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50346 | 450,347
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50347 | 450,348
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50348 | 450,349
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50349 | 450,350
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50350 | 450,351
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50351 | 450,352
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50352 | 450,353
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50353 | 450,354
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50354 | 450,355
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50355 | 450,356
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50356 | 450,357
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50357 | 450,358
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50358 | 450,359
56 | 43 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50359 | 450,360
56 | 44 | 1 | Thermistor Input | 5 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31746 | 431,747
56 | 44 | 2 | Thermistor Input | 5 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 31748 | 431,749
56 | 44 | 3 | Thermistor Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 31750 | 431,751
56 | 44 | 4 | Thermistor Input | 5 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31752 | 431,753
56 | 44 | 5 | Thermistor Input | 5 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 31754 | 431,755
56 | 44 | 6 | Thermistor Input | 5 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 31756 | 431,757
56 | 44 | 7 | Thermistor Input | 5 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 31758 | 431,759
56 | 44 | 8 | Thermistor Input | 5 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 31760 | 431,761
56 | 44 | 9 | Thermistor Input | 5 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 31762 | 431,763
56 | 44 | 10 | Thermistor Input | 5 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 31764 | 431,765
56 | 44 | 14 | Thermistor Input | 5 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 31772 | 431,773
56 | 44 | 16 | Thermistor Input | 5 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31776 | 431,777
56 | 44 | 17 | Thermistor Input | 5 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 31778 | 431,779
56 | 44 | 18 | Thermistor Input | 5 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 31780 | 431,781
56 | 44 | 28 | Thermistor Input | 5 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 31800 | 431,801
56 | 44 | 29 | Thermistor Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31802 | 431,803
56 | 44 | 30 | Thermistor Input | 5 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 31804 | 431,805
56 | 44 | 31 | Thermistor Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31806 | 431,807
56 | 44 | 35 | Thermistor Input | 5 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31814 | 431,815
56 | 44 | 36 | Thermistor Input | 5 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31816 | 431,817
56 | 44 | 37 | Thermistor Input | 5 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31818 | 431,819
56 | 44 | 38 | Thermistor Input | 5 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31820 | 431,821
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50360 | 450,361
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50361 | 450,362
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50362 | 450,363
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50363 | 450,364
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50364 | 450,365
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50365 | 450,366
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50366 | 450,367
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50367 | 450,368
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50368 | 450,369
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50369 | 450,370
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50370 | 450,371
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50371 | 450,372
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50372 | 450,373
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50373 | 450,374
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50374 | 450,375
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50375 | 450,376
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50376 | 450,377
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50377 | 450,378
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50378 | 450,379
56 | 44 | 47 | Thermistor Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50379 | 450,380
56 | 51 | 1 | Thermistor Input | 6 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31826 | 431,827
56 | 51 | 2 | Thermistor Input | 6 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 31828 | 431,829
56 | 51 | 3 | Thermistor Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 31830 | 431,831
56 | 51 | 4 | Thermistor Input | 6 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31832 | 431,833
56 | 51 | 5 | Thermistor Input | 6 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 31834 | 431,835
56 | 51 | 6 | Thermistor Input | 6 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 31836 | 431,837
56 | 51 | 7 | Thermistor Input | 6 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 31838 | 431,839
56 | 51 | 8 | Thermistor Input | 6 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 31840 | 431,841
56 | 51 | 9 | Thermistor Input | 6 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 31842 | 431,843
56 | 51 | 10 | Thermistor Input | 6 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 31844 | 431,845
56 | 51 | 14 | Thermistor Input | 6 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 31852 | 431,853
56 | 51 | 16 | Thermistor Input | 6 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31856 | 431,857
56 | 51 | 17 | Thermistor Input | 6 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 31858 | 431,859
56 | 51 | 18 | Thermistor Input | 6 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 31860 | 431,861
56 | 51 | 28 | Thermistor Input | 6 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 31880 | 431,881
56 | 51 | 29 | Thermistor Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31882 | 431,883
56 | 51 | 30 | Thermistor Input | 6 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 31884 | 431,885
56 | 51 | 31 | Thermistor Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31886 | 431,887
56 | 51 | 35 | Thermistor Input | 6 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31894 | 431,895
56 | 51 | 36 | Thermistor Input | 6 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31896 | 431,897
56 | 51 | 37 | Thermistor Input | 6 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31898 | 431,899
56 | 51 | 38 | Thermistor Input | 6 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31900 | 431,901
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50380 | 450,381
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50381 | 450,382
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50382 | 450,383
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50383 | 450,384
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50384 | 450,385
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50385 | 450,386
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50386 | 450,387
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50387 | 450,388
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50388 | 450,389
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50389 | 450,390
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50390 | 450,391
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50391 | 450,392
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50392 | 450,393
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50393 | 450,394
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50394 | 450,395
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50395 | 450,396
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50396 | 450,397
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50397 | 450,398
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50398 | 450,399
56 | 51 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50399 | 450,400
56 | 52 | 1 | Thermistor Input | 6 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31906 | 431,907
56 | 52 | 2 | Thermistor Input | 6 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 31908 | 431,909
56 | 52 | 3 | Thermistor Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 31910 | 431,911
56 | 52 | 4 | Thermistor Input | 6 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31912 | 431,913
56 | 52 | 5 | Thermistor Input | 6 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 31914 | 431,915
56 | 52 | 6 | Thermistor Input | 6 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 31916 | 431,917
56 | 52 | 7 | Thermistor Input | 6 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 31918 | 431,919
56 | 52 | 8 | Thermistor Input | 6 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 31920 | 431,921
56 | 52 | 9 | Thermistor Input | 6 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 31922 | 431,923
56 | 52 | 10 | Thermistor Input | 6 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 31924 | 431,925
56 | 52 | 14 | Thermistor Input | 6 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 31932 | 431,933
56 | 52 | 16 | Thermistor Input | 6 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31936 | 431,937
56 | 52 | 17 | Thermistor Input | 6 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 31938 | 431,939
56 | 52 | 18 | Thermistor Input | 6 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 31940 | 431,941
56 | 52 | 28 | Thermistor Input | 6 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 31960 | 431,961
56 | 52 | 29 | Thermistor Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31962 | 431,963
56 | 52 | 30 | Thermistor Input | 6 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 31964 | 431,965
56 | 52 | 31 | Thermistor Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31966 | 431,967
56 | 52 | 35 | Thermistor Input | 6 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31974 | 431,975
56 | 52 | 36 | Thermistor Input | 6 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 31976 | 431,977
56 | 52 | 37 | Thermistor Input | 6 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31978 | 431,979
56 | 52 | 38 | Thermistor Input | 6 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 31980 | 431,981
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50400 | 450,401
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50401 | 450,402
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50402 | 450,403
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50403 | 450,404
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50404 | 450,405
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50405 | 450,406
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50406 | 450,407
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50407 | 450,408
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50408 | 450,409
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50409 | 450,410
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50410 | 450,411
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50411 | 450,412
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50412 | 450,413
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50413 | 450,414
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50414 | 450,415
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50415 | 450,416
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50416 | 450,417
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50417 | 450,418
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50418 | 450,419
56 | 52 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50419 | 450,420
56 | 53 | 1 | Thermistor Input | 6 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31986 | 431,987
56 | 53 | 2 | Thermistor Input | 6 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 31988 | 431,989
56 | 53 | 3 | Thermistor Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 31990 | 431,991
56 | 53 | 4 | Thermistor Input | 6 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 31992 | 431,993
56 | 53 | 5 | Thermistor Input | 6 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 31994 | 431,995
56 | 53 | 6 | Thermistor Input | 6 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 31996 | 431,997
56 | 53 | 7 | Thermistor Input | 6 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 31998 | 431,999
56 | 53 | 8 | Thermistor Input | 6 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 32000 | 432,001
56 | 53 | 9 | Thermistor Input | 6 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 32002 | 432,003
56 | 53 | 10 | Thermistor Input | 6 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 32004 | 432,005
56 | 53 | 14 | Thermistor Input | 6 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 32012 | 432,013
56 | 53 | 16 | Thermistor Input | 6 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32016 | 432,017
56 | 53 | 17 | Thermistor Input | 6 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 32018 | 432,019
56 | 53 | 18 | Thermistor Input | 6 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 32020 | 432,021
56 | 53 | 28 | Thermistor Input | 6 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 32040 | 432,041
56 | 53 | 29 | Thermistor Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32042 | 432,043
56 | 53 | 30 | Thermistor Input | 6 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 32044 | 432,045
56 | 53 | 31 | Thermistor Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32046 | 432,047
56 | 53 | 35 | Thermistor Input | 6 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32054 | 432,055
56 | 53 | 36 | Thermistor Input | 6 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32056 | 432,057
56 | 53 | 37 | Thermistor Input | 6 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32058 | 432,059
56 | 53 | 38 | Thermistor Input | 6 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32060 | 432,061
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50420 | 450,421
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50421 | 450,422
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50422 | 450,423
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50423 | 450,424
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50424 | 450,425
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50425 | 450,426
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50426 | 450,427
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50427 | 450,428
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50428 | 450,429
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50429 | 450,430
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50430 | 450,431
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50431 | 450,432
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50432 | 450,433
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50433 | 450,434
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50434 | 450,435
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50435 | 450,436
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50436 | 450,437
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50437 | 450,438
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50438 | 450,439
56 | 53 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50439 | 450,440
56 | 54 | 1 | Thermistor Input | 6 | Analog Input Value | Monitor the signal from the thermistor input which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32066 | 432,067
56 | 54 | 2 | Thermistor Input | 6 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 32068 | 432,069
56 | 54 | 3 | Thermistor Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 32070 | 432,071
56 | 54 | 4 | Thermistor Input | 6 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32072 | 432,073
56 | 54 | 5 | Thermistor Input | 6 | Sensor Type | Set sensor type connected. | Thermistor (229), Off (62) | Thermistor (229) | Enumeration | R/W | 32074 | 432,075
56 | 54 | 6 | Thermistor Input | 6 | Resistance Range | Set resistance range of thermistor. | 5K (1448), 10K (1360), 20K (1361), 40K (1449) | 40K (1449) | Enumeration | R/W | 32076 | 432,077
56 | 54 | 7 | Thermistor Input | 6 | Thermistor Curve | Set curve for sensor attached. | Curve A (1451), Curve B (1452), Curve C (1453), Custom (180) | Curve A (1451) | Enumeration | R/W | 32078 | 432,079
56 | 54 | 8 | Thermistor Input | 6 | Coefficient A | Set coefficient A when custom is selected. | -3.4e38 to 3.4e38 | 0.001471388 | IEEE Float | R/W | 32080 | 432,081
56 | 54 | 9 | Thermistor Input | 6 | Coefficient B | Set coefficient B when custom is selected. | -3.4e38 to 3.4e38 | 0.0002376138 | IEEE Float | R/W | 32082 | 432,083
56 | 54 | 10 | Thermistor Input | 6 | Coefficient C | Set coefficient C when custom is selected. | -3.4e38 to 3.4e38 | 1.051058e-07 | IEEE Float | R/W | 32084 | 432,085
56 | 54 | 14 | Thermistor Input | 6 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 32092 | 432,093
56 | 54 | 16 | Thermistor Input | 6 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32096 | 432,097
56 | 54 | 17 | Thermistor Input | 6 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 32098 | 432,099
56 | 54 | 18 | Thermistor Input | 6 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 32100 | 432,101
56 | 54 | 28 | Thermistor Input | 6 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 32120 | 432,121
56 | 54 | 29 | Thermistor Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32122 | 432,123
56 | 54 | 30 | Thermistor Input | 6 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 32124 | 432,125
56 | 54 | 31 | Thermistor Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32126 | 432,127
56 | 54 | 35 | Thermistor Input | 6 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32134 | 432,135
56 | 54 | 36 | Thermistor Input | 6 | Electrical Input Offset | Set the electrical input offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32136 | 432,137
56 | 54 | 37 | Thermistor Input | 6 | Electrical Input Slope | Set the electrical input slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32138 | 432,139
56 | 54 | 38 | Thermistor Input | 6 | Calibration Slope | Set the calibration slope. | -99,999.0 to 99,999.0 | 1.0 | IEEE Float | R/W | 32140 | 432,141
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50440 | 450,441
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50441 | 450,442
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50442 | 450,443
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50443 | 450,444
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50444 | 450,445
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50445 | 450,446
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50446 | 450,447
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50447 | 450,448
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50448 | 450,449
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50449 | 450,450
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50450 | 450,451
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50451 | 450,452
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50452 | 450,453
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50453 | 450,454
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50454 | 450,455
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50455 | 450,456
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50456 | 450,457
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50457 | 450,458
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50458 | 450,459
56 | 54 | 47 | Thermistor Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50459 | 450,460
57 | 1 | 1 | Temperature Input | 1 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32146 | 432,147
57 | 1 | 2 | Temperature Input | 1 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 32148 | 432,149
57 | 1 | 3 | Temperature Input | 1 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 32150 | 432,151
57 | 1 | 4 | Temperature Input | 1 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32152 | 432,153
57 | 1 | 5 | Temperature Input | 1 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | Enumeration | R/W | 32154 | 432,155
57 | 1 | 6 | Temperature Input | 1 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 32156 | 432,157
57 | 1 | 7 | Temperature Input | 1 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | Enumeration | R/W | 32158 | 432,159
57 | 1 | 14 | Temperature Input | 1 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 32172 | 432,173
57 | 1 | 16 | Temperature Input | 1 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32176 | 432,177
57 | 1 | 17 | Temperature Input | 1 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 32178 | 432,179
57 | 1 | 18 | Temperature Input | 1 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 32180 | 432,181
57 | 1 | 28 | Temperature Input | 1 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 32200 | 432,201
57 | 1 | 29 | Temperature Input | 1 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32202 | 432,203
57 | 1 | 30 | Temperature Input | 1 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 32204 | 432,205
57 | 1 | 31 | Temperature Input | 1 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32206 | 432,207
57 | 1 | 35 | Temperature Input | 1 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32214 | 432,215
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50460 | 450,461
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50461 | 450,462
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50462 | 450,463
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50463 | 450,464
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50464 | 450,465
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50465 | 450,466
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50466 | 450,467
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50467 | 450,468
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50468 | 450,469
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50469 | 450,470
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50470 | 450,471
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50471 | 450,472
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50472 | 450,473
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50473 | 450,474
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50474 | 450,475
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50475 | 450,476
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50476 | 450,477
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50477 | 450,478
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50478 | 450,479
57 | 1 | 47 | Temperature Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50479 | 450,480
57 | 11 | 1 | Temperature Input | 2 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32216 | 432,217
57 | 11 | 2 | Temperature Input | 2 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 32218 | 432,219
57 | 11 | 3 | Temperature Input | 2 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 32220 | 432,221
57 | 11 | 4 | Temperature Input | 2 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32222 | 432,223
57 | 11 | 5 | Temperature Input | 2 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | Enumeration | R/W | 32224 | 432,225
57 | 11 | 6 | Temperature Input | 2 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 32226 | 432,227
57 | 11 | 7 | Temperature Input | 2 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | Enumeration | R/W | 32228 | 432,229
57 | 11 | 14 | Temperature Input | 2 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 32242 | 432,243
57 | 11 | 16 | Temperature Input | 2 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32246 | 432,247
57 | 11 | 17 | Temperature Input | 2 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 32248 | 432,249
57 | 11 | 18 | Temperature Input | 2 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 32250 | 432,251
57 | 11 | 28 | Temperature Input | 2 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 32270 | 432,271
57 | 11 | 29 | Temperature Input | 2 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32272 | 432,273
57 | 11 | 30 | Temperature Input | 2 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 32274 | 432,275
57 | 11 | 31 | Temperature Input | 2 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32276 | 432,277
57 | 11 | 35 | Temperature Input | 2 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32284 | 432,285
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50480 | 450,481
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50481 | 450,482
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50482 | 450,483
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50483 | 450,484
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50484 | 450,485
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50485 | 450,486
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50486 | 450,487
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50487 | 450,488
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50488 | 450,489
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50489 | 450,490
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50490 | 450,491
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50491 | 450,492
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50492 | 450,493
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50493 | 450,494
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50494 | 450,495
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50495 | 450,496
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50496 | 450,497
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50497 | 450,498
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50498 | 450,499
57 | 11 | 47 | Temperature Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50499 | 450,500
57 | 21 | 1 | Temperature Input | 3 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32286 | 432,287
57 | 21 | 2 | Temperature Input | 3 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 32288 | 432,289
57 | 21 | 3 | Temperature Input | 3 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 32290 | 432,291
57 | 21 | 4 | Temperature Input | 3 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32292 | 432,293
57 | 21 | 5 | Temperature Input | 3 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | Enumeration | R/W | 32294 | 432,295
57 | 21 | 6 | Temperature Input | 3 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 32296 | 432,297
57 | 21 | 7 | Temperature Input | 3 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | Enumeration | R/W | 32298 | 432,299
57 | 21 | 14 | Temperature Input | 3 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 32312 | 432,313
57 | 21 | 16 | Temperature Input | 3 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32316 | 432,317
57 | 21 | 17 | Temperature Input | 3 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 32318 | 432,319
57 | 21 | 18 | Temperature Input | 3 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 32320 | 432,321
57 | 21 | 28 | Temperature Input | 3 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 32340 | 432,341
57 | 21 | 29 | Temperature Input | 3 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32342 | 432,343
57 | 21 | 30 | Temperature Input | 3 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 32344 | 432,345
57 | 21 | 31 | Temperature Input | 3 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32346 | 432,347
57 | 21 | 35 | Temperature Input | 3 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32354 | 432,355
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50500 | 450,501
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50501 | 450,502
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50502 | 450,503
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50503 | 450,504
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50504 | 450,505
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50505 | 450,506
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50506 | 450,507
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50507 | 450,508
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50508 | 450,509
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50509 | 450,510
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50510 | 450,511
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50511 | 450,512
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50512 | 450,513
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50513 | 450,514
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50514 | 450,515
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50515 | 450,516
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50516 | 450,517
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50517 | 450,518
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50518 | 450,519
57 | 21 | 47 | Temperature Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50519 | 450,520
57 | 31 | 1 | Temperature Input | 4 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32356 | 432,357
57 | 31 | 2 | Temperature Input | 4 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 32358 | 432,359
57 | 31 | 3 | Temperature Input | 4 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 32360 | 432,361
57 | 31 | 4 | Temperature Input | 4 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32362 | 432,363
57 | 31 | 5 | Temperature Input | 4 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | Enumeration | R/W | 32364 | 432,365
57 | 31 | 6 | Temperature Input | 4 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 32366 | 432,367
57 | 31 | 7 | Temperature Input | 4 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | Enumeration | R/W | 32368 | 432,369
57 | 31 | 14 | Temperature Input | 4 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 32382 | 432,383
57 | 31 | 16 | Temperature Input | 4 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32386 | 432,387
57 | 31 | 17 | Temperature Input | 4 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 32388 | 432,389
57 | 31 | 18 | Temperature Input | 4 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 32390 | 432,391
57 | 31 | 28 | Temperature Input | 4 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 32410 | 432,411
57 | 31 | 29 | Temperature Input | 4 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32412 | 432,413
57 | 31 | 30 | Temperature Input | 4 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 32414 | 432,415
57 | 31 | 31 | Temperature Input | 4 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32416 | 432,417
57 | 31 | 35 | Temperature Input | 4 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32424 | 432,425
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50520 | 450,521
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50521 | 450,522
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50522 | 450,523
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50523 | 450,524
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50524 | 450,525
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50525 | 450,526
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50526 | 450,527
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50527 | 450,528
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50528 | 450,529
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50529 | 450,530
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50530 | 450,531
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50531 | 450,532
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50532 | 450,533
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50533 | 450,534
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50534 | 450,535
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50535 | 450,536
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50536 | 450,537
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50537 | 450,538
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50538 | 450,539
57 | 31 | 47 | Temperature Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50539 | 450,540
57 | 41 | 1 | Temperature Input | 5 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32426 | 432,427
57 | 41 | 2 | Temperature Input | 5 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 32428 | 432,429
57 | 41 | 3 | Temperature Input | 5 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 32430 | 432,431
57 | 41 | 4 | Temperature Input | 5 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32432 | 432,433
57 | 41 | 5 | Temperature Input | 5 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | Enumeration | R/W | 32434 | 432,435
57 | 41 | 6 | Temperature Input | 5 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 32436 | 432,437
57 | 41 | 7 | Temperature Input | 5 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | Enumeration | R/W | 32438 | 432,439
57 | 41 | 14 | Temperature Input | 5 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 32452 | 432,453
57 | 41 | 16 | Temperature Input | 5 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32456 | 432,457
57 | 41 | 17 | Temperature Input | 5 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 32458 | 432,459
57 | 41 | 18 | Temperature Input | 5 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 32460 | 432,461
57 | 41 | 28 | Temperature Input | 5 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 32480 | 432,481
57 | 41 | 29 | Temperature Input | 5 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32482 | 432,483
57 | 41 | 30 | Temperature Input | 5 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 32484 | 432,485
57 | 41 | 31 | Temperature Input | 5 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32486 | 432,487
57 | 41 | 35 | Temperature Input | 5 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32494 | 432,495
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50540 | 450,541
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50541 | 450,542
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50542 | 450,543
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50543 | 450,544
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50544 | 450,545
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50545 | 450,546
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50546 | 450,547
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50547 | 450,548
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50548 | 450,549
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50549 | 450,550
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50550 | 450,551
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50551 | 450,552
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50552 | 450,553
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50553 | 450,554
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50554 | 450,555
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50555 | 450,556
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50556 | 450,557
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50557 | 450,558
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50558 | 450,559
57 | 41 | 47 | Temperature Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50559 | 450,560
57 | 51 | 1 | Temperature Input | 6 | Analog Input Value | Monitor the signal from the sensor input before filter is applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32496 | 432,497
57 | 51 | 2 | Temperature Input | 6 | Input Error | Monitor the sensor for an input error. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32) |  | Enumeration | R | 32498 | 432,499
57 | 51 | 3 | Temperature Input | 6 | Filter | Set to apply a first-order filter time constant to the sensor signal. | 0.0 to 60.0 | 0.5 | IEEE Float | R/W | 32500 | 432,501
57 | 51 | 4 | Temperature Input | 6 | Filtered Process Value | Monitor the signal from the sensor input after filter has been applied which carries the process value to the PV receiver on the loop block where it is used as feedback to the control algorithm. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32502 | 432,503
57 | 51 | 5 | Temperature Input | 6 | Sensor Type | Set sensor type connected. | Off (62), Thermocouple (95), RTD 100 Ohm (113), RTD 1000 Ohm (114) | Thermocouple (95) | Enumeration | R/W | 32504 | 432,505
57 | 51 | 6 | Temperature Input | 6 | TC Linearization | Set sensor linearization when thermocouple. | B (11), C (15), D (23), E (26), F (30), J (46), K (48), N (58), R (80), S (84), T (93) | J (46) | Enumeration | R/W | 32506 | 432,507
57 | 51 | 7 | Temperature Input | 6 | RTD Leads | Set number of RTD wires connected. | 2 (1) | 2 (1) | Enumeration | R/W | 32508 | 432,509
57 | 51 | 14 | Temperature Input | 6 | Display Precision | Set display precision. | Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 32522 | 432,523
57 | 51 | 16 | Temperature Input | 6 | Calibration Offset | Set offset to apply to sensor read value to compensate for an inaccurate sensor, lead resistance or other factors that affect the input value. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32526 | 432,527
57 | 51 | 17 | Temperature Input | 6 | Input Error Latching | Set behavior for intermittent sensor failure. | Off (62), On (63) | Off (62) | Enumeration | R/W | 32528 | 432,529
57 | 51 | 18 | Temperature Input | 6 | Clear Error | Request a latched sensor error to be cleared. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 32530 | 432,531
57 | 51 | 28 | Temperature Input | 6 | Electrical Measurement | Monitor the sensor's electrical value. | -3.4e38 to 3.4e38 |  | IEEE Float | R | 32550 | 432,551
57 | 51 | 29 | Temperature Input | 6 | RTD Lead Resistance | Monitor the RTD measured lead resistance. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32552 | 432,553
57 | 51 | 30 | Temperature Input | 6 | Measure CJC | Set to enable/disable cold junction compensation for thermocouples. | Off (62), On (63) | On (63) | Enumeration | R/W | 32554 | 432,555
57 | 51 | 31 | Temperature Input | 6 | Ambient Temperature | Monitor the ambient temperature inside controller. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 32556 | 432,557
57 | 51 | 35 | Temperature Input | 6 | Ambient Offset | Set ambient temperature offset. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 32564 | 432,565
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50560 | 450,561
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50561 | 450,562
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50562 | 450,563
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50563 | 450,564
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50564 | 450,565
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50565 | 450,566
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50566 | 450,567
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50567 | 450,568
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50568 | 450,569
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50569 | 450,570
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50570 | 450,571
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50571 | 450,572
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50572 | 450,573
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50573 | 450,574
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50574 | 450,575
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50575 | 450,576
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50576 | 450,577
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50577 | 450,578
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50578 | 450,579
57 | 51 | 47 | Temperature Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50579 | 450,580
60 | 2 | 1 | Digital Input | 1 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | Enumeration | R/W | 33466 | 433,467
60 | 2 | 11 | Digital Input | 1 | Input State | Monitor input state. | On (63), Off (62) |  | Enumeration | R | 33486 | 433,487
60 | 2 | 18 | Digital Input | 1 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 33500 | 433,501
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50580 | 450,581
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50581 | 450,582
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50582 | 450,583
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50583 | 450,584
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50584 | 450,585
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50585 | 450,586
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50586 | 450,587
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50587 | 450,588
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50588 | 450,589
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50589 | 450,590
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50590 | 450,591
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50591 | 450,592
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50592 | 450,593
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50593 | 450,594
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50594 | 450,595
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50595 | 450,596
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50596 | 450,597
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50597 | 450,598
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50598 | 450,599
60 | 2 | 19 | Digital Input | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50599 | 450,600
60 | 12 | 1 | Digital Input | 2 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | Enumeration | R/W | 33506 | 433,507
60 | 12 | 11 | Digital Input | 2 | Input State | Monitor input state. | On (63), Off (62) |  | Enumeration | R | 33526 | 433,527
60 | 12 | 18 | Digital Input | 2 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 33540 | 433,541
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50600 | 450,601
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50601 | 450,602
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50602 | 450,603
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50603 | 450,604
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50604 | 450,605
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50605 | 450,606
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50606 | 450,607
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50607 | 450,608
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50608 | 450,609
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50609 | 450,610
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50610 | 450,611
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50611 | 450,612
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50612 | 450,613
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50613 | 450,614
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50614 | 450,615
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50615 | 450,616
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50616 | 450,617
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50617 | 450,618
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50618 | 450,619
60 | 12 | 19 | Digital Input | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50619 | 450,620
60 | 22 | 1 | Digital Input | 3 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | Enumeration | R/W | 33546 | 433,547
60 | 22 | 11 | Digital Input | 3 | Input State | Monitor input state. | On (63), Off (62) |  | Enumeration | R | 33566 | 433,567
60 | 22 | 18 | Digital Input | 3 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 33580 | 433,581
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50620 | 450,621
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50621 | 450,622
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50622 | 450,623
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50623 | 450,624
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50624 | 450,625
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50625 | 450,626
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50626 | 450,627
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50627 | 450,628
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50628 | 450,629
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50629 | 450,630
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50630 | 450,631
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50631 | 450,632
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50632 | 450,633
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50633 | 450,634
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50634 | 450,635
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50635 | 450,636
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50636 | 450,637
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50637 | 450,638
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50638 | 450,639
60 | 22 | 19 | Digital Input | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50639 | 450,640
60 | 32 | 1 | Digital Input | 4 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | Enumeration | R/W | 33586 | 433,587
60 | 32 | 11 | Digital Input | 4 | Input State | Monitor input state. | On (63), Off (62) |  | Enumeration | R | 33606 | 433,607
60 | 32 | 18 | Digital Input | 4 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 33620 | 433,621
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50640 | 450,641
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50641 | 450,642
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50642 | 450,643
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50643 | 450,644
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50644 | 450,645
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50645 | 450,646
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50646 | 450,647
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50647 | 450,648
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50648 | 450,649
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50649 | 450,650
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50650 | 450,651
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50651 | 450,652
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50652 | 450,653
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50653 | 450,654
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50654 | 450,655
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50655 | 450,656
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50656 | 450,657
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50657 | 450,658
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50658 | 450,659
60 | 32 | 19 | Digital Input | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50659 | 450,660
60 | 42 | 1 | Digital Input | 5 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | Enumeration | R/W | 33626 | 433,627
60 | 42 | 11 | Digital Input | 5 | Input State | Monitor input state. | On (63), Off (62) |  | Enumeration | R | 33646 | 433,647
60 | 42 | 18 | Digital Input | 5 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 33660 | 433,661
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50660 | 450,661
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50661 | 450,662
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50662 | 450,663
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50663 | 450,664
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50664 | 450,665
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50665 | 450,666
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50666 | 450,667
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50667 | 450,668
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50668 | 450,669
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50669 | 450,670
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50670 | 450,671
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50671 | 450,672
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50672 | 450,673
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50673 | 450,674
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50674 | 450,675
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50675 | 450,676
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50676 | 450,677
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50677 | 450,678
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50678 | 450,679
60 | 42 | 19 | Digital Input | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50679 | 450,680
60 | 52 | 1 | Digital Input | 6 | Input Type | Set input type. | Input Voltage (193), Input Dry Contact (44) | Input Dry Contact (44) | Enumeration | R/W | 33666 | 433,667
60 | 52 | 11 | Digital Input | 6 | Input State | Monitor input state. | On (63), Off (62) |  | Enumeration | R | 33686 | 433,687
60 | 52 | 18 | Digital Input | 6 | Error | Monitor input for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 33700 | 433,701
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50680 | 450,681
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50681 | 450,682
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50682 | 450,683
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50683 | 450,684
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50684 | 450,685
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50685 | 450,686
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50686 | 450,687
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50687 | 450,688
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50688 | 450,689
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50689 | 450,690
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50690 | 450,691
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50691 | 450,692
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50692 | 450,693
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50693 | 450,694
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50694 | 450,695
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50695 | 450,696
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50696 | 450,697
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50697 | 450,698
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50698 | 450,699
60 | 52 | 19 | Digital Input | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50699 | 450,700
61 | 1 | 1 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 33706 | 433,707
61 | 1 | 2 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 33708 | 433,709
61 | 1 | 3 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 33710 | 433,711
61 | 1 | 4 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 33712 | 433,713
61 | 1 | 5 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 33714 | 433,715
61 | 1 | 6 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33716 | 433,717
61 | 1 | 7 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 33718 | 433,719
61 | 1 | 8 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 33720 | 433,721
61 | 1 | 9 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 33722 | 433,723
61 | 1 | 10 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 33724 | 433,725
61 | 1 | 11 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 33726 | 433,727
61 | 1 | 12 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33728 | 433,729
61 | 1 | 13 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 33730 | 433,731
61 | 1 | 15 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 33734 | 433,735
61 | 1 | 18 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 33740 | 433,741
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50700 | 450,701
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50701 | 450,702
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50702 | 450,703
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50703 | 450,704
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50704 | 450,705
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50705 | 450,706
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50706 | 450,707
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50707 | 450,708
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50708 | 450,709
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50709 | 450,710
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50710 | 450,711
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50711 | 450,712
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50712 | 450,713
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50713 | 450,714
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50714 | 450,715
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50715 | 450,716
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50716 | 450,717
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50717 | 450,718
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50718 | 450,719
61 | 1 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50719 | 450,720
61 | 2 | 1 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 33746 | 433,747
61 | 2 | 2 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 33748 | 433,749
61 | 2 | 3 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 33750 | 433,751
61 | 2 | 4 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 33752 | 433,753
61 | 2 | 5 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 33754 | 433,755
61 | 2 | 6 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33756 | 433,757
61 | 2 | 7 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 33758 | 433,759
61 | 2 | 8 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 33760 | 433,761
61 | 2 | 9 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 33762 | 433,763
61 | 2 | 10 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 33764 | 433,765
61 | 2 | 11 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 33766 | 433,767
61 | 2 | 12 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33768 | 433,769
61 | 2 | 13 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 33770 | 433,771
61 | 2 | 15 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 33774 | 433,775
61 | 2 | 18 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 33780 | 433,781
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50720 | 450,721
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50721 | 450,722
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50722 | 450,723
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50723 | 450,724
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50724 | 450,725
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50725 | 450,726
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50726 | 450,727
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50727 | 450,728
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50728 | 450,729
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50729 | 450,730
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50730 | 450,731
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50731 | 450,732
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50732 | 450,733
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50733 | 450,734
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50734 | 450,735
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50735 | 450,736
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50736 | 450,737
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50737 | 450,738
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50738 | 450,739
61 | 2 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50739 | 450,740
61 | 3 | 1 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 33786 | 433,787
61 | 3 | 2 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 33788 | 433,789
61 | 3 | 3 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 33790 | 433,791
61 | 3 | 4 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 33792 | 433,793
61 | 3 | 5 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 33794 | 433,795
61 | 3 | 6 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33796 | 433,797
61 | 3 | 7 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 33798 | 433,799
61 | 3 | 8 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 33800 | 433,801
61 | 3 | 9 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 33802 | 433,803
61 | 3 | 10 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 33804 | 433,805
61 | 3 | 11 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 33806 | 433,807
61 | 3 | 12 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33808 | 433,809
61 | 3 | 13 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 33810 | 433,811
61 | 3 | 15 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 33814 | 433,815
61 | 3 | 18 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 33820 | 433,821
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50740 | 450,741
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50741 | 450,742
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50742 | 450,743
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50743 | 450,744
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50744 | 450,745
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50745 | 450,746
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50746 | 450,747
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50747 | 450,748
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50748 | 450,749
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50749 | 450,750
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50750 | 450,751
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50751 | 450,752
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50752 | 450,753
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50753 | 450,754
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50754 | 450,755
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50755 | 450,756
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50756 | 450,757
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50757 | 450,758
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50758 | 450,759
61 | 3 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50759 | 450,760
61 | 4 | 1 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 33826 | 433,827
61 | 4 | 2 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 33828 | 433,829
61 | 4 | 3 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 33830 | 433,831
61 | 4 | 4 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 33832 | 433,833
61 | 4 | 5 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 33834 | 433,835
61 | 4 | 6 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33836 | 433,837
61 | 4 | 7 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 33838 | 433,839
61 | 4 | 8 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 33840 | 433,841
61 | 4 | 9 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 33842 | 433,843
61 | 4 | 10 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 33844 | 433,845
61 | 4 | 11 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 33846 | 433,847
61 | 4 | 12 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33848 | 433,849
61 | 4 | 13 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 33850 | 433,851
61 | 4 | 15 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 33854 | 433,855
61 | 4 | 18 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 33860 | 433,861
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50760 | 450,761
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50761 | 450,762
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50762 | 450,763
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50763 | 450,764
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50764 | 450,765
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50765 | 450,766
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50766 | 450,767
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50767 | 450,768
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50768 | 450,769
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50769 | 450,770
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50770 | 450,771
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50771 | 450,772
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50772 | 450,773
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50773 | 450,774
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50774 | 450,775
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50775 | 450,776
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50776 | 450,777
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50777 | 450,778
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50778 | 450,779
61 | 4 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50779 | 450,780
61 | 5 | 1 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 33866 | 433,867
61 | 5 | 2 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 33868 | 433,869
61 | 5 | 3 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 33870 | 433,871
61 | 5 | 4 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 33872 | 433,873
61 | 5 | 5 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 33874 | 433,875
61 | 5 | 6 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33876 | 433,877
61 | 5 | 7 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 33878 | 433,879
61 | 5 | 8 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 33880 | 433,881
61 | 5 | 9 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 33882 | 433,883
61 | 5 | 10 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 33884 | 433,885
61 | 5 | 11 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 33886 | 433,887
61 | 5 | 12 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33888 | 433,889
61 | 5 | 13 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 33890 | 433,891
61 | 5 | 15 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 33894 | 433,895
61 | 5 | 18 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 33900 | 433,901
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50780 | 450,781
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50781 | 450,782
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50782 | 450,783
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50783 | 450,784
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50784 | 450,785
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50785 | 450,786
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50786 | 450,787
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50787 | 450,788
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50788 | 450,789
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50789 | 450,790
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50790 | 450,791
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50791 | 450,792
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50792 | 450,793
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50793 | 450,794
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50794 | 450,795
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50795 | 450,796
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50796 | 450,797
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50797 | 450,798
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50798 | 450,799
61 | 5 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50799 | 450,800
61 | 6 | 1 | Digital I/O | 1 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 33906 | 433,907
61 | 6 | 2 | Digital I/O | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 33908 | 433,909
61 | 6 | 3 | Digital I/O | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 33910 | 433,911
61 | 6 | 4 | Digital I/O | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 33912 | 433,913
61 | 6 | 5 | Digital I/O | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 33914 | 433,915
61 | 6 | 6 | Digital I/O | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33916 | 433,917
61 | 6 | 7 | Digital I/O | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 33918 | 433,919
61 | 6 | 8 | Digital I/O | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 33920 | 433,921
61 | 6 | 9 | Digital I/O | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 33922 | 433,923
61 | 6 | 10 | Digital I/O | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 33924 | 433,925
61 | 6 | 11 | Digital I/O | 1 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 33926 | 433,927
61 | 6 | 12 | Digital I/O | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33928 | 433,929
61 | 6 | 13 | Digital I/O | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 33930 | 433,931
61 | 6 | 15 | Digital I/O | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 33934 | 433,935
61 | 6 | 18 | Digital I/O | 1 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 33940 | 433,941
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50800 | 450,801
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50801 | 450,802
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50802 | 450,803
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50803 | 450,804
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50804 | 450,805
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50805 | 450,806
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50806 | 450,807
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50807 | 450,808
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50808 | 450,809
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50809 | 450,810
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50810 | 450,811
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50811 | 450,812
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50812 | 450,813
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50813 | 450,814
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50814 | 450,815
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50815 | 450,816
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50816 | 450,817
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50817 | 450,818
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50818 | 450,819
61 | 6 | 19 | Digital I/O | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50819 | 450,820
61 | 11 | 1 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 33946 | 433,947
61 | 11 | 2 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 33948 | 433,949
61 | 11 | 3 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 33950 | 433,951
61 | 11 | 4 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 33952 | 433,953
61 | 11 | 5 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 33954 | 433,955
61 | 11 | 6 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33956 | 433,957
61 | 11 | 7 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 33958 | 433,959
61 | 11 | 8 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 33960 | 433,961
61 | 11 | 9 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 33962 | 433,963
61 | 11 | 10 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 33964 | 433,965
61 | 11 | 11 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 33966 | 433,967
61 | 11 | 12 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 33968 | 433,969
61 | 11 | 13 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 33970 | 433,971
61 | 11 | 15 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 33974 | 433,975
61 | 11 | 18 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 33980 | 433,981
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50820 | 450,821
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50821 | 450,822
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50822 | 450,823
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50823 | 450,824
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50824 | 450,825
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50825 | 450,826
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50826 | 450,827
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50827 | 450,828
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50828 | 450,829
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50829 | 450,830
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50830 | 450,831
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50831 | 450,832
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50832 | 450,833
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50833 | 450,834
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50834 | 450,835
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50835 | 450,836
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50836 | 450,837
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50837 | 450,838
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50838 | 450,839
61 | 11 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50839 | 450,840
61 | 12 | 1 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 33986 | 433,987
61 | 12 | 2 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 33988 | 433,989
61 | 12 | 3 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 33990 | 433,991
61 | 12 | 4 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 33992 | 433,993
61 | 12 | 5 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 33994 | 433,995
61 | 12 | 6 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 33996 | 433,997
61 | 12 | 7 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 33998 | 433,999
61 | 12 | 8 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34000 | 434,001
61 | 12 | 9 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34002 | 434,003
61 | 12 | 10 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34004 | 434,005
61 | 12 | 11 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34006 | 434,007
61 | 12 | 12 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34008 | 434,009
61 | 12 | 13 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34010 | 434,011
61 | 12 | 15 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34014 | 434,015
61 | 12 | 18 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34020 | 434,021
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50840 | 450,841
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50841 | 450,842
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50842 | 450,843
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50843 | 450,844
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50844 | 450,845
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50845 | 450,846
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50846 | 450,847
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50847 | 450,848
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50848 | 450,849
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50849 | 450,850
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50850 | 450,851
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50851 | 450,852
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50852 | 450,853
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50853 | 450,854
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50854 | 450,855
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50855 | 450,856
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50856 | 450,857
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50857 | 450,858
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50858 | 450,859
61 | 12 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50859 | 450,860
61 | 13 | 1 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34026 | 434,027
61 | 13 | 2 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34028 | 434,029
61 | 13 | 3 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34030 | 434,031
61 | 13 | 4 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34032 | 434,033
61 | 13 | 5 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34034 | 434,035
61 | 13 | 6 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34036 | 434,037
61 | 13 | 7 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34038 | 434,039
61 | 13 | 8 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34040 | 434,041
61 | 13 | 9 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34042 | 434,043
61 | 13 | 10 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34044 | 434,045
61 | 13 | 11 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34046 | 434,047
61 | 13 | 12 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34048 | 434,049
61 | 13 | 13 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34050 | 434,051
61 | 13 | 15 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34054 | 434,055
61 | 13 | 18 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34060 | 434,061
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50860 | 450,861
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50861 | 450,862
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50862 | 450,863
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50863 | 450,864
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50864 | 450,865
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50865 | 450,866
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50866 | 450,867
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50867 | 450,868
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50868 | 450,869
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50869 | 450,870
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50870 | 450,871
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50871 | 450,872
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50872 | 450,873
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50873 | 450,874
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50874 | 450,875
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50875 | 450,876
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50876 | 450,877
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50877 | 450,878
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50878 | 450,879
61 | 13 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50879 | 450,880
61 | 14 | 1 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34066 | 434,067
61 | 14 | 2 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34068 | 434,069
61 | 14 | 3 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34070 | 434,071
61 | 14 | 4 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34072 | 434,073
61 | 14 | 5 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34074 | 434,075
61 | 14 | 6 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34076 | 434,077
61 | 14 | 7 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34078 | 434,079
61 | 14 | 8 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34080 | 434,081
61 | 14 | 9 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34082 | 434,083
61 | 14 | 10 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34084 | 434,085
61 | 14 | 11 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34086 | 434,087
61 | 14 | 12 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34088 | 434,089
61 | 14 | 13 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34090 | 434,091
61 | 14 | 15 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34094 | 434,095
61 | 14 | 18 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34100 | 434,101
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50880 | 450,881
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50881 | 450,882
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50882 | 450,883
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50883 | 450,884
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50884 | 450,885
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50885 | 450,886
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50886 | 450,887
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50887 | 450,888
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50888 | 450,889
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50889 | 450,890
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50890 | 450,891
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50891 | 450,892
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50892 | 450,893
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50893 | 450,894
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50894 | 450,895
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50895 | 450,896
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50896 | 450,897
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50897 | 450,898
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50898 | 450,899
61 | 14 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50899 | 450,900
61 | 15 | 1 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34106 | 434,107
61 | 15 | 2 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34108 | 434,109
61 | 15 | 3 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34110 | 434,111
61 | 15 | 4 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34112 | 434,113
61 | 15 | 5 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34114 | 434,115
61 | 15 | 6 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34116 | 434,117
61 | 15 | 7 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34118 | 434,119
61 | 15 | 8 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34120 | 434,121
61 | 15 | 9 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34122 | 434,123
61 | 15 | 10 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34124 | 434,125
61 | 15 | 11 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34126 | 434,127
61 | 15 | 12 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34128 | 434,129
61 | 15 | 13 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34130 | 434,131
61 | 15 | 15 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34134 | 434,135
61 | 15 | 18 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34140 | 434,141
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50900 | 450,901
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50901 | 450,902
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50902 | 450,903
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50903 | 450,904
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50904 | 450,905
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50905 | 450,906
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50906 | 450,907
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50907 | 450,908
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50908 | 450,909
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50909 | 450,910
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50910 | 450,911
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50911 | 450,912
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50912 | 450,913
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50913 | 450,914
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50914 | 450,915
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50915 | 450,916
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50916 | 450,917
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50917 | 450,918
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50918 | 450,919
61 | 15 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50919 | 450,920
61 | 16 | 1 | Digital I/O | 2 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34146 | 434,147
61 | 16 | 2 | Digital I/O | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34148 | 434,149
61 | 16 | 3 | Digital I/O | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34150 | 434,151
61 | 16 | 4 | Digital I/O | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34152 | 434,153
61 | 16 | 5 | Digital I/O | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34154 | 434,155
61 | 16 | 6 | Digital I/O | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34156 | 434,157
61 | 16 | 7 | Digital I/O | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34158 | 434,159
61 | 16 | 8 | Digital I/O | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34160 | 434,161
61 | 16 | 9 | Digital I/O | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34162 | 434,163
61 | 16 | 10 | Digital I/O | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34164 | 434,165
61 | 16 | 11 | Digital I/O | 2 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34166 | 434,167
61 | 16 | 12 | Digital I/O | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34168 | 434,169
61 | 16 | 13 | Digital I/O | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34170 | 434,171
61 | 16 | 15 | Digital I/O | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34174 | 434,175
61 | 16 | 18 | Digital I/O | 2 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34180 | 434,181
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50920 | 450,921
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50921 | 450,922
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50922 | 450,923
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50923 | 450,924
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50924 | 450,925
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50925 | 450,926
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50926 | 450,927
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50927 | 450,928
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50928 | 450,929
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50929 | 450,930
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50930 | 450,931
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50931 | 450,932
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50932 | 450,933
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50933 | 450,934
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50934 | 450,935
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50935 | 450,936
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50936 | 450,937
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50937 | 450,938
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50938 | 450,939
61 | 16 | 19 | Digital I/O | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50939 | 450,940
61 | 21 | 1 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34186 | 434,187
61 | 21 | 2 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34188 | 434,189
61 | 21 | 3 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34190 | 434,191
61 | 21 | 4 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34192 | 434,193
61 | 21 | 5 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34194 | 434,195
61 | 21 | 6 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34196 | 434,197
61 | 21 | 7 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34198 | 434,199
61 | 21 | 8 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34200 | 434,201
61 | 21 | 9 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34202 | 434,203
61 | 21 | 10 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34204 | 434,205
61 | 21 | 11 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34206 | 434,207
61 | 21 | 12 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34208 | 434,209
61 | 21 | 13 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34210 | 434,211
61 | 21 | 15 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34214 | 434,215
61 | 21 | 18 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34220 | 434,221
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50940 | 450,941
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50941 | 450,942
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50942 | 450,943
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50943 | 450,944
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50944 | 450,945
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50945 | 450,946
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50946 | 450,947
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50947 | 450,948
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50948 | 450,949
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50949 | 450,950
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50950 | 450,951
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50951 | 450,952
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50952 | 450,953
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50953 | 450,954
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50954 | 450,955
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50955 | 450,956
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50956 | 450,957
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50957 | 450,958
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50958 | 450,959
61 | 21 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50959 | 450,960
61 | 22 | 1 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34226 | 434,227
61 | 22 | 2 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34228 | 434,229
61 | 22 | 3 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34230 | 434,231
61 | 22 | 4 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34232 | 434,233
61 | 22 | 5 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34234 | 434,235
61 | 22 | 6 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34236 | 434,237
61 | 22 | 7 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34238 | 434,239
61 | 22 | 8 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34240 | 434,241
61 | 22 | 9 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34242 | 434,243
61 | 22 | 10 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34244 | 434,245
61 | 22 | 11 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34246 | 434,247
61 | 22 | 12 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34248 | 434,249
61 | 22 | 13 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34250 | 434,251
61 | 22 | 15 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34254 | 434,255
61 | 22 | 18 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34260 | 434,261
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50960 | 450,961
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50961 | 450,962
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50962 | 450,963
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50963 | 450,964
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50964 | 450,965
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50965 | 450,966
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50966 | 450,967
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50967 | 450,968
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50968 | 450,969
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50969 | 450,970
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50970 | 450,971
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50971 | 450,972
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50972 | 450,973
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50973 | 450,974
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50974 | 450,975
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50975 | 450,976
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50976 | 450,977
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50977 | 450,978
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50978 | 450,979
61 | 22 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50979 | 450,980
61 | 23 | 1 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34266 | 434,267
61 | 23 | 2 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34268 | 434,269
61 | 23 | 3 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34270 | 434,271
61 | 23 | 4 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34272 | 434,273
61 | 23 | 5 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34274 | 434,275
61 | 23 | 6 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34276 | 434,277
61 | 23 | 7 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34278 | 434,279
61 | 23 | 8 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34280 | 434,281
61 | 23 | 9 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34282 | 434,283
61 | 23 | 10 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34284 | 434,285
61 | 23 | 11 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34286 | 434,287
61 | 23 | 12 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34288 | 434,289
61 | 23 | 13 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34290 | 434,291
61 | 23 | 15 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34294 | 434,295
61 | 23 | 18 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34300 | 434,301
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50980 | 450,981
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50981 | 450,982
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50982 | 450,983
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50983 | 450,984
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50984 | 450,985
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50985 | 450,986
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50986 | 450,987
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50987 | 450,988
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50988 | 450,989
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50989 | 450,990
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50990 | 450,991
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50991 | 450,992
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50992 | 450,993
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50993 | 450,994
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50994 | 450,995
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50995 | 450,996
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50996 | 450,997
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50997 | 450,998
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50998 | 450,999
61 | 23 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 50999 | 451,000
61 | 24 | 1 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34306 | 434,307
61 | 24 | 2 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34308 | 434,309
61 | 24 | 3 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34310 | 434,311
61 | 24 | 4 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34312 | 434,313
61 | 24 | 5 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34314 | 434,315
61 | 24 | 6 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34316 | 434,317
61 | 24 | 7 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34318 | 434,319
61 | 24 | 8 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34320 | 434,321
61 | 24 | 9 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34322 | 434,323
61 | 24 | 10 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34324 | 434,325
61 | 24 | 11 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34326 | 434,327
61 | 24 | 12 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34328 | 434,329
61 | 24 | 13 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34330 | 434,331
61 | 24 | 15 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34334 | 434,335
61 | 24 | 18 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34340 | 434,341
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51000 | 451,001
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51001 | 451,002
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51002 | 451,003
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51003 | 451,004
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51004 | 451,005
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51005 | 451,006
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51006 | 451,007
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51007 | 451,008
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51008 | 451,009
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51009 | 451,010
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51010 | 451,011
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51011 | 451,012
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51012 | 451,013
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51013 | 451,014
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51014 | 451,015
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51015 | 451,016
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51016 | 451,017
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51017 | 451,018
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51018 | 451,019
61 | 24 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51019 | 451,020
61 | 25 | 1 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34346 | 434,347
61 | 25 | 2 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34348 | 434,349
61 | 25 | 3 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34350 | 434,351
61 | 25 | 4 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34352 | 434,353
61 | 25 | 5 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34354 | 434,355
61 | 25 | 6 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34356 | 434,357
61 | 25 | 7 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34358 | 434,359
61 | 25 | 8 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34360 | 434,361
61 | 25 | 9 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34362 | 434,363
61 | 25 | 10 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34364 | 434,365
61 | 25 | 11 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34366 | 434,367
61 | 25 | 12 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34368 | 434,369
61 | 25 | 13 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34370 | 434,371
61 | 25 | 15 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34374 | 434,375
61 | 25 | 18 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34380 | 434,381
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51020 | 451,021
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51021 | 451,022
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51022 | 451,023
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51023 | 451,024
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51024 | 451,025
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51025 | 451,026
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51026 | 451,027
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51027 | 451,028
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51028 | 451,029
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51029 | 451,030
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51030 | 451,031
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51031 | 451,032
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51032 | 451,033
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51033 | 451,034
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51034 | 451,035
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51035 | 451,036
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51036 | 451,037
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51037 | 451,038
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51038 | 451,039
61 | 25 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51039 | 451,040
61 | 26 | 1 | Digital I/O | 3 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34386 | 434,387
61 | 26 | 2 | Digital I/O | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34388 | 434,389
61 | 26 | 3 | Digital I/O | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34390 | 434,391
61 | 26 | 4 | Digital I/O | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34392 | 434,393
61 | 26 | 5 | Digital I/O | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34394 | 434,395
61 | 26 | 6 | Digital I/O | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34396 | 434,397
61 | 26 | 7 | Digital I/O | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34398 | 434,399
61 | 26 | 8 | Digital I/O | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34400 | 434,401
61 | 26 | 9 | Digital I/O | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34402 | 434,403
61 | 26 | 10 | Digital I/O | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34404 | 434,405
61 | 26 | 11 | Digital I/O | 3 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34406 | 434,407
61 | 26 | 12 | Digital I/O | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34408 | 434,409
61 | 26 | 13 | Digital I/O | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34410 | 434,411
61 | 26 | 15 | Digital I/O | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34414 | 434,415
61 | 26 | 18 | Digital I/O | 3 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34420 | 434,421
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51040 | 451,041
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51041 | 451,042
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51042 | 451,043
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51043 | 451,044
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51044 | 451,045
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51045 | 451,046
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51046 | 451,047
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51047 | 451,048
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51048 | 451,049
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51049 | 451,050
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51050 | 451,051
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51051 | 451,052
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51052 | 451,053
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51053 | 451,054
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51054 | 451,055
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51055 | 451,056
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51056 | 451,057
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51057 | 451,058
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51058 | 451,059
61 | 26 | 19 | Digital I/O | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51059 | 451,060
61 | 31 | 1 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34426 | 434,427
61 | 31 | 2 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34428 | 434,429
61 | 31 | 3 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34430 | 434,431
61 | 31 | 4 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34432 | 434,433
61 | 31 | 5 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34434 | 434,435
61 | 31 | 6 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34436 | 434,437
61 | 31 | 7 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34438 | 434,439
61 | 31 | 8 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34440 | 434,441
61 | 31 | 9 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34442 | 434,443
61 | 31 | 10 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34444 | 434,445
61 | 31 | 11 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34446 | 434,447
61 | 31 | 12 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34448 | 434,449
61 | 31 | 13 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34450 | 434,451
61 | 31 | 15 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34454 | 434,455
61 | 31 | 18 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34460 | 434,461
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51060 | 451,061
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51061 | 451,062
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51062 | 451,063
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51063 | 451,064
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51064 | 451,065
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51065 | 451,066
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51066 | 451,067
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51067 | 451,068
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51068 | 451,069
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51069 | 451,070
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51070 | 451,071
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51071 | 451,072
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51072 | 451,073
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51073 | 451,074
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51074 | 451,075
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51075 | 451,076
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51076 | 451,077
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51077 | 451,078
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51078 | 451,079
61 | 31 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51079 | 451,080
61 | 32 | 1 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34466 | 434,467
61 | 32 | 2 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34468 | 434,469
61 | 32 | 3 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34470 | 434,471
61 | 32 | 4 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34472 | 434,473
61 | 32 | 5 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34474 | 434,475
61 | 32 | 6 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34476 | 434,477
61 | 32 | 7 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34478 | 434,479
61 | 32 | 8 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34480 | 434,481
61 | 32 | 9 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34482 | 434,483
61 | 32 | 10 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34484 | 434,485
61 | 32 | 11 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34486 | 434,487
61 | 32 | 12 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34488 | 434,489
61 | 32 | 13 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34490 | 434,491
61 | 32 | 15 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34494 | 434,495
61 | 32 | 18 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34500 | 434,501
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51080 | 451,081
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51081 | 451,082
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51082 | 451,083
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51083 | 451,084
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51084 | 451,085
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51085 | 451,086
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51086 | 451,087
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51087 | 451,088
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51088 | 451,089
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51089 | 451,090
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51090 | 451,091
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51091 | 451,092
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51092 | 451,093
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51093 | 451,094
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51094 | 451,095
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51095 | 451,096
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51096 | 451,097
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51097 | 451,098
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51098 | 451,099
61 | 32 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51099 | 451,100
61 | 33 | 1 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34506 | 434,507
61 | 33 | 2 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34508 | 434,509
61 | 33 | 3 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34510 | 434,511
61 | 33 | 4 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34512 | 434,513
61 | 33 | 5 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34514 | 434,515
61 | 33 | 6 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34516 | 434,517
61 | 33 | 7 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34518 | 434,519
61 | 33 | 8 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34520 | 434,521
61 | 33 | 9 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34522 | 434,523
61 | 33 | 10 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34524 | 434,525
61 | 33 | 11 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34526 | 434,527
61 | 33 | 12 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34528 | 434,529
61 | 33 | 13 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34530 | 434,531
61 | 33 | 15 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34534 | 434,535
61 | 33 | 18 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34540 | 434,541
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51100 | 451,101
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51101 | 451,102
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51102 | 451,103
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51103 | 451,104
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51104 | 451,105
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51105 | 451,106
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51106 | 451,107
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51107 | 451,108
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51108 | 451,109
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51109 | 451,110
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51110 | 451,111
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51111 | 451,112
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51112 | 451,113
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51113 | 451,114
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51114 | 451,115
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51115 | 451,116
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51116 | 451,117
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51117 | 451,118
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51118 | 451,119
61 | 33 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51119 | 451,120
61 | 34 | 1 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34546 | 434,547
61 | 34 | 2 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34548 | 434,549
61 | 34 | 3 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34550 | 434,551
61 | 34 | 4 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34552 | 434,553
61 | 34 | 5 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34554 | 434,555
61 | 34 | 6 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34556 | 434,557
61 | 34 | 7 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34558 | 434,559
61 | 34 | 8 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34560 | 434,561
61 | 34 | 9 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34562 | 434,563
61 | 34 | 10 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34564 | 434,565
61 | 34 | 11 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34566 | 434,567
61 | 34 | 12 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34568 | 434,569
61 | 34 | 13 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34570 | 434,571
61 | 34 | 15 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34574 | 434,575
61 | 34 | 18 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34580 | 434,581
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51120 | 451,121
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51121 | 451,122
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51122 | 451,123
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51123 | 451,124
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51124 | 451,125
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51125 | 451,126
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51126 | 451,127
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51127 | 451,128
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51128 | 451,129
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51129 | 451,130
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51130 | 451,131
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51131 | 451,132
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51132 | 451,133
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51133 | 451,134
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51134 | 451,135
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51135 | 451,136
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51136 | 451,137
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51137 | 451,138
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51138 | 451,139
61 | 34 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51139 | 451,140
61 | 35 | 1 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34586 | 434,587
61 | 35 | 2 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34588 | 434,589
61 | 35 | 3 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34590 | 434,591
61 | 35 | 4 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34592 | 434,593
61 | 35 | 5 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34594 | 434,595
61 | 35 | 6 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34596 | 434,597
61 | 35 | 7 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34598 | 434,599
61 | 35 | 8 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34600 | 434,601
61 | 35 | 9 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34602 | 434,603
61 | 35 | 10 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34604 | 434,605
61 | 35 | 11 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34606 | 434,607
61 | 35 | 12 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34608 | 434,609
61 | 35 | 13 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34610 | 434,611
61 | 35 | 15 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34614 | 434,615
61 | 35 | 18 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34620 | 434,621
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51140 | 451,141
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51141 | 451,142
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51142 | 451,143
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51143 | 451,144
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51144 | 451,145
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51145 | 451,146
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51146 | 451,147
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51147 | 451,148
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51148 | 451,149
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51149 | 451,150
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51150 | 451,151
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51151 | 451,152
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51152 | 451,153
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51153 | 451,154
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51154 | 451,155
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51155 | 451,156
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51156 | 451,157
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51157 | 451,158
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51158 | 451,159
61 | 35 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51159 | 451,160
61 | 36 | 1 | Digital I/O | 4 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34626 | 434,627
61 | 36 | 2 | Digital I/O | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34628 | 434,629
61 | 36 | 3 | Digital I/O | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34630 | 434,631
61 | 36 | 4 | Digital I/O | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34632 | 434,633
61 | 36 | 5 | Digital I/O | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34634 | 434,635
61 | 36 | 6 | Digital I/O | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34636 | 434,637
61 | 36 | 7 | Digital I/O | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34638 | 434,639
61 | 36 | 8 | Digital I/O | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34640 | 434,641
61 | 36 | 9 | Digital I/O | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34642 | 434,643
61 | 36 | 10 | Digital I/O | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34644 | 434,645
61 | 36 | 11 | Digital I/O | 4 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34646 | 434,647
61 | 36 | 12 | Digital I/O | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34648 | 434,649
61 | 36 | 13 | Digital I/O | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34650 | 434,651
61 | 36 | 15 | Digital I/O | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34654 | 434,655
61 | 36 | 18 | Digital I/O | 4 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34660 | 434,661
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51160 | 451,161
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51161 | 451,162
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51162 | 451,163
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51163 | 451,164
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51164 | 451,165
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51165 | 451,166
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51166 | 451,167
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51167 | 451,168
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51168 | 451,169
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51169 | 451,170
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51170 | 451,171
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51171 | 451,172
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51172 | 451,173
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51173 | 451,174
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51174 | 451,175
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51175 | 451,176
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51176 | 451,177
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51177 | 451,178
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51178 | 451,179
61 | 36 | 19 | Digital I/O | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51179 | 451,180
61 | 41 | 1 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34666 | 434,667
61 | 41 | 2 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34668 | 434,669
61 | 41 | 3 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34670 | 434,671
61 | 41 | 4 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34672 | 434,673
61 | 41 | 5 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34674 | 434,675
61 | 41 | 6 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34676 | 434,677
61 | 41 | 7 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34678 | 434,679
61 | 41 | 8 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34680 | 434,681
61 | 41 | 9 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34682 | 434,683
61 | 41 | 10 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34684 | 434,685
61 | 41 | 11 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34686 | 434,687
61 | 41 | 12 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34688 | 434,689
61 | 41 | 13 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34690 | 434,691
61 | 41 | 15 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34694 | 434,695
61 | 41 | 18 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34700 | 434,701
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51180 | 451,181
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51181 | 451,182
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51182 | 451,183
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51183 | 451,184
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51184 | 451,185
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51185 | 451,186
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51186 | 451,187
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51187 | 451,188
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51188 | 451,189
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51189 | 451,190
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51190 | 451,191
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51191 | 451,192
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51192 | 451,193
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51193 | 451,194
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51194 | 451,195
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51195 | 451,196
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51196 | 451,197
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51197 | 451,198
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51198 | 451,199
61 | 41 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51199 | 451,200
61 | 42 | 1 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34706 | 434,707
61 | 42 | 2 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34708 | 434,709
61 | 42 | 3 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34710 | 434,711
61 | 42 | 4 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34712 | 434,713
61 | 42 | 5 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34714 | 434,715
61 | 42 | 6 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34716 | 434,717
61 | 42 | 7 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34718 | 434,719
61 | 42 | 8 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34720 | 434,721
61 | 42 | 9 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34722 | 434,723
61 | 42 | 10 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34724 | 434,725
61 | 42 | 11 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34726 | 434,727
61 | 42 | 12 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34728 | 434,729
61 | 42 | 13 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34730 | 434,731
61 | 42 | 15 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34734 | 434,735
61 | 42 | 18 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34740 | 434,741
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51200 | 451,201
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51201 | 451,202
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51202 | 451,203
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51203 | 451,204
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51204 | 451,205
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51205 | 451,206
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51206 | 451,207
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51207 | 451,208
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51208 | 451,209
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51209 | 451,210
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51210 | 451,211
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51211 | 451,212
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51212 | 451,213
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51213 | 451,214
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51214 | 451,215
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51215 | 451,216
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51216 | 451,217
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51217 | 451,218
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51218 | 451,219
61 | 42 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51219 | 451,220
61 | 43 | 1 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34746 | 434,747
61 | 43 | 2 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34748 | 434,749
61 | 43 | 3 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34750 | 434,751
61 | 43 | 4 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34752 | 434,753
61 | 43 | 5 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34754 | 434,755
61 | 43 | 6 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34756 | 434,757
61 | 43 | 7 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34758 | 434,759
61 | 43 | 8 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34760 | 434,761
61 | 43 | 9 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34762 | 434,763
61 | 43 | 10 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34764 | 434,765
61 | 43 | 11 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34766 | 434,767
61 | 43 | 12 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34768 | 434,769
61 | 43 | 13 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34770 | 434,771
61 | 43 | 15 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34774 | 434,775
61 | 43 | 18 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34780 | 434,781
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51220 | 451,221
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51221 | 451,222
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51222 | 451,223
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51223 | 451,224
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51224 | 451,225
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51225 | 451,226
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51226 | 451,227
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51227 | 451,228
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51228 | 451,229
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51229 | 451,230
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51230 | 451,231
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51231 | 451,232
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51232 | 451,233
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51233 | 451,234
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51234 | 451,235
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51235 | 451,236
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51236 | 451,237
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51237 | 451,238
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51238 | 451,239
61 | 43 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51239 | 451,240
61 | 44 | 1 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34786 | 434,787
61 | 44 | 2 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34788 | 434,789
61 | 44 | 3 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34790 | 434,791
61 | 44 | 4 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34792 | 434,793
61 | 44 | 5 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34794 | 434,795
61 | 44 | 6 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34796 | 434,797
61 | 44 | 7 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34798 | 434,799
61 | 44 | 8 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34800 | 434,801
61 | 44 | 9 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34802 | 434,803
61 | 44 | 10 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34804 | 434,805
61 | 44 | 11 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34806 | 434,807
61 | 44 | 12 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34808 | 434,809
61 | 44 | 13 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34810 | 434,811
61 | 44 | 15 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34814 | 434,815
61 | 44 | 18 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34820 | 434,821
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51240 | 451,241
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51241 | 451,242
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51242 | 451,243
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51243 | 451,244
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51244 | 451,245
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51245 | 451,246
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51246 | 451,247
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51247 | 451,248
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51248 | 451,249
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51249 | 451,250
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51250 | 451,251
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51251 | 451,252
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51252 | 451,253
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51253 | 451,254
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51254 | 451,255
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51255 | 451,256
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51256 | 451,257
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51257 | 451,258
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51258 | 451,259
61 | 44 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51259 | 451,260
61 | 45 | 1 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34826 | 434,827
61 | 45 | 2 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34828 | 434,829
61 | 45 | 3 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34830 | 434,831
61 | 45 | 4 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34832 | 434,833
61 | 45 | 5 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34834 | 434,835
61 | 45 | 6 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34836 | 434,837
61 | 45 | 7 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34838 | 434,839
61 | 45 | 8 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34840 | 434,841
61 | 45 | 9 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34842 | 434,843
61 | 45 | 10 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34844 | 434,845
61 | 45 | 11 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34846 | 434,847
61 | 45 | 12 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34848 | 434,849
61 | 45 | 13 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34850 | 434,851
61 | 45 | 15 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34854 | 434,855
61 | 45 | 18 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34860 | 434,861
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51260 | 451,261
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51261 | 451,262
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51262 | 451,263
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51263 | 451,264
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51264 | 451,265
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51265 | 451,266
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51266 | 451,267
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51267 | 451,268
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51268 | 451,269
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51269 | 451,270
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51270 | 451,271
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51271 | 451,272
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51272 | 451,273
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51273 | 451,274
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51274 | 451,275
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51275 | 451,276
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51276 | 451,277
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51277 | 451,278
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51278 | 451,279
61 | 45 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51279 | 451,280
61 | 46 | 1 | Digital I/O | 5 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34866 | 434,867
61 | 46 | 2 | Digital I/O | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34868 | 434,869
61 | 46 | 3 | Digital I/O | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34870 | 434,871
61 | 46 | 4 | Digital I/O | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34872 | 434,873
61 | 46 | 5 | Digital I/O | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34874 | 434,875
61 | 46 | 6 | Digital I/O | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34876 | 434,877
61 | 46 | 7 | Digital I/O | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34878 | 434,879
61 | 46 | 8 | Digital I/O | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34880 | 434,881
61 | 46 | 9 | Digital I/O | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34882 | 434,883
61 | 46 | 10 | Digital I/O | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34884 | 434,885
61 | 46 | 11 | Digital I/O | 5 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34886 | 434,887
61 | 46 | 12 | Digital I/O | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34888 | 434,889
61 | 46 | 13 | Digital I/O | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34890 | 434,891
61 | 46 | 15 | Digital I/O | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34894 | 434,895
61 | 46 | 18 | Digital I/O | 5 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34900 | 434,901
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51280 | 451,281
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51281 | 451,282
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51282 | 451,283
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51283 | 451,284
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51284 | 451,285
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51285 | 451,286
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51286 | 451,287
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51287 | 451,288
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51288 | 451,289
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51289 | 451,290
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51290 | 451,291
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51291 | 451,292
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51292 | 451,293
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51293 | 451,294
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51294 | 451,295
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51295 | 451,296
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51296 | 451,297
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51297 | 451,298
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51298 | 451,299
61 | 46 | 19 | Digital I/O | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51299 | 451,300
61 | 51 | 1 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34906 | 434,907
61 | 51 | 2 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34908 | 434,909
61 | 51 | 3 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34910 | 434,911
61 | 51 | 4 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34912 | 434,913
61 | 51 | 5 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34914 | 434,915
61 | 51 | 6 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34916 | 434,917
61 | 51 | 7 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34918 | 434,919
61 | 51 | 8 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34920 | 434,921
61 | 51 | 9 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34922 | 434,923
61 | 51 | 10 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34924 | 434,925
61 | 51 | 11 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34926 | 434,927
61 | 51 | 12 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34928 | 434,929
61 | 51 | 13 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34930 | 434,931
61 | 51 | 15 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34934 | 434,935
61 | 51 | 18 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34940 | 434,941
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51300 | 451,301
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51301 | 451,302
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51302 | 451,303
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51303 | 451,304
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51304 | 451,305
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51305 | 451,306
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51306 | 451,307
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51307 | 451,308
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51308 | 451,309
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51309 | 451,310
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51310 | 451,311
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51311 | 451,312
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51312 | 451,313
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51313 | 451,314
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51314 | 451,315
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51315 | 451,316
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51316 | 451,317
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51317 | 451,318
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51318 | 451,319
61 | 51 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51319 | 451,320
61 | 52 | 1 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34946 | 434,947
61 | 52 | 2 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34948 | 434,949
61 | 52 | 3 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34950 | 434,951
61 | 52 | 4 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34952 | 434,953
61 | 52 | 5 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34954 | 434,955
61 | 52 | 6 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34956 | 434,957
61 | 52 | 7 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34958 | 434,959
61 | 52 | 8 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 34960 | 434,961
61 | 52 | 9 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 34962 | 434,963
61 | 52 | 10 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 34964 | 434,965
61 | 52 | 11 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 34966 | 434,967
61 | 52 | 12 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 34968 | 434,969
61 | 52 | 13 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 34970 | 434,971
61 | 52 | 15 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 34974 | 434,975
61 | 52 | 18 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 34980 | 434,981
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51320 | 451,321
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51321 | 451,322
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51322 | 451,323
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51323 | 451,324
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51324 | 451,325
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51325 | 451,326
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51326 | 451,327
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51327 | 451,328
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51328 | 451,329
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51329 | 451,330
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51330 | 451,331
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51331 | 451,332
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51332 | 451,333
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51333 | 451,334
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51334 | 451,335
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51335 | 451,336
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51336 | 451,337
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51337 | 451,338
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51338 | 451,339
61 | 52 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51339 | 451,340
61 | 53 | 1 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 34986 | 434,987
61 | 53 | 2 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 34988 | 434,989
61 | 53 | 3 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 34990 | 434,991
61 | 53 | 4 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 34992 | 434,993
61 | 53 | 5 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 34994 | 434,995
61 | 53 | 6 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 34996 | 434,997
61 | 53 | 7 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 34998 | 434,999
61 | 53 | 8 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35000 | 435,001
61 | 53 | 9 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35002 | 435,003
61 | 53 | 10 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35004 | 435,005
61 | 53 | 11 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 35006 | 435,007
61 | 53 | 12 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35008 | 435,009
61 | 53 | 13 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35010 | 435,011
61 | 53 | 15 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35014 | 435,015
61 | 53 | 18 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 35020 | 435,021
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51340 | 451,341
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51341 | 451,342
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51342 | 451,343
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51343 | 451,344
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51344 | 451,345
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51345 | 451,346
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51346 | 451,347
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51347 | 451,348
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51348 | 451,349
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51349 | 451,350
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51350 | 451,351
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51351 | 451,352
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51352 | 451,353
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51353 | 451,354
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51354 | 451,355
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51355 | 451,356
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51356 | 451,357
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51357 | 451,358
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51358 | 451,359
61 | 53 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51359 | 451,360
61 | 54 | 1 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 35026 | 435,027
61 | 54 | 2 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35028 | 435,029
61 | 54 | 3 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35030 | 435,031
61 | 54 | 4 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35032 | 435,033
61 | 54 | 5 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35034 | 435,035
61 | 54 | 6 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35036 | 435,037
61 | 54 | 7 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35038 | 435,039
61 | 54 | 8 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35040 | 435,041
61 | 54 | 9 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35042 | 435,043
61 | 54 | 10 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35044 | 435,045
61 | 54 | 11 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 35046 | 435,047
61 | 54 | 12 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35048 | 435,049
61 | 54 | 13 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35050 | 435,051
61 | 54 | 15 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35054 | 435,055
61 | 54 | 18 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 35060 | 435,061
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51360 | 451,361
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51361 | 451,362
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51362 | 451,363
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51363 | 451,364
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51364 | 451,365
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51365 | 451,366
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51366 | 451,367
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51367 | 451,368
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51368 | 451,369
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51369 | 451,370
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51370 | 451,371
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51371 | 451,372
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51372 | 451,373
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51373 | 451,374
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51374 | 451,375
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51375 | 451,376
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51376 | 451,377
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51377 | 451,378
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51378 | 451,379
61 | 54 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51379 | 451,380
61 | 55 | 1 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 35066 | 435,067
61 | 55 | 2 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35068 | 435,069
61 | 55 | 3 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35070 | 435,071
61 | 55 | 4 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35072 | 435,073
61 | 55 | 5 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35074 | 435,075
61 | 55 | 6 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35076 | 435,077
61 | 55 | 7 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35078 | 435,079
61 | 55 | 8 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35080 | 435,081
61 | 55 | 9 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35082 | 435,083
61 | 55 | 10 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35084 | 435,085
61 | 55 | 11 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 35086 | 435,087
61 | 55 | 12 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35088 | 435,089
61 | 55 | 13 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35090 | 435,091
61 | 55 | 15 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35094 | 435,095
61 | 55 | 18 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 35100 | 435,101
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51380 | 451,381
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51381 | 451,382
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51382 | 451,383
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51383 | 451,384
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51384 | 451,385
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51385 | 451,386
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51386 | 451,387
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51387 | 451,388
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51388 | 451,389
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51389 | 451,390
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51390 | 451,391
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51391 | 451,392
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51392 | 451,393
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51393 | 451,394
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51394 | 451,395
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51395 | 451,396
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51396 | 451,397
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51397 | 451,398
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51398 | 451,399
61 | 55 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51399 | 451,400
61 | 56 | 1 | Digital I/O | 6 | Direction | Set this function to operate as an input or output. | Output (68), Input Voltage (193), Input Dry Contact (44) | Output (68) | Enumeration | R/W | 35106 | 435,107
61 | 56 | 2 | Digital I/O | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35108 | 435,109
61 | 56 | 3 | Digital I/O | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35110 | 435,111
61 | 56 | 4 | Digital I/O | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35112 | 435,113
61 | 56 | 5 | Digital I/O | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35114 | 435,115
61 | 56 | 6 | Digital I/O | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35116 | 435,117
61 | 56 | 7 | Digital I/O | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35118 | 435,119
61 | 56 | 8 | Digital I/O | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35120 | 435,121
61 | 56 | 9 | Digital I/O | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35122 | 435,123
61 | 56 | 10 | Digital I/O | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35124 | 435,125
61 | 56 | 11 | Digital I/O | 6 | Input State | Monitor the input state when direction is input. | On (63), Off (62) |  | Enumeration | R | 35126 | 435,127
61 | 56 | 12 | Digital I/O | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35128 | 435,129
61 | 56 | 13 | Digital I/O | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35130 | 435,131
61 | 56 | 15 | Digital I/O | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35134 | 435,135
61 | 56 | 18 | Digital I/O | 6 | Error | Monitor the output source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 35140 | 435,141
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51400 | 451,401
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51401 | 451,402
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51402 | 451,403
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51403 | 451,404
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51404 | 451,405
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51405 | 451,406
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51406 | 451,407
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51407 | 451,408
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51408 | 451,409
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51409 | 451,410
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51410 | 451,411
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51411 | 451,412
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51412 | 451,413
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51413 | 451,414
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51414 | 451,415
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51415 | 451,416
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51416 | 451,417
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51417 | 451,418
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51418 | 451,419
61 | 56 | 19 | Digital I/O | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51419 | 451,420
62 | 1 | 2 | Digital Output Fast | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35148 | 435,149
62 | 1 | 3 | Digital Output Fast | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35150 | 435,151
62 | 1 | 4 | Digital Output Fast | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35152 | 435,153
62 | 1 | 5 | Digital Output Fast | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35154 | 435,155
62 | 1 | 6 | Digital Output Fast | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35156 | 435,157
62 | 1 | 7 | Digital Output Fast | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35158 | 435,159
62 | 1 | 8 | Digital Output Fast | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35160 | 435,161
62 | 1 | 9 | Digital Output Fast | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35162 | 435,163
62 | 1 | 10 | Digital Output Fast | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35164 | 435,165
62 | 1 | 12 | Digital Output Fast | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35168 | 435,169
62 | 1 | 13 | Digital Output Fast | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35170 | 435,171
62 | 1 | 15 | Digital Output Fast | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35174 | 435,175
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51420 | 451,421
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51421 | 451,422
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51422 | 451,423
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51423 | 451,424
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51424 | 451,425
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51425 | 451,426
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51426 | 451,427
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51427 | 451,428
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51428 | 451,429
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51429 | 451,430
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51430 | 451,431
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51431 | 451,432
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51432 | 451,433
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51433 | 451,434
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51434 | 451,435
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51435 | 451,436
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51436 | 451,437
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51437 | 451,438
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51438 | 451,439
62 | 1 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51439 | 451,440
62 | 1 | 20 | Digital Output Fast | 1 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35184 | 435,185
62 | 2 | 2 | Digital Output Fast | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35188 | 435,189
62 | 2 | 3 | Digital Output Fast | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35190 | 435,191
62 | 2 | 4 | Digital Output Fast | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35192 | 435,193
62 | 2 | 5 | Digital Output Fast | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35194 | 435,195
62 | 2 | 6 | Digital Output Fast | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35196 | 435,197
62 | 2 | 7 | Digital Output Fast | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35198 | 435,199
62 | 2 | 8 | Digital Output Fast | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35200 | 435,201
62 | 2 | 9 | Digital Output Fast | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35202 | 435,203
62 | 2 | 10 | Digital Output Fast | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35204 | 435,205
62 | 2 | 12 | Digital Output Fast | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35208 | 435,209
62 | 2 | 13 | Digital Output Fast | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35210 | 435,211
62 | 2 | 15 | Digital Output Fast | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35214 | 435,215
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51440 | 451,441
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51441 | 451,442
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51442 | 451,443
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51443 | 451,444
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51444 | 451,445
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51445 | 451,446
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51446 | 451,447
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51447 | 451,448
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51448 | 451,449
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51449 | 451,450
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51450 | 451,451
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51451 | 451,452
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51452 | 451,453
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51453 | 451,454
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51454 | 451,455
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51455 | 451,456
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51456 | 451,457
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51457 | 451,458
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51458 | 451,459
62 | 2 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51459 | 451,460
62 | 2 | 20 | Digital Output Fast | 1 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35224 | 435,225
62 | 3 | 2 | Digital Output Fast | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35228 | 435,229
62 | 3 | 3 | Digital Output Fast | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35230 | 435,231
62 | 3 | 4 | Digital Output Fast | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35232 | 435,233
62 | 3 | 5 | Digital Output Fast | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35234 | 435,235
62 | 3 | 6 | Digital Output Fast | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35236 | 435,237
62 | 3 | 7 | Digital Output Fast | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35238 | 435,239
62 | 3 | 8 | Digital Output Fast | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35240 | 435,241
62 | 3 | 9 | Digital Output Fast | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35242 | 435,243
62 | 3 | 10 | Digital Output Fast | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35244 | 435,245
62 | 3 | 12 | Digital Output Fast | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35248 | 435,249
62 | 3 | 13 | Digital Output Fast | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35250 | 435,251
62 | 3 | 15 | Digital Output Fast | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35254 | 435,255
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51460 | 451,461
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51461 | 451,462
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51462 | 451,463
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51463 | 451,464
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51464 | 451,465
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51465 | 451,466
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51466 | 451,467
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51467 | 451,468
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51468 | 451,469
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51469 | 451,470
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51470 | 451,471
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51471 | 451,472
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51472 | 451,473
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51473 | 451,474
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51474 | 451,475
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51475 | 451,476
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51476 | 451,477
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51477 | 451,478
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51478 | 451,479
62 | 3 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51479 | 451,480
62 | 3 | 20 | Digital Output Fast | 1 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35264 | 435,265
62 | 4 | 2 | Digital Output Fast | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35268 | 435,269
62 | 4 | 3 | Digital Output Fast | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35270 | 435,271
62 | 4 | 4 | Digital Output Fast | 1 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35272 | 435,273
62 | 4 | 5 | Digital Output Fast | 1 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35274 | 435,275
62 | 4 | 6 | Digital Output Fast | 1 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35276 | 435,277
62 | 4 | 7 | Digital Output Fast | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35278 | 435,279
62 | 4 | 8 | Digital Output Fast | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35280 | 435,281
62 | 4 | 9 | Digital Output Fast | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35282 | 435,283
62 | 4 | 10 | Digital Output Fast | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35284 | 435,285
62 | 4 | 12 | Digital Output Fast | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35288 | 435,289
62 | 4 | 13 | Digital Output Fast | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35290 | 435,291
62 | 4 | 15 | Digital Output Fast | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35294 | 435,295
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51480 | 451,481
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51481 | 451,482
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51482 | 451,483
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51483 | 451,484
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51484 | 451,485
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51485 | 451,486
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51486 | 451,487
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51487 | 451,488
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51488 | 451,489
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51489 | 451,490
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51490 | 451,491
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51491 | 451,492
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51492 | 451,493
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51493 | 451,494
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51494 | 451,495
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51495 | 451,496
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51496 | 451,497
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51497 | 451,498
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51498 | 451,499
62 | 4 | 19 | Digital Output Fast | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51499 | 451,500
62 | 4 | 20 | Digital Output Fast | 1 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35304 | 435,305
62 | 11 | 2 | Digital Output Fast | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35308 | 435,309
62 | 11 | 3 | Digital Output Fast | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35310 | 435,311
62 | 11 | 4 | Digital Output Fast | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35312 | 435,313
62 | 11 | 5 | Digital Output Fast | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35314 | 435,315
62 | 11 | 6 | Digital Output Fast | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35316 | 435,317
62 | 11 | 7 | Digital Output Fast | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35318 | 435,319
62 | 11 | 8 | Digital Output Fast | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35320 | 435,321
62 | 11 | 9 | Digital Output Fast | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35322 | 435,323
62 | 11 | 10 | Digital Output Fast | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35324 | 435,325
62 | 11 | 12 | Digital Output Fast | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35328 | 435,329
62 | 11 | 13 | Digital Output Fast | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35330 | 435,331
62 | 11 | 15 | Digital Output Fast | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35334 | 435,335
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51500 | 451,501
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51501 | 451,502
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51502 | 451,503
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51503 | 451,504
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51504 | 451,505
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51505 | 451,506
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51506 | 451,507
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51507 | 451,508
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51508 | 451,509
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51509 | 451,510
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51510 | 451,511
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51511 | 451,512
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51512 | 451,513
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51513 | 451,514
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51514 | 451,515
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51515 | 451,516
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51516 | 451,517
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51517 | 451,518
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51518 | 451,519
62 | 11 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51519 | 451,520
62 | 11 | 20 | Digital Output Fast | 2 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35344 | 435,345
62 | 12 | 2 | Digital Output Fast | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35348 | 435,349
62 | 12 | 3 | Digital Output Fast | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35350 | 435,351
62 | 12 | 4 | Digital Output Fast | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35352 | 435,353
62 | 12 | 5 | Digital Output Fast | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35354 | 435,355
62 | 12 | 6 | Digital Output Fast | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35356 | 435,357
62 | 12 | 7 | Digital Output Fast | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35358 | 435,359
62 | 12 | 8 | Digital Output Fast | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35360 | 435,361
62 | 12 | 9 | Digital Output Fast | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35362 | 435,363
62 | 12 | 10 | Digital Output Fast | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35364 | 435,365
62 | 12 | 12 | Digital Output Fast | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35368 | 435,369
62 | 12 | 13 | Digital Output Fast | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35370 | 435,371
62 | 12 | 15 | Digital Output Fast | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35374 | 435,375
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51520 | 451,521
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51521 | 451,522
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51522 | 451,523
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51523 | 451,524
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51524 | 451,525
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51525 | 451,526
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51526 | 451,527
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51527 | 451,528
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51528 | 451,529
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51529 | 451,530
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51530 | 451,531
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51531 | 451,532
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51532 | 451,533
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51533 | 451,534
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51534 | 451,535
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51535 | 451,536
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51536 | 451,537
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51537 | 451,538
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51538 | 451,539
62 | 12 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51539 | 451,540
62 | 12 | 20 | Digital Output Fast | 2 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35384 | 435,385
62 | 13 | 2 | Digital Output Fast | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35388 | 435,389
62 | 13 | 3 | Digital Output Fast | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35390 | 435,391
62 | 13 | 4 | Digital Output Fast | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35392 | 435,393
62 | 13 | 5 | Digital Output Fast | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35394 | 435,395
62 | 13 | 6 | Digital Output Fast | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35396 | 435,397
62 | 13 | 7 | Digital Output Fast | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35398 | 435,399
62 | 13 | 8 | Digital Output Fast | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35400 | 435,401
62 | 13 | 9 | Digital Output Fast | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35402 | 435,403
62 | 13 | 10 | Digital Output Fast | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35404 | 435,405
62 | 13 | 12 | Digital Output Fast | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35408 | 435,409
62 | 13 | 13 | Digital Output Fast | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35410 | 435,411
62 | 13 | 15 | Digital Output Fast | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35414 | 435,415
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51540 | 451,541
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51541 | 451,542
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51542 | 451,543
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51543 | 451,544
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51544 | 451,545
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51545 | 451,546
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51546 | 451,547
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51547 | 451,548
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51548 | 451,549
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51549 | 451,550
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51550 | 451,551
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51551 | 451,552
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51552 | 451,553
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51553 | 451,554
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51554 | 451,555
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51555 | 451,556
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51556 | 451,557
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51557 | 451,558
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51558 | 451,559
62 | 13 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51559 | 451,560
62 | 13 | 20 | Digital Output Fast | 2 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35424 | 435,425
62 | 14 | 2 | Digital Output Fast | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35428 | 435,429
62 | 14 | 3 | Digital Output Fast | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35430 | 435,431
62 | 14 | 4 | Digital Output Fast | 2 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35432 | 435,433
62 | 14 | 5 | Digital Output Fast | 2 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35434 | 435,435
62 | 14 | 6 | Digital Output Fast | 2 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35436 | 435,437
62 | 14 | 7 | Digital Output Fast | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35438 | 435,439
62 | 14 | 8 | Digital Output Fast | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35440 | 435,441
62 | 14 | 9 | Digital Output Fast | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35442 | 435,443
62 | 14 | 10 | Digital Output Fast | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35444 | 435,445
62 | 14 | 12 | Digital Output Fast | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35448 | 435,449
62 | 14 | 13 | Digital Output Fast | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35450 | 435,451
62 | 14 | 15 | Digital Output Fast | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35454 | 435,455
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51560 | 451,561
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51561 | 451,562
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51562 | 451,563
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51563 | 451,564
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51564 | 451,565
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51565 | 451,566
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51566 | 451,567
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51567 | 451,568
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51568 | 451,569
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51569 | 451,570
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51570 | 451,571
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51571 | 451,572
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51572 | 451,573
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51573 | 451,574
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51574 | 451,575
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51575 | 451,576
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51576 | 451,577
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51577 | 451,578
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51578 | 451,579
62 | 14 | 19 | Digital Output Fast | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51579 | 451,580
62 | 14 | 20 | Digital Output Fast | 2 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35464 | 435,465
62 | 21 | 2 | Digital Output Fast | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35468 | 435,469
62 | 21 | 3 | Digital Output Fast | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35470 | 435,471
62 | 21 | 4 | Digital Output Fast | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35472 | 435,473
62 | 21 | 5 | Digital Output Fast | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35474 | 435,475
62 | 21 | 6 | Digital Output Fast | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35476 | 435,477
62 | 21 | 7 | Digital Output Fast | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35478 | 435,479
62 | 21 | 8 | Digital Output Fast | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35480 | 435,481
62 | 21 | 9 | Digital Output Fast | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35482 | 435,483
62 | 21 | 10 | Digital Output Fast | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35484 | 435,485
62 | 21 | 12 | Digital Output Fast | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35488 | 435,489
62 | 21 | 13 | Digital Output Fast | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35490 | 435,491
62 | 21 | 15 | Digital Output Fast | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35494 | 435,495
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51580 | 451,581
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51581 | 451,582
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51582 | 451,583
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51583 | 451,584
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51584 | 451,585
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51585 | 451,586
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51586 | 451,587
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51587 | 451,588
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51588 | 451,589
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51589 | 451,590
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51590 | 451,591
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51591 | 451,592
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51592 | 451,593
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51593 | 451,594
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51594 | 451,595
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51595 | 451,596
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51596 | 451,597
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51597 | 451,598
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51598 | 451,599
62 | 21 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51599 | 451,600
62 | 21 | 20 | Digital Output Fast | 3 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35504 | 435,505
62 | 22 | 2 | Digital Output Fast | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35508 | 435,509
62 | 22 | 3 | Digital Output Fast | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35510 | 435,511
62 | 22 | 4 | Digital Output Fast | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35512 | 435,513
62 | 22 | 5 | Digital Output Fast | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35514 | 435,515
62 | 22 | 6 | Digital Output Fast | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35516 | 435,517
62 | 22 | 7 | Digital Output Fast | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35518 | 435,519
62 | 22 | 8 | Digital Output Fast | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35520 | 435,521
62 | 22 | 9 | Digital Output Fast | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35522 | 435,523
62 | 22 | 10 | Digital Output Fast | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35524 | 435,525
62 | 22 | 12 | Digital Output Fast | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35528 | 435,529
62 | 22 | 13 | Digital Output Fast | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35530 | 435,531
62 | 22 | 15 | Digital Output Fast | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35534 | 435,535
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51600 | 451,601
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51601 | 451,602
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51602 | 451,603
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51603 | 451,604
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51604 | 451,605
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51605 | 451,606
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51606 | 451,607
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51607 | 451,608
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51608 | 451,609
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51609 | 451,610
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51610 | 451,611
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51611 | 451,612
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51612 | 451,613
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51613 | 451,614
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51614 | 451,615
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51615 | 451,616
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51616 | 451,617
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51617 | 451,618
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51618 | 451,619
62 | 22 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51619 | 451,620
62 | 22 | 20 | Digital Output Fast | 3 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35544 | 435,545
62 | 23 | 2 | Digital Output Fast | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35548 | 435,549
62 | 23 | 3 | Digital Output Fast | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35550 | 435,551
62 | 23 | 4 | Digital Output Fast | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35552 | 435,553
62 | 23 | 5 | Digital Output Fast | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35554 | 435,555
62 | 23 | 6 | Digital Output Fast | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35556 | 435,557
62 | 23 | 7 | Digital Output Fast | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35558 | 435,559
62 | 23 | 8 | Digital Output Fast | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35560 | 435,561
62 | 23 | 9 | Digital Output Fast | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35562 | 435,563
62 | 23 | 10 | Digital Output Fast | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35564 | 435,565
62 | 23 | 12 | Digital Output Fast | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35568 | 435,569
62 | 23 | 13 | Digital Output Fast | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35570 | 435,571
62 | 23 | 15 | Digital Output Fast | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35574 | 435,575
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51620 | 451,621
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51621 | 451,622
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51622 | 451,623
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51623 | 451,624
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51624 | 451,625
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51625 | 451,626
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51626 | 451,627
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51627 | 451,628
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51628 | 451,629
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51629 | 451,630
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51630 | 451,631
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51631 | 451,632
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51632 | 451,633
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51633 | 451,634
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51634 | 451,635
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51635 | 451,636
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51636 | 451,637
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51637 | 451,638
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51638 | 451,639
62 | 23 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51639 | 451,640
62 | 23 | 20 | Digital Output Fast | 3 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35584 | 435,585
62 | 24 | 2 | Digital Output Fast | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35588 | 435,589
62 | 24 | 3 | Digital Output Fast | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35590 | 435,591
62 | 24 | 4 | Digital Output Fast | 3 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35592 | 435,593
62 | 24 | 5 | Digital Output Fast | 3 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35594 | 435,595
62 | 24 | 6 | Digital Output Fast | 3 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35596 | 435,597
62 | 24 | 7 | Digital Output Fast | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35598 | 435,599
62 | 24 | 8 | Digital Output Fast | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35600 | 435,601
62 | 24 | 9 | Digital Output Fast | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35602 | 435,603
62 | 24 | 10 | Digital Output Fast | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35604 | 435,605
62 | 24 | 12 | Digital Output Fast | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35608 | 435,609
62 | 24 | 13 | Digital Output Fast | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35610 | 435,611
62 | 24 | 15 | Digital Output Fast | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35614 | 435,615
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51640 | 451,641
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51641 | 451,642
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51642 | 451,643
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51643 | 451,644
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51644 | 451,645
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51645 | 451,646
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51646 | 451,647
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51647 | 451,648
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51648 | 451,649
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51649 | 451,650
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51650 | 451,651
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51651 | 451,652
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51652 | 451,653
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51653 | 451,654
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51654 | 451,655
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51655 | 451,656
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51656 | 451,657
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51657 | 451,658
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51658 | 451,659
62 | 24 | 19 | Digital Output Fast | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51659 | 451,660
62 | 24 | 20 | Digital Output Fast | 3 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35624 | 435,625
62 | 31 | 2 | Digital Output Fast | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35628 | 435,629
62 | 31 | 3 | Digital Output Fast | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35630 | 435,631
62 | 31 | 4 | Digital Output Fast | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35632 | 435,633
62 | 31 | 5 | Digital Output Fast | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35634 | 435,635
62 | 31 | 6 | Digital Output Fast | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35636 | 435,637
62 | 31 | 7 | Digital Output Fast | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35638 | 435,639
62 | 31 | 8 | Digital Output Fast | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35640 | 435,641
62 | 31 | 9 | Digital Output Fast | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35642 | 435,643
62 | 31 | 10 | Digital Output Fast | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35644 | 435,645
62 | 31 | 12 | Digital Output Fast | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35648 | 435,649
62 | 31 | 13 | Digital Output Fast | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35650 | 435,651
62 | 31 | 15 | Digital Output Fast | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35654 | 435,655
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51660 | 451,661
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51661 | 451,662
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51662 | 451,663
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51663 | 451,664
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51664 | 451,665
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51665 | 451,666
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51666 | 451,667
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51667 | 451,668
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51668 | 451,669
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51669 | 451,670
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51670 | 451,671
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51671 | 451,672
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51672 | 451,673
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51673 | 451,674
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51674 | 451,675
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51675 | 451,676
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51676 | 451,677
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51677 | 451,678
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51678 | 451,679
62 | 31 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51679 | 451,680
62 | 31 | 20 | Digital Output Fast | 4 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35664 | 435,665
62 | 32 | 2 | Digital Output Fast | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35668 | 435,669
62 | 32 | 3 | Digital Output Fast | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35670 | 435,671
62 | 32 | 4 | Digital Output Fast | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35672 | 435,673
62 | 32 | 5 | Digital Output Fast | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35674 | 435,675
62 | 32 | 6 | Digital Output Fast | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35676 | 435,677
62 | 32 | 7 | Digital Output Fast | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35678 | 435,679
62 | 32 | 8 | Digital Output Fast | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35680 | 435,681
62 | 32 | 9 | Digital Output Fast | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35682 | 435,683
62 | 32 | 10 | Digital Output Fast | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35684 | 435,685
62 | 32 | 12 | Digital Output Fast | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35688 | 435,689
62 | 32 | 13 | Digital Output Fast | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35690 | 435,691
62 | 32 | 15 | Digital Output Fast | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35694 | 435,695
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51680 | 451,681
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51681 | 451,682
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51682 | 451,683
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51683 | 451,684
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51684 | 451,685
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51685 | 451,686
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51686 | 451,687
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51687 | 451,688
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51688 | 451,689
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51689 | 451,690
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51690 | 451,691
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51691 | 451,692
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51692 | 451,693
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51693 | 451,694
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51694 | 451,695
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51695 | 451,696
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51696 | 451,697
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51697 | 451,698
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51698 | 451,699
62 | 32 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51699 | 451,700
62 | 32 | 20 | Digital Output Fast | 4 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35704 | 435,705
62 | 33 | 2 | Digital Output Fast | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35708 | 435,709
62 | 33 | 3 | Digital Output Fast | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35710 | 435,711
62 | 33 | 4 | Digital Output Fast | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35712 | 435,713
62 | 33 | 5 | Digital Output Fast | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35714 | 435,715
62 | 33 | 6 | Digital Output Fast | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35716 | 435,717
62 | 33 | 7 | Digital Output Fast | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35718 | 435,719
62 | 33 | 8 | Digital Output Fast | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35720 | 435,721
62 | 33 | 9 | Digital Output Fast | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35722 | 435,723
62 | 33 | 10 | Digital Output Fast | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35724 | 435,725
62 | 33 | 12 | Digital Output Fast | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35728 | 435,729
62 | 33 | 13 | Digital Output Fast | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35730 | 435,731
62 | 33 | 15 | Digital Output Fast | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35734 | 435,735
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51700 | 451,701
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51701 | 451,702
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51702 | 451,703
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51703 | 451,704
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51704 | 451,705
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51705 | 451,706
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51706 | 451,707
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51707 | 451,708
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51708 | 451,709
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51709 | 451,710
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51710 | 451,711
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51711 | 451,712
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51712 | 451,713
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51713 | 451,714
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51714 | 451,715
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51715 | 451,716
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51716 | 451,717
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51717 | 451,718
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51718 | 451,719
62 | 33 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51719 | 451,720
62 | 33 | 20 | Digital Output Fast | 4 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35744 | 435,745
62 | 34 | 2 | Digital Output Fast | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35748 | 435,749
62 | 34 | 3 | Digital Output Fast | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35750 | 435,751
62 | 34 | 4 | Digital Output Fast | 4 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35752 | 435,753
62 | 34 | 5 | Digital Output Fast | 4 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35754 | 435,755
62 | 34 | 6 | Digital Output Fast | 4 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35756 | 435,757
62 | 34 | 7 | Digital Output Fast | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35758 | 435,759
62 | 34 | 8 | Digital Output Fast | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35760 | 435,761
62 | 34 | 9 | Digital Output Fast | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35762 | 435,763
62 | 34 | 10 | Digital Output Fast | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35764 | 435,765
62 | 34 | 12 | Digital Output Fast | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35768 | 435,769
62 | 34 | 13 | Digital Output Fast | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35770 | 435,771
62 | 34 | 15 | Digital Output Fast | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35774 | 435,775
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51720 | 451,721
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51721 | 451,722
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51722 | 451,723
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51723 | 451,724
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51724 | 451,725
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51725 | 451,726
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51726 | 451,727
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51727 | 451,728
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51728 | 451,729
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51729 | 451,730
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51730 | 451,731
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51731 | 451,732
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51732 | 451,733
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51733 | 451,734
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51734 | 451,735
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51735 | 451,736
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51736 | 451,737
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51737 | 451,738
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51738 | 451,739
62 | 34 | 19 | Digital Output Fast | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51739 | 451,740
62 | 34 | 20 | Digital Output Fast | 4 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35784 | 435,785
62 | 41 | 2 | Digital Output Fast | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35788 | 435,789
62 | 41 | 3 | Digital Output Fast | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35790 | 435,791
62 | 41 | 4 | Digital Output Fast | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35792 | 435,793
62 | 41 | 5 | Digital Output Fast | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35794 | 435,795
62 | 41 | 6 | Digital Output Fast | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35796 | 435,797
62 | 41 | 7 | Digital Output Fast | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35798 | 435,799
62 | 41 | 8 | Digital Output Fast | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35800 | 435,801
62 | 41 | 9 | Digital Output Fast | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35802 | 435,803
62 | 41 | 10 | Digital Output Fast | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35804 | 435,805
62 | 41 | 12 | Digital Output Fast | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35808 | 435,809
62 | 41 | 13 | Digital Output Fast | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35810 | 435,811
62 | 41 | 15 | Digital Output Fast | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35814 | 435,815
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51740 | 451,741
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51741 | 451,742
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51742 | 451,743
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51743 | 451,744
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51744 | 451,745
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51745 | 451,746
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51746 | 451,747
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51747 | 451,748
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51748 | 451,749
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51749 | 451,750
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51750 | 451,751
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51751 | 451,752
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51752 | 451,753
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51753 | 451,754
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51754 | 451,755
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51755 | 451,756
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51756 | 451,757
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51757 | 451,758
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51758 | 451,759
62 | 41 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51759 | 451,760
62 | 41 | 20 | Digital Output Fast | 5 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35824 | 435,825
62 | 42 | 2 | Digital Output Fast | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35828 | 435,829
62 | 42 | 3 | Digital Output Fast | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35830 | 435,831
62 | 42 | 4 | Digital Output Fast | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35832 | 435,833
62 | 42 | 5 | Digital Output Fast | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35834 | 435,835
62 | 42 | 6 | Digital Output Fast | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35836 | 435,837
62 | 42 | 7 | Digital Output Fast | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35838 | 435,839
62 | 42 | 8 | Digital Output Fast | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35840 | 435,841
62 | 42 | 9 | Digital Output Fast | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35842 | 435,843
62 | 42 | 10 | Digital Output Fast | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35844 | 435,845
62 | 42 | 12 | Digital Output Fast | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35848 | 435,849
62 | 42 | 13 | Digital Output Fast | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35850 | 435,851
62 | 42 | 15 | Digital Output Fast | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35854 | 435,855
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51760 | 451,761
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51761 | 451,762
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51762 | 451,763
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51763 | 451,764
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51764 | 451,765
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51765 | 451,766
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51766 | 451,767
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51767 | 451,768
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51768 | 451,769
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51769 | 451,770
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51770 | 451,771
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51771 | 451,772
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51772 | 451,773
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51773 | 451,774
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51774 | 451,775
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51775 | 451,776
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51776 | 451,777
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51777 | 451,778
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51778 | 451,779
62 | 42 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51779 | 451,780
62 | 42 | 20 | Digital Output Fast | 5 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35864 | 435,865
62 | 43 | 2 | Digital Output Fast | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35868 | 435,869
62 | 43 | 3 | Digital Output Fast | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35870 | 435,871
62 | 43 | 4 | Digital Output Fast | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35872 | 435,873
62 | 43 | 5 | Digital Output Fast | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35874 | 435,875
62 | 43 | 6 | Digital Output Fast | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35876 | 435,877
62 | 43 | 7 | Digital Output Fast | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35878 | 435,879
62 | 43 | 8 | Digital Output Fast | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35880 | 435,881
62 | 43 | 9 | Digital Output Fast | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35882 | 435,883
62 | 43 | 10 | Digital Output Fast | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35884 | 435,885
62 | 43 | 12 | Digital Output Fast | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35888 | 435,889
62 | 43 | 13 | Digital Output Fast | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35890 | 435,891
62 | 43 | 15 | Digital Output Fast | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35894 | 435,895
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51780 | 451,781
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51781 | 451,782
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51782 | 451,783
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51783 | 451,784
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51784 | 451,785
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51785 | 451,786
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51786 | 451,787
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51787 | 451,788
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51788 | 451,789
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51789 | 451,790
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51790 | 451,791
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51791 | 451,792
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51792 | 451,793
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51793 | 451,794
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51794 | 451,795
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51795 | 451,796
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51796 | 451,797
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51797 | 451,798
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51798 | 451,799
62 | 43 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51799 | 451,800
62 | 43 | 20 | Digital Output Fast | 5 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35904 | 435,905
62 | 44 | 2 | Digital Output Fast | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35908 | 435,909
62 | 44 | 3 | Digital Output Fast | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35910 | 435,911
62 | 44 | 4 | Digital Output Fast | 5 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35912 | 435,913
62 | 44 | 5 | Digital Output Fast | 5 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35914 | 435,915
62 | 44 | 6 | Digital Output Fast | 5 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35916 | 435,917
62 | 44 | 7 | Digital Output Fast | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35918 | 435,919
62 | 44 | 8 | Digital Output Fast | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35920 | 435,921
62 | 44 | 9 | Digital Output Fast | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35922 | 435,923
62 | 44 | 10 | Digital Output Fast | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35924 | 435,925
62 | 44 | 12 | Digital Output Fast | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35928 | 435,929
62 | 44 | 13 | Digital Output Fast | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35930 | 435,931
62 | 44 | 15 | Digital Output Fast | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35934 | 435,935
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51800 | 451,801
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51801 | 451,802
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51802 | 451,803
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51803 | 451,804
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51804 | 451,805
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51805 | 451,806
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51806 | 451,807
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51807 | 451,808
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51808 | 451,809
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51809 | 451,810
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51810 | 451,811
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51811 | 451,812
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51812 | 451,813
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51813 | 451,814
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51814 | 451,815
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51815 | 451,816
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51816 | 451,817
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51817 | 451,818
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51818 | 451,819
62 | 44 | 19 | Digital Output Fast | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51819 | 451,820
62 | 44 | 20 | Digital Output Fast | 5 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35944 | 435,945
62 | 51 | 2 | Digital Output Fast | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35948 | 435,949
62 | 51 | 3 | Digital Output Fast | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35950 | 435,951
62 | 51 | 4 | Digital Output Fast | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35952 | 435,953
62 | 51 | 5 | Digital Output Fast | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35954 | 435,955
62 | 51 | 6 | Digital Output Fast | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35956 | 435,957
62 | 51 | 7 | Digital Output Fast | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35958 | 435,959
62 | 51 | 8 | Digital Output Fast | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 35960 | 435,961
62 | 51 | 9 | Digital Output Fast | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 35962 | 435,963
62 | 51 | 10 | Digital Output Fast | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 35964 | 435,965
62 | 51 | 12 | Digital Output Fast | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 35968 | 435,969
62 | 51 | 13 | Digital Output Fast | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 35970 | 435,971
62 | 51 | 15 | Digital Output Fast | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 35974 | 435,975
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51820 | 451,821
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51821 | 451,822
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51822 | 451,823
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51823 | 451,824
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51824 | 451,825
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51825 | 451,826
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51826 | 451,827
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51827 | 451,828
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51828 | 451,829
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51829 | 451,830
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51830 | 451,831
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51831 | 451,832
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51832 | 451,833
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51833 | 451,834
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51834 | 451,835
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51835 | 451,836
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51836 | 451,837
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51837 | 451,838
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51838 | 451,839
62 | 51 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51839 | 451,840
62 | 51 | 20 | Digital Output Fast | 6 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 35984 | 435,985
62 | 52 | 2 | Digital Output Fast | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 35988 | 435,989
62 | 52 | 3 | Digital Output Fast | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 35990 | 435,991
62 | 52 | 4 | Digital Output Fast | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 35992 | 435,993
62 | 52 | 5 | Digital Output Fast | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 35994 | 435,995
62 | 52 | 6 | Digital Output Fast | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 35996 | 435,997
62 | 52 | 7 | Digital Output Fast | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 35998 | 435,999
62 | 52 | 8 | Digital Output Fast | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 36000 | 436,001
62 | 52 | 9 | Digital Output Fast | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 36002 | 436,003
62 | 52 | 10 | Digital Output Fast | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 36004 | 436,005
62 | 52 | 12 | Digital Output Fast | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 36008 | 436,009
62 | 52 | 13 | Digital Output Fast | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36010 | 436,011
62 | 52 | 15 | Digital Output Fast | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36014 | 436,015
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51840 | 451,841
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51841 | 451,842
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51842 | 451,843
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51843 | 451,844
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51844 | 451,845
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51845 | 451,846
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51846 | 451,847
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51847 | 451,848
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51848 | 451,849
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51849 | 451,850
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51850 | 451,851
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51851 | 451,852
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51852 | 451,853
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51853 | 451,854
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51854 | 451,855
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51855 | 451,856
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51856 | 451,857
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51857 | 451,858
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51858 | 451,859
62 | 52 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51859 | 451,860
62 | 52 | 20 | Digital Output Fast | 6 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 36024 | 436,025
62 | 53 | 2 | Digital Output Fast | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 36028 | 436,029
62 | 53 | 3 | Digital Output Fast | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 36030 | 436,031
62 | 53 | 4 | Digital Output Fast | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 36032 | 436,033
62 | 53 | 5 | Digital Output Fast | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 36034 | 436,035
62 | 53 | 6 | Digital Output Fast | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 36036 | 436,037
62 | 53 | 7 | Digital Output Fast | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36038 | 436,039
62 | 53 | 8 | Digital Output Fast | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 36040 | 436,041
62 | 53 | 9 | Digital Output Fast | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 36042 | 436,043
62 | 53 | 10 | Digital Output Fast | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 36044 | 436,045
62 | 53 | 12 | Digital Output Fast | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 36048 | 436,049
62 | 53 | 13 | Digital Output Fast | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36050 | 436,051
62 | 53 | 15 | Digital Output Fast | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36054 | 436,055
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51860 | 451,861
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51861 | 451,862
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51862 | 451,863
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51863 | 451,864
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51864 | 451,865
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51865 | 451,866
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51866 | 451,867
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51867 | 451,868
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51868 | 451,869
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51869 | 451,870
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51870 | 451,871
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51871 | 451,872
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51872 | 451,873
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51873 | 451,874
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51874 | 451,875
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51875 | 451,876
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51876 | 451,877
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51877 | 451,878
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51878 | 451,879
62 | 53 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51879 | 451,880
62 | 53 | 20 | Digital Output Fast | 6 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 36064 | 436,065
62 | 54 | 2 | Digital Output Fast | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34), Variable Time Base (103) | Fixed Time Base (34) | Enumeration | R/W | 36068 | 436,069
62 | 54 | 3 | Digital Output Fast | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 0.1 to 60.0 | 1.0 | IEEE Float | R/W | 36070 | 436,071
62 | 54 | 4 | Digital Output Fast | 6 | AC Line Frequency | Set line frequency applied to control. Setting of any in DIO applies to all DIO. | 50 Hz (3), 60 Hz (4) |  | Enumeration | R/W | 36072 | 436,073
62 | 54 | 5 | Digital Output Fast | 6 | Function | Set what function will drive this output when direction is output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 36074 | 436,075
62 | 54 | 6 | Digital Output Fast | 6 | Output Function Instance | Set the instance of the function which will drive this output when direction is output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 36076 | 436,077
62 | 54 | 7 | Digital Output Fast | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36078 | 436,079
62 | 54 | 8 | Digital Output Fast | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 36080 | 436,081
62 | 54 | 9 | Digital Output Fast | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 36082 | 436,083
62 | 54 | 10 | Digital Output Fast | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 36084 | 436,085
62 | 54 | 12 | Digital Output Fast | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 36088 | 436,089
62 | 54 | 13 | Digital Output Fast | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36090 | 436,091
62 | 54 | 15 | Digital Output Fast | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36094 | 436,095
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51880 | 451,881
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51881 | 451,882
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51882 | 451,883
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51883 | 451,884
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51884 | 451,885
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51885 | 451,886
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51886 | 451,887
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51887 | 451,888
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51888 | 451,889
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51889 | 451,890
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51890 | 451,891
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51891 | 451,892
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51892 | 451,893
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51893 | 451,894
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51894 | 451,895
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51895 | 451,896
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51896 | 451,897
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51897 | 451,898
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51898 | 451,899
62 | 54 | 19 | Digital Output Fast | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51899 | 451,900
62 | 54 | 20 | Digital Output Fast | 6 | Output Type | Monitor the hardware type of this output. | SSR (10034), SSR w/ Shared Common (10035), Switched DC (10033), Switched DC / Open Collector (10032) |  | Enumeration | R | 36104 | 436,105
63 | 1 | 5 | Digital Output Limit | 1 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 36114 | 436,115
63 | 1 | 6 | Digital Output Limit | 1 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 36116 | 436,117
63 | 1 | 7 | Digital Output Limit | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36118 | 436,119
63 | 1 | 12 | Digital Output Limit | 1 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 36128 | 436,129
63 | 1 | 13 | Digital Output Limit | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36130 | 436,131
63 | 1 | 15 | Digital Output Limit | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36134 | 436,135
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51900 | 451,901
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51901 | 451,902
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51902 | 451,903
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51903 | 451,904
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51904 | 451,905
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51905 | 451,906
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51906 | 451,907
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51907 | 451,908
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51908 | 451,909
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51909 | 451,910
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51910 | 451,911
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51911 | 451,912
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51912 | 451,913
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51913 | 451,914
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51914 | 451,915
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51915 | 451,916
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51916 | 451,917
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51917 | 451,918
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51918 | 451,919
63 | 1 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51919 | 451,920
63 | 1 | 20 | Digital Output Limit | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 36144 | 436,145
63 | 2 | 5 | Digital Output Limit | 1 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 36154 | 436,155
63 | 2 | 6 | Digital Output Limit | 1 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 36156 | 436,157
63 | 2 | 7 | Digital Output Limit | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36158 | 436,159
63 | 2 | 12 | Digital Output Limit | 1 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 36168 | 436,169
63 | 2 | 13 | Digital Output Limit | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36170 | 436,171
63 | 2 | 15 | Digital Output Limit | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36174 | 436,175
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51920 | 451,921
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51921 | 451,922
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51922 | 451,923
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51923 | 451,924
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51924 | 451,925
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51925 | 451,926
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51926 | 451,927
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51927 | 451,928
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51928 | 451,929
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51929 | 451,930
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51930 | 451,931
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51931 | 451,932
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51932 | 451,933
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51933 | 451,934
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51934 | 451,935
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51935 | 451,936
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51936 | 451,937
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51937 | 451,938
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51938 | 451,939
63 | 2 | 19 | Digital Output Limit | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51939 | 451,940
63 | 2 | 20 | Digital Output Limit | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 36184 | 436,185
63 | 11 | 5 | Digital Output Limit | 2 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 36194 | 436,195
63 | 11 | 6 | Digital Output Limit | 2 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 36196 | 436,197
63 | 11 | 7 | Digital Output Limit | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36198 | 436,199
63 | 11 | 12 | Digital Output Limit | 2 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 36208 | 436,209
63 | 11 | 13 | Digital Output Limit | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36210 | 436,211
63 | 11 | 15 | Digital Output Limit | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36214 | 436,215
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51940 | 451,941
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51941 | 451,942
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51942 | 451,943
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51943 | 451,944
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51944 | 451,945
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51945 | 451,946
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51946 | 451,947
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51947 | 451,948
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51948 | 451,949
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51949 | 451,950
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51950 | 451,951
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51951 | 451,952
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51952 | 451,953
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51953 | 451,954
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51954 | 451,955
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51955 | 451,956
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51956 | 451,957
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51957 | 451,958
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51958 | 451,959
63 | 11 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51959 | 451,960
63 | 11 | 20 | Digital Output Limit | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 36224 | 436,225
63 | 12 | 5 | Digital Output Limit | 2 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 36234 | 436,235
63 | 12 | 6 | Digital Output Limit | 2 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 36236 | 436,237
63 | 12 | 7 | Digital Output Limit | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36238 | 436,239
63 | 12 | 12 | Digital Output Limit | 2 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 36248 | 436,249
63 | 12 | 13 | Digital Output Limit | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36250 | 436,251
63 | 12 | 15 | Digital Output Limit | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36254 | 436,255
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51960 | 451,961
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51961 | 451,962
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51962 | 451,963
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51963 | 451,964
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51964 | 451,965
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51965 | 451,966
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51966 | 451,967
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51967 | 451,968
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51968 | 451,969
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51969 | 451,970
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51970 | 451,971
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51971 | 451,972
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51972 | 451,973
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51973 | 451,974
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51974 | 451,975
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51975 | 451,976
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51976 | 451,977
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51977 | 451,978
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51978 | 451,979
63 | 12 | 19 | Digital Output Limit | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51979 | 451,980
63 | 12 | 20 | Digital Output Limit | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 36264 | 436,265
63 | 21 | 5 | Digital Output Limit | 3 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 36274 | 436,275
63 | 21 | 6 | Digital Output Limit | 3 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 36276 | 436,277
63 | 21 | 7 | Digital Output Limit | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36278 | 436,279
63 | 21 | 12 | Digital Output Limit | 3 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 36288 | 436,289
63 | 21 | 13 | Digital Output Limit | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36290 | 436,291
63 | 21 | 15 | Digital Output Limit | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36294 | 436,295
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51980 | 451,981
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51981 | 451,982
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51982 | 451,983
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51983 | 451,984
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51984 | 451,985
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51985 | 451,986
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51986 | 451,987
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51987 | 451,988
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51988 | 451,989
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51989 | 451,990
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51990 | 451,991
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51991 | 451,992
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51992 | 451,993
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51993 | 451,994
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51994 | 451,995
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51995 | 451,996
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51996 | 451,997
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51997 | 451,998
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51998 | 451,999
63 | 21 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 51999 | 452,000
63 | 21 | 20 | Digital Output Limit | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 36304 | 436,305
63 | 22 | 5 | Digital Output Limit | 3 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 36314 | 436,315
63 | 22 | 6 | Digital Output Limit | 3 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 36316 | 436,317
63 | 22 | 7 | Digital Output Limit | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36318 | 436,319
63 | 22 | 12 | Digital Output Limit | 3 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 36328 | 436,329
63 | 22 | 13 | Digital Output Limit | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36330 | 436,331
63 | 22 | 15 | Digital Output Limit | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36334 | 436,335
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52000 | 452,001
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52001 | 452,002
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52002 | 452,003
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52003 | 452,004
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52004 | 452,005
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52005 | 452,006
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52006 | 452,007
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52007 | 452,008
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52008 | 452,009
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52009 | 452,010
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52010 | 452,011
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52011 | 452,012
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52012 | 452,013
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52013 | 452,014
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52014 | 452,015
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52015 | 452,016
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52016 | 452,017
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52017 | 452,018
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52018 | 452,019
63 | 22 | 19 | Digital Output Limit | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52019 | 452,020
63 | 22 | 20 | Digital Output Limit | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 36344 | 436,345
63 | 31 | 5 | Digital Output Limit | 4 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 36354 | 436,355
63 | 31 | 6 | Digital Output Limit | 4 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 36356 | 436,357
63 | 31 | 7 | Digital Output Limit | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36358 | 436,359
63 | 31 | 12 | Digital Output Limit | 4 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 36368 | 436,369
63 | 31 | 13 | Digital Output Limit | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36370 | 436,371
63 | 31 | 15 | Digital Output Limit | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36374 | 436,375
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52020 | 452,021
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52021 | 452,022
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52022 | 452,023
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52023 | 452,024
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52024 | 452,025
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52025 | 452,026
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52026 | 452,027
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52027 | 452,028
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52028 | 452,029
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52029 | 452,030
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52030 | 452,031
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52031 | 452,032
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52032 | 452,033
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52033 | 452,034
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52034 | 452,035
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52035 | 452,036
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52036 | 452,037
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52037 | 452,038
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52038 | 452,039
63 | 31 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52039 | 452,040
63 | 31 | 20 | Digital Output Limit | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 36384 | 436,385
63 | 32 | 5 | Digital Output Limit | 4 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 36394 | 436,395
63 | 32 | 6 | Digital Output Limit | 4 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 36396 | 436,397
63 | 32 | 7 | Digital Output Limit | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36398 | 436,399
63 | 32 | 12 | Digital Output Limit | 4 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 36408 | 436,409
63 | 32 | 13 | Digital Output Limit | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36410 | 436,411
63 | 32 | 15 | Digital Output Limit | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36414 | 436,415
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52040 | 452,041
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52041 | 452,042
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52042 | 452,043
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52043 | 452,044
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52044 | 452,045
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52045 | 452,046
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52046 | 452,047
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52047 | 452,048
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52048 | 452,049
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52049 | 452,050
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52050 | 452,051
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52051 | 452,052
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52052 | 452,053
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52053 | 452,054
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52054 | 452,055
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52055 | 452,056
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52056 | 452,057
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52057 | 452,058
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52058 | 452,059
63 | 32 | 19 | Digital Output Limit | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52059 | 452,060
63 | 32 | 20 | Digital Output Limit | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 36424 | 436,425
63 | 41 | 5 | Digital Output Limit | 5 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 36434 | 436,435
63 | 41 | 6 | Digital Output Limit | 5 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 36436 | 436,437
63 | 41 | 7 | Digital Output Limit | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36438 | 436,439
63 | 41 | 12 | Digital Output Limit | 5 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 36448 | 436,449
63 | 41 | 13 | Digital Output Limit | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36450 | 436,451
63 | 41 | 15 | Digital Output Limit | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36454 | 436,455
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52060 | 452,061
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52061 | 452,062
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52062 | 452,063
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52063 | 452,064
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52064 | 452,065
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52065 | 452,066
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52066 | 452,067
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52067 | 452,068
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52068 | 452,069
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52069 | 452,070
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52070 | 452,071
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52071 | 452,072
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52072 | 452,073
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52073 | 452,074
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52074 | 452,075
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52075 | 452,076
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52076 | 452,077
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52077 | 452,078
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52078 | 452,079
63 | 41 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52079 | 452,080
63 | 41 | 20 | Digital Output Limit | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 36464 | 436,465
63 | 42 | 5 | Digital Output Limit | 5 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 36474 | 436,475
63 | 42 | 6 | Digital Output Limit | 5 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 36476 | 436,477
63 | 42 | 7 | Digital Output Limit | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36478 | 436,479
63 | 42 | 12 | Digital Output Limit | 5 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 36488 | 436,489
63 | 42 | 13 | Digital Output Limit | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36490 | 436,491
63 | 42 | 15 | Digital Output Limit | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36494 | 436,495
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52080 | 452,081
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52081 | 452,082
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52082 | 452,083
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52083 | 452,084
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52084 | 452,085
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52085 | 452,086
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52086 | 452,087
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52087 | 452,088
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52088 | 452,089
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52089 | 452,090
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52090 | 452,091
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52091 | 452,092
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52092 | 452,093
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52093 | 452,094
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52094 | 452,095
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52095 | 452,096
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52096 | 452,097
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52097 | 452,098
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52098 | 452,099
63 | 42 | 19 | Digital Output Limit | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52099 | 452,100
63 | 42 | 20 | Digital Output Limit | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 36504 | 436,505
63 | 51 | 5 | Digital Output Limit | 6 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 36514 | 436,515
63 | 51 | 6 | Digital Output Limit | 6 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 36516 | 436,517
63 | 51 | 7 | Digital Output Limit | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36518 | 436,519
63 | 51 | 12 | Digital Output Limit | 6 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 36528 | 436,529
63 | 51 | 13 | Digital Output Limit | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36530 | 436,531
63 | 51 | 15 | Digital Output Limit | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36534 | 436,535
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52100 | 452,101
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52101 | 452,102
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52102 | 452,103
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52103 | 452,104
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52104 | 452,105
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52105 | 452,106
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52106 | 452,107
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52107 | 452,108
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52108 | 452,109
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52109 | 452,110
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52110 | 452,111
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52111 | 452,112
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52112 | 452,113
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52113 | 452,114
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52114 | 452,115
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52115 | 452,116
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52116 | 452,117
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52117 | 452,118
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52118 | 452,119
63 | 51 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52119 | 452,120
63 | 51 | 20 | Digital Output Limit | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 36544 | 436,545
63 | 52 | 5 | Digital Output Limit | 6 | Function | Set the function. | Limit (126) | Limit (126) | Enumeration | R/W | 36554 | 436,555
63 | 52 | 6 | Digital Output Limit | 6 | Output Function Instance | Set the instance of the function that will drive this output. | 1 to 250 |  | Unsigned 8-bit | R/W | 36556 | 436,557
63 | 52 | 7 | Digital Output Limit | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36558 | 436,559
63 | 52 | 12 | Digital Output Limit | 6 | Output Source Zone | Set the zone of the function that will drive this output. | 0 to 0 | 0 | Unsigned 8-bit | R/W | 36568 | 436,569
63 | 52 | 13 | Digital Output Limit | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36570 | 436,571
63 | 52 | 15 | Digital Output Limit | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36574 | 436,575
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52120 | 452,121
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52121 | 452,122
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52122 | 452,123
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52123 | 452,124
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52124 | 452,125
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52125 | 452,126
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52126 | 452,127
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52127 | 452,128
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52128 | 452,129
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52129 | 452,130
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52130 | 452,131
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52131 | 452,132
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52132 | 452,133
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52133 | 452,134
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52134 | 452,135
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52135 | 452,136
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52136 | 452,137
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52137 | 452,138
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52138 | 452,139
63 | 52 | 19 | Digital Output Limit | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52139 | 452,140
63 | 52 | 20 | Digital Output Limit | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form C Mechanical Relay (10028) |  | Enumeration | R | 36584 | 436,585
64 | 1 | 2 | Digital Output Slow | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 36588 | 436,589
64 | 1 | 3 | Digital Output Slow | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 36590 | 436,591
64 | 1 | 5 | Digital Output Slow | 1 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 36594 | 436,595
64 | 1 | 6 | Digital Output Slow | 1 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 36596 | 436,597
64 | 1 | 7 | Digital Output Slow | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36598 | 436,599
64 | 1 | 8 | Digital Output Slow | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 36600 | 436,601
64 | 1 | 9 | Digital Output Slow | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 36602 | 436,603
64 | 1 | 10 | Digital Output Slow | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 36604 | 436,605
64 | 1 | 12 | Digital Output Slow | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 36608 | 436,609
64 | 1 | 13 | Digital Output Slow | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36610 | 436,611
64 | 1 | 15 | Digital Output Slow | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36614 | 436,615
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52140 | 452,141
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52141 | 452,142
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52142 | 452,143
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52143 | 452,144
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52144 | 452,145
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52145 | 452,146
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52146 | 452,147
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52147 | 452,148
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52148 | 452,149
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52149 | 452,150
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52150 | 452,151
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52151 | 452,152
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52152 | 452,153
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52153 | 452,154
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52154 | 452,155
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52155 | 452,156
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52156 | 452,157
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52157 | 452,158
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52158 | 452,159
64 | 1 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52159 | 452,160
64 | 1 | 20 | Digital Output Slow | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 36624 | 436,625
64 | 2 | 2 | Digital Output Slow | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 36628 | 436,629
64 | 2 | 3 | Digital Output Slow | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 36630 | 436,631
64 | 2 | 5 | Digital Output Slow | 1 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 36634 | 436,635
64 | 2 | 6 | Digital Output Slow | 1 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 36636 | 436,637
64 | 2 | 7 | Digital Output Slow | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36638 | 436,639
64 | 2 | 8 | Digital Output Slow | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 36640 | 436,641
64 | 2 | 9 | Digital Output Slow | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 36642 | 436,643
64 | 2 | 10 | Digital Output Slow | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 36644 | 436,645
64 | 2 | 12 | Digital Output Slow | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 36648 | 436,649
64 | 2 | 13 | Digital Output Slow | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36650 | 436,651
64 | 2 | 15 | Digital Output Slow | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36654 | 436,655
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52160 | 452,161
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52161 | 452,162
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52162 | 452,163
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52163 | 452,164
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52164 | 452,165
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52165 | 452,166
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52166 | 452,167
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52167 | 452,168
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52168 | 452,169
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52169 | 452,170
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52170 | 452,171
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52171 | 452,172
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52172 | 452,173
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52173 | 452,174
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52174 | 452,175
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52175 | 452,176
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52176 | 452,177
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52177 | 452,178
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52178 | 452,179
64 | 2 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52179 | 452,180
64 | 2 | 20 | Digital Output Slow | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 36664 | 436,665
64 | 3 | 2 | Digital Output Slow | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 36668 | 436,669
64 | 3 | 3 | Digital Output Slow | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 36670 | 436,671
64 | 3 | 5 | Digital Output Slow | 1 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 36674 | 436,675
64 | 3 | 6 | Digital Output Slow | 1 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 36676 | 436,677
64 | 3 | 7 | Digital Output Slow | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36678 | 436,679
64 | 3 | 8 | Digital Output Slow | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 36680 | 436,681
64 | 3 | 9 | Digital Output Slow | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 36682 | 436,683
64 | 3 | 10 | Digital Output Slow | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 36684 | 436,685
64 | 3 | 12 | Digital Output Slow | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 36688 | 436,689
64 | 3 | 13 | Digital Output Slow | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36690 | 436,691
64 | 3 | 15 | Digital Output Slow | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36694 | 436,695
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52180 | 452,181
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52181 | 452,182
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52182 | 452,183
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52183 | 452,184
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52184 | 452,185
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52185 | 452,186
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52186 | 452,187
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52187 | 452,188
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52188 | 452,189
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52189 | 452,190
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52190 | 452,191
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52191 | 452,192
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52192 | 452,193
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52193 | 452,194
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52194 | 452,195
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52195 | 452,196
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52196 | 452,197
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52197 | 452,198
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52198 | 452,199
64 | 3 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52199 | 452,200
64 | 3 | 20 | Digital Output Slow | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 36704 | 436,705
64 | 4 | 2 | Digital Output Slow | 1 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 36708 | 436,709
64 | 4 | 3 | Digital Output Slow | 1 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 36710 | 436,711
64 | 4 | 5 | Digital Output Slow | 1 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 36714 | 436,715
64 | 4 | 6 | Digital Output Slow | 1 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 36716 | 436,717
64 | 4 | 7 | Digital Output Slow | 1 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36718 | 436,719
64 | 4 | 8 | Digital Output Slow | 1 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 36720 | 436,721
64 | 4 | 9 | Digital Output Slow | 1 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 36722 | 436,723
64 | 4 | 10 | Digital Output Slow | 1 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 36724 | 436,725
64 | 4 | 12 | Digital Output Slow | 1 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 36728 | 436,729
64 | 4 | 13 | Digital Output Slow | 1 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36730 | 436,731
64 | 4 | 15 | Digital Output Slow | 1 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36734 | 436,735
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52200 | 452,201
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52201 | 452,202
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52202 | 452,203
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52203 | 452,204
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52204 | 452,205
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52205 | 452,206
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52206 | 452,207
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52207 | 452,208
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52208 | 452,209
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52209 | 452,210
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52210 | 452,211
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52211 | 452,212
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52212 | 452,213
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52213 | 452,214
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52214 | 452,215
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52215 | 452,216
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52216 | 452,217
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52217 | 452,218
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52218 | 452,219
64 | 4 | 19 | Digital Output Slow | 1 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52219 | 452,220
64 | 4 | 20 | Digital Output Slow | 1 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 36744 | 436,745
64 | 11 | 2 | Digital Output Slow | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 36748 | 436,749
64 | 11 | 3 | Digital Output Slow | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 36750 | 436,751
64 | 11 | 5 | Digital Output Slow | 2 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 36754 | 436,755
64 | 11 | 6 | Digital Output Slow | 2 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 36756 | 436,757
64 | 11 | 7 | Digital Output Slow | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36758 | 436,759
64 | 11 | 8 | Digital Output Slow | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 36760 | 436,761
64 | 11 | 9 | Digital Output Slow | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 36762 | 436,763
64 | 11 | 10 | Digital Output Slow | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 36764 | 436,765
64 | 11 | 12 | Digital Output Slow | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 36768 | 436,769
64 | 11 | 13 | Digital Output Slow | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36770 | 436,771
64 | 11 | 15 | Digital Output Slow | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36774 | 436,775
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52220 | 452,221
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52221 | 452,222
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52222 | 452,223
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52223 | 452,224
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52224 | 452,225
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52225 | 452,226
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52226 | 452,227
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52227 | 452,228
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52228 | 452,229
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52229 | 452,230
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52230 | 452,231
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52231 | 452,232
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52232 | 452,233
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52233 | 452,234
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52234 | 452,235
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52235 | 452,236
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52236 | 452,237
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52237 | 452,238
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52238 | 452,239
64 | 11 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52239 | 452,240
64 | 11 | 20 | Digital Output Slow | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 36784 | 436,785
64 | 12 | 2 | Digital Output Slow | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 36788 | 436,789
64 | 12 | 3 | Digital Output Slow | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 36790 | 436,791
64 | 12 | 5 | Digital Output Slow | 2 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 36794 | 436,795
64 | 12 | 6 | Digital Output Slow | 2 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 36796 | 436,797
64 | 12 | 7 | Digital Output Slow | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36798 | 436,799
64 | 12 | 8 | Digital Output Slow | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 36800 | 436,801
64 | 12 | 9 | Digital Output Slow | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 36802 | 436,803
64 | 12 | 10 | Digital Output Slow | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 36804 | 436,805
64 | 12 | 12 | Digital Output Slow | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 36808 | 436,809
64 | 12 | 13 | Digital Output Slow | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36810 | 436,811
64 | 12 | 15 | Digital Output Slow | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36814 | 436,815
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52240 | 452,241
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52241 | 452,242
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52242 | 452,243
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52243 | 452,244
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52244 | 452,245
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52245 | 452,246
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52246 | 452,247
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52247 | 452,248
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52248 | 452,249
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52249 | 452,250
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52250 | 452,251
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52251 | 452,252
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52252 | 452,253
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52253 | 452,254
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52254 | 452,255
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52255 | 452,256
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52256 | 452,257
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52257 | 452,258
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52258 | 452,259
64 | 12 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52259 | 452,260
64 | 12 | 20 | Digital Output Slow | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 36824 | 436,825
64 | 13 | 2 | Digital Output Slow | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 36828 | 436,829
64 | 13 | 3 | Digital Output Slow | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 36830 | 436,831
64 | 13 | 5 | Digital Output Slow | 2 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 36834 | 436,835
64 | 13 | 6 | Digital Output Slow | 2 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 36836 | 436,837
64 | 13 | 7 | Digital Output Slow | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36838 | 436,839
64 | 13 | 8 | Digital Output Slow | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 36840 | 436,841
64 | 13 | 9 | Digital Output Slow | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 36842 | 436,843
64 | 13 | 10 | Digital Output Slow | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 36844 | 436,845
64 | 13 | 12 | Digital Output Slow | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 36848 | 436,849
64 | 13 | 13 | Digital Output Slow | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36850 | 436,851
64 | 13 | 15 | Digital Output Slow | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36854 | 436,855
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52260 | 452,261
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52261 | 452,262
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52262 | 452,263
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52263 | 452,264
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52264 | 452,265
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52265 | 452,266
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52266 | 452,267
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52267 | 452,268
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52268 | 452,269
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52269 | 452,270
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52270 | 452,271
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52271 | 452,272
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52272 | 452,273
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52273 | 452,274
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52274 | 452,275
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52275 | 452,276
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52276 | 452,277
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52277 | 452,278
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52278 | 452,279
64 | 13 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52279 | 452,280
64 | 13 | 20 | Digital Output Slow | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 36864 | 436,865
64 | 14 | 2 | Digital Output Slow | 2 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 36868 | 436,869
64 | 14 | 3 | Digital Output Slow | 2 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 36870 | 436,871
64 | 14 | 5 | Digital Output Slow | 2 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 36874 | 436,875
64 | 14 | 6 | Digital Output Slow | 2 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 36876 | 436,877
64 | 14 | 7 | Digital Output Slow | 2 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36878 | 436,879
64 | 14 | 8 | Digital Output Slow | 2 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 36880 | 436,881
64 | 14 | 9 | Digital Output Slow | 2 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 36882 | 436,883
64 | 14 | 10 | Digital Output Slow | 2 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 36884 | 436,885
64 | 14 | 12 | Digital Output Slow | 2 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 36888 | 436,889
64 | 14 | 13 | Digital Output Slow | 2 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36890 | 436,891
64 | 14 | 15 | Digital Output Slow | 2 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36894 | 436,895
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52280 | 452,281
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52281 | 452,282
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52282 | 452,283
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52283 | 452,284
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52284 | 452,285
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52285 | 452,286
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52286 | 452,287
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52287 | 452,288
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52288 | 452,289
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52289 | 452,290
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52290 | 452,291
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52291 | 452,292
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52292 | 452,293
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52293 | 452,294
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52294 | 452,295
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52295 | 452,296
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52296 | 452,297
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52297 | 452,298
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52298 | 452,299
64 | 14 | 19 | Digital Output Slow | 2 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52299 | 452,300
64 | 14 | 20 | Digital Output Slow | 2 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 36904 | 436,905
64 | 21 | 2 | Digital Output Slow | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 36908 | 436,909
64 | 21 | 3 | Digital Output Slow | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 36910 | 436,911
64 | 21 | 5 | Digital Output Slow | 3 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 36914 | 436,915
64 | 21 | 6 | Digital Output Slow | 3 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 36916 | 436,917
64 | 21 | 7 | Digital Output Slow | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36918 | 436,919
64 | 21 | 8 | Digital Output Slow | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 36920 | 436,921
64 | 21 | 9 | Digital Output Slow | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 36922 | 436,923
64 | 21 | 10 | Digital Output Slow | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 36924 | 436,925
64 | 21 | 12 | Digital Output Slow | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 36928 | 436,929
64 | 21 | 13 | Digital Output Slow | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36930 | 436,931
64 | 21 | 15 | Digital Output Slow | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36934 | 436,935
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52300 | 452,301
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52301 | 452,302
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52302 | 452,303
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52303 | 452,304
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52304 | 452,305
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52305 | 452,306
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52306 | 452,307
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52307 | 452,308
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52308 | 452,309
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52309 | 452,310
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52310 | 452,311
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52311 | 452,312
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52312 | 452,313
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52313 | 452,314
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52314 | 452,315
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52315 | 452,316
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52316 | 452,317
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52317 | 452,318
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52318 | 452,319
64 | 21 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52319 | 452,320
64 | 21 | 20 | Digital Output Slow | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 36944 | 436,945
64 | 22 | 2 | Digital Output Slow | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 36948 | 436,949
64 | 22 | 3 | Digital Output Slow | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 36950 | 436,951
64 | 22 | 5 | Digital Output Slow | 3 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 36954 | 436,955
64 | 22 | 6 | Digital Output Slow | 3 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 36956 | 436,957
64 | 22 | 7 | Digital Output Slow | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36958 | 436,959
64 | 22 | 8 | Digital Output Slow | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 36960 | 436,961
64 | 22 | 9 | Digital Output Slow | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 36962 | 436,963
64 | 22 | 10 | Digital Output Slow | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 36964 | 436,965
64 | 22 | 12 | Digital Output Slow | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 36968 | 436,969
64 | 22 | 13 | Digital Output Slow | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 36970 | 436,971
64 | 22 | 15 | Digital Output Slow | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 36974 | 436,975
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52320 | 452,321
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52321 | 452,322
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52322 | 452,323
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52323 | 452,324
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52324 | 452,325
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52325 | 452,326
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52326 | 452,327
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52327 | 452,328
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52328 | 452,329
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52329 | 452,330
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52330 | 452,331
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52331 | 452,332
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52332 | 452,333
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52333 | 452,334
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52334 | 452,335
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52335 | 452,336
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52336 | 452,337
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52337 | 452,338
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52338 | 452,339
64 | 22 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52339 | 452,340
64 | 22 | 20 | Digital Output Slow | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 36984 | 436,985
64 | 23 | 2 | Digital Output Slow | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 36988 | 436,989
64 | 23 | 3 | Digital Output Slow | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 36990 | 436,991
64 | 23 | 5 | Digital Output Slow | 3 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 36994 | 436,995
64 | 23 | 6 | Digital Output Slow | 3 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 36996 | 436,997
64 | 23 | 7 | Digital Output Slow | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 36998 | 436,999
64 | 23 | 8 | Digital Output Slow | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 37000 | 437,001
64 | 23 | 9 | Digital Output Slow | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 37002 | 437,003
64 | 23 | 10 | Digital Output Slow | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 37004 | 437,005
64 | 23 | 12 | Digital Output Slow | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 37008 | 437,009
64 | 23 | 13 | Digital Output Slow | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 37010 | 437,011
64 | 23 | 15 | Digital Output Slow | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 37014 | 437,015
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52340 | 452,341
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52341 | 452,342
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52342 | 452,343
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52343 | 452,344
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52344 | 452,345
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52345 | 452,346
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52346 | 452,347
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52347 | 452,348
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52348 | 452,349
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52349 | 452,350
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52350 | 452,351
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52351 | 452,352
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52352 | 452,353
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52353 | 452,354
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52354 | 452,355
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52355 | 452,356
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52356 | 452,357
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52357 | 452,358
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52358 | 452,359
64 | 23 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52359 | 452,360
64 | 23 | 20 | Digital Output Slow | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 37024 | 437,025
64 | 24 | 2 | Digital Output Slow | 3 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 37028 | 437,029
64 | 24 | 3 | Digital Output Slow | 3 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 37030 | 437,031
64 | 24 | 5 | Digital Output Slow | 3 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 37034 | 437,035
64 | 24 | 6 | Digital Output Slow | 3 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 37036 | 437,037
64 | 24 | 7 | Digital Output Slow | 3 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 37038 | 437,039
64 | 24 | 8 | Digital Output Slow | 3 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 37040 | 437,041
64 | 24 | 9 | Digital Output Slow | 3 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 37042 | 437,043
64 | 24 | 10 | Digital Output Slow | 3 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 37044 | 437,045
64 | 24 | 12 | Digital Output Slow | 3 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 37048 | 437,049
64 | 24 | 13 | Digital Output Slow | 3 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 37050 | 437,051
64 | 24 | 15 | Digital Output Slow | 3 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 37054 | 437,055
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52360 | 452,361
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52361 | 452,362
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52362 | 452,363
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52363 | 452,364
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52364 | 452,365
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52365 | 452,366
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52366 | 452,367
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52367 | 452,368
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52368 | 452,369
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52369 | 452,370
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52370 | 452,371
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52371 | 452,372
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52372 | 452,373
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52373 | 452,374
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52374 | 452,375
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52375 | 452,376
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52376 | 452,377
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52377 | 452,378
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52378 | 452,379
64 | 24 | 19 | Digital Output Slow | 3 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52379 | 452,380
64 | 24 | 20 | Digital Output Slow | 3 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 37064 | 437,065
64 | 31 | 2 | Digital Output Slow | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 37068 | 437,069
64 | 31 | 3 | Digital Output Slow | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 37070 | 437,071
64 | 31 | 5 | Digital Output Slow | 4 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 37074 | 437,075
64 | 31 | 6 | Digital Output Slow | 4 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 37076 | 437,077
64 | 31 | 7 | Digital Output Slow | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 37078 | 437,079
64 | 31 | 8 | Digital Output Slow | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 37080 | 437,081
64 | 31 | 9 | Digital Output Slow | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 37082 | 437,083
64 | 31 | 10 | Digital Output Slow | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 37084 | 437,085
64 | 31 | 12 | Digital Output Slow | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 37088 | 437,089
64 | 31 | 13 | Digital Output Slow | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 37090 | 437,091
64 | 31 | 15 | Digital Output Slow | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 37094 | 437,095
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52380 | 452,381
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52381 | 452,382
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52382 | 452,383
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52383 | 452,384
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52384 | 452,385
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52385 | 452,386
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52386 | 452,387
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52387 | 452,388
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52388 | 452,389
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52389 | 452,390
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52390 | 452,391
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52391 | 452,392
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52392 | 452,393
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52393 | 452,394
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52394 | 452,395
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52395 | 452,396
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52396 | 452,397
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52397 | 452,398
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52398 | 452,399
64 | 31 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52399 | 452,400
64 | 31 | 20 | Digital Output Slow | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 37104 | 437,105
64 | 32 | 2 | Digital Output Slow | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 37108 | 437,109
64 | 32 | 3 | Digital Output Slow | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 37110 | 437,111
64 | 32 | 5 | Digital Output Slow | 4 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 37114 | 437,115
64 | 32 | 6 | Digital Output Slow | 4 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 37116 | 437,117
64 | 32 | 7 | Digital Output Slow | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 37118 | 437,119
64 | 32 | 8 | Digital Output Slow | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 37120 | 437,121
64 | 32 | 9 | Digital Output Slow | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 37122 | 437,123
64 | 32 | 10 | Digital Output Slow | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 37124 | 437,125
64 | 32 | 12 | Digital Output Slow | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 37128 | 437,129
64 | 32 | 13 | Digital Output Slow | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 37130 | 437,131
64 | 32 | 15 | Digital Output Slow | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 37134 | 437,135
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52400 | 452,401
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52401 | 452,402
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52402 | 452,403
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52403 | 452,404
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52404 | 452,405
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52405 | 452,406
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52406 | 452,407
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52407 | 452,408
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52408 | 452,409
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52409 | 452,410
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52410 | 452,411
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52411 | 452,412
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52412 | 452,413
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52413 | 452,414
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52414 | 452,415
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52415 | 452,416
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52416 | 452,417
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52417 | 452,418
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52418 | 452,419
64 | 32 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52419 | 452,420
64 | 32 | 20 | Digital Output Slow | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 37144 | 437,145
64 | 33 | 2 | Digital Output Slow | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 37148 | 437,149
64 | 33 | 3 | Digital Output Slow | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 37150 | 437,151
64 | 33 | 5 | Digital Output Slow | 4 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 37154 | 437,155
64 | 33 | 6 | Digital Output Slow | 4 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 37156 | 437,157
64 | 33 | 7 | Digital Output Slow | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 37158 | 437,159
64 | 33 | 8 | Digital Output Slow | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 37160 | 437,161
64 | 33 | 9 | Digital Output Slow | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 37162 | 437,163
64 | 33 | 10 | Digital Output Slow | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 37164 | 437,165
64 | 33 | 12 | Digital Output Slow | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 37168 | 437,169
64 | 33 | 13 | Digital Output Slow | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 37170 | 437,171
64 | 33 | 15 | Digital Output Slow | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 37174 | 437,175
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52420 | 452,421
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52421 | 452,422
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52422 | 452,423
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52423 | 452,424
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52424 | 452,425
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52425 | 452,426
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52426 | 452,427
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52427 | 452,428
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52428 | 452,429
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52429 | 452,430
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52430 | 452,431
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52431 | 452,432
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52432 | 452,433
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52433 | 452,434
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52434 | 452,435
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52435 | 452,436
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52436 | 452,437
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52437 | 452,438
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52438 | 452,439
64 | 33 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52439 | 452,440
64 | 33 | 20 | Digital Output Slow | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 37184 | 437,185
64 | 34 | 2 | Digital Output Slow | 4 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 37188 | 437,189
64 | 34 | 3 | Digital Output Slow | 4 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 37190 | 437,191
64 | 34 | 5 | Digital Output Slow | 4 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 37194 | 437,195
64 | 34 | 6 | Digital Output Slow | 4 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 37196 | 437,197
64 | 34 | 7 | Digital Output Slow | 4 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 37198 | 437,199
64 | 34 | 8 | Digital Output Slow | 4 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 37200 | 437,201
64 | 34 | 9 | Digital Output Slow | 4 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 37202 | 437,203
64 | 34 | 10 | Digital Output Slow | 4 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 37204 | 437,205
64 | 34 | 12 | Digital Output Slow | 4 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 37208 | 437,209
64 | 34 | 13 | Digital Output Slow | 4 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 37210 | 437,211
64 | 34 | 15 | Digital Output Slow | 4 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 37214 | 437,215
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52440 | 452,441
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52441 | 452,442
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52442 | 452,443
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52443 | 452,444
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52444 | 452,445
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52445 | 452,446
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52446 | 452,447
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52447 | 452,448
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52448 | 452,449
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52449 | 452,450
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52450 | 452,451
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52451 | 452,452
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52452 | 452,453
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52453 | 452,454
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52454 | 452,455
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52455 | 452,456
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52456 | 452,457
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52457 | 452,458
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52458 | 452,459
64 | 34 | 19 | Digital Output Slow | 4 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52459 | 452,460
64 | 34 | 20 | Digital Output Slow | 4 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 37224 | 437,225
64 | 41 | 2 | Digital Output Slow | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 37228 | 437,229
64 | 41 | 3 | Digital Output Slow | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 37230 | 437,231
64 | 41 | 5 | Digital Output Slow | 5 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 37234 | 437,235
64 | 41 | 6 | Digital Output Slow | 5 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 37236 | 437,237
64 | 41 | 7 | Digital Output Slow | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 37238 | 437,239
64 | 41 | 8 | Digital Output Slow | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 37240 | 437,241
64 | 41 | 9 | Digital Output Slow | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 37242 | 437,243
64 | 41 | 10 | Digital Output Slow | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 37244 | 437,245
64 | 41 | 12 | Digital Output Slow | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 37248 | 437,249
64 | 41 | 13 | Digital Output Slow | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 37250 | 437,251
64 | 41 | 15 | Digital Output Slow | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 37254 | 437,255
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52460 | 452,461
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52461 | 452,462
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52462 | 452,463
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52463 | 452,464
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52464 | 452,465
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52465 | 452,466
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52466 | 452,467
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52467 | 452,468
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52468 | 452,469
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52469 | 452,470
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52470 | 452,471
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52471 | 452,472
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52472 | 452,473
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52473 | 452,474
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52474 | 452,475
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52475 | 452,476
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52476 | 452,477
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52477 | 452,478
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52478 | 452,479
64 | 41 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52479 | 452,480
64 | 41 | 20 | Digital Output Slow | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 37264 | 437,265
64 | 42 | 2 | Digital Output Slow | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 37268 | 437,269
64 | 42 | 3 | Digital Output Slow | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 37270 | 437,271
64 | 42 | 5 | Digital Output Slow | 5 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 37274 | 437,275
64 | 42 | 6 | Digital Output Slow | 5 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 37276 | 437,277
64 | 42 | 7 | Digital Output Slow | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 37278 | 437,279
64 | 42 | 8 | Digital Output Slow | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 37280 | 437,281
64 | 42 | 9 | Digital Output Slow | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 37282 | 437,283
64 | 42 | 10 | Digital Output Slow | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 37284 | 437,285
64 | 42 | 12 | Digital Output Slow | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 37288 | 437,289
64 | 42 | 13 | Digital Output Slow | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 37290 | 437,291
64 | 42 | 15 | Digital Output Slow | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 37294 | 437,295
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52480 | 452,481
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52481 | 452,482
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52482 | 452,483
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52483 | 452,484
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52484 | 452,485
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52485 | 452,486
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52486 | 452,487
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52487 | 452,488
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52488 | 452,489
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52489 | 452,490
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52490 | 452,491
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52491 | 452,492
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52492 | 452,493
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52493 | 452,494
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52494 | 452,495
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52495 | 452,496
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52496 | 452,497
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52497 | 452,498
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52498 | 452,499
64 | 42 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52499 | 452,500
64 | 42 | 20 | Digital Output Slow | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 37304 | 437,305
64 | 43 | 2 | Digital Output Slow | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 37308 | 437,309
64 | 43 | 3 | Digital Output Slow | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 37310 | 437,311
64 | 43 | 5 | Digital Output Slow | 5 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 37314 | 437,315
64 | 43 | 6 | Digital Output Slow | 5 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 37316 | 437,317
64 | 43 | 7 | Digital Output Slow | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 37318 | 437,319
64 | 43 | 8 | Digital Output Slow | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 37320 | 437,321
64 | 43 | 9 | Digital Output Slow | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 37322 | 437,323
64 | 43 | 10 | Digital Output Slow | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 37324 | 437,325
64 | 43 | 12 | Digital Output Slow | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 37328 | 437,329
64 | 43 | 13 | Digital Output Slow | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 37330 | 437,331
64 | 43 | 15 | Digital Output Slow | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 37334 | 437,335
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52500 | 452,501
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52501 | 452,502
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52502 | 452,503
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52503 | 452,504
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52504 | 452,505
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52505 | 452,506
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52506 | 452,507
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52507 | 452,508
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52508 | 452,509
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52509 | 452,510
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52510 | 452,511
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52511 | 452,512
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52512 | 452,513
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52513 | 452,514
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52514 | 452,515
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52515 | 452,516
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52516 | 452,517
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52517 | 452,518
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52518 | 452,519
64 | 43 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52519 | 452,520
64 | 43 | 20 | Digital Output Slow | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 37344 | 437,345
64 | 44 | 2 | Digital Output Slow | 5 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 37348 | 437,349
64 | 44 | 3 | Digital Output Slow | 5 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 37350 | 437,351
64 | 44 | 5 | Digital Output Slow | 5 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 37354 | 437,355
64 | 44 | 6 | Digital Output Slow | 5 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 37356 | 437,357
64 | 44 | 7 | Digital Output Slow | 5 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 37358 | 437,359
64 | 44 | 8 | Digital Output Slow | 5 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 37360 | 437,361
64 | 44 | 9 | Digital Output Slow | 5 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 37362 | 437,363
64 | 44 | 10 | Digital Output Slow | 5 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 37364 | 437,365
64 | 44 | 12 | Digital Output Slow | 5 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 37368 | 437,369
64 | 44 | 13 | Digital Output Slow | 5 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 37370 | 437,371
64 | 44 | 15 | Digital Output Slow | 5 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 37374 | 437,375
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52520 | 452,521
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52521 | 452,522
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52522 | 452,523
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52523 | 452,524
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52524 | 452,525
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52525 | 452,526
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52526 | 452,527
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52527 | 452,528
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52528 | 452,529
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52529 | 452,530
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52530 | 452,531
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52531 | 452,532
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52532 | 452,533
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52533 | 452,534
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52534 | 452,535
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52535 | 452,536
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52536 | 452,537
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52537 | 452,538
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52538 | 452,539
64 | 44 | 19 | Digital Output Slow | 5 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52539 | 452,540
64 | 44 | 20 | Digital Output Slow | 5 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 37384 | 437,385
64 | 51 | 2 | Digital Output Slow | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 37388 | 437,389
64 | 51 | 3 | Digital Output Slow | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 37390 | 437,391
64 | 51 | 5 | Digital Output Slow | 6 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 37394 | 437,395
64 | 51 | 6 | Digital Output Slow | 6 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 37396 | 437,397
64 | 51 | 7 | Digital Output Slow | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 37398 | 437,399
64 | 51 | 8 | Digital Output Slow | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 37400 | 437,401
64 | 51 | 9 | Digital Output Slow | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 37402 | 437,403
64 | 51 | 10 | Digital Output Slow | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 37404 | 437,405
64 | 51 | 12 | Digital Output Slow | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 37408 | 437,409
64 | 51 | 13 | Digital Output Slow | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 37410 | 437,411
64 | 51 | 15 | Digital Output Slow | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 37414 | 437,415
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52540 | 452,541
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52541 | 452,542
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52542 | 452,543
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52543 | 452,544
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52544 | 452,545
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52545 | 452,546
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52546 | 452,547
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52547 | 452,548
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52548 | 452,549
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52549 | 452,550
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52550 | 452,551
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52551 | 452,552
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52552 | 452,553
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52553 | 452,554
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52554 | 452,555
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52555 | 452,556
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52556 | 452,557
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52557 | 452,558
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52558 | 452,559
64 | 51 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52559 | 452,560
64 | 51 | 20 | Digital Output Slow | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 37424 | 437,425
64 | 52 | 2 | Digital Output Slow | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 37428 | 437,429
64 | 52 | 3 | Digital Output Slow | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 37430 | 437,431
64 | 52 | 5 | Digital Output Slow | 6 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 37434 | 437,435
64 | 52 | 6 | Digital Output Slow | 6 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 37436 | 437,437
64 | 52 | 7 | Digital Output Slow | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 37438 | 437,439
64 | 52 | 8 | Digital Output Slow | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 37440 | 437,441
64 | 52 | 9 | Digital Output Slow | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 37442 | 437,443
64 | 52 | 10 | Digital Output Slow | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 37444 | 437,445
64 | 52 | 12 | Digital Output Slow | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 37448 | 437,449
64 | 52 | 13 | Digital Output Slow | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 37450 | 437,451
64 | 52 | 15 | Digital Output Slow | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 37454 | 437,455
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52560 | 452,561
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52561 | 452,562
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52562 | 452,563
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52563 | 452,564
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52564 | 452,565
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52565 | 452,566
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52566 | 452,567
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52567 | 452,568
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52568 | 452,569
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52569 | 452,570
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52570 | 452,571
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52571 | 452,572
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52572 | 452,573
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52573 | 452,574
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52574 | 452,575
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52575 | 452,576
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52576 | 452,577
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52577 | 452,578
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52578 | 452,579
64 | 52 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52579 | 452,580
64 | 52 | 20 | Digital Output Slow | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 37464 | 437,465
64 | 53 | 2 | Digital Output Slow | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 37468 | 437,469
64 | 53 | 3 | Digital Output Slow | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 37470 | 437,471
64 | 53 | 5 | Digital Output Slow | 6 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 37474 | 437,475
64 | 53 | 6 | Digital Output Slow | 6 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 37476 | 437,477
64 | 53 | 7 | Digital Output Slow | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 37478 | 437,479
64 | 53 | 8 | Digital Output Slow | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 37480 | 437,481
64 | 53 | 9 | Digital Output Slow | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 37482 | 437,483
64 | 53 | 10 | Digital Output Slow | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 37484 | 437,485
64 | 53 | 12 | Digital Output Slow | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 37488 | 437,489
64 | 53 | 13 | Digital Output Slow | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 37490 | 437,491
64 | 53 | 15 | Digital Output Slow | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 37494 | 437,495
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52580 | 452,581
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52581 | 452,582
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52582 | 452,583
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52583 | 452,584
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52584 | 452,585
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52585 | 452,586
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52586 | 452,587
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52587 | 452,588
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52588 | 452,589
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52589 | 452,590
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52590 | 452,591
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52591 | 452,592
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52592 | 452,593
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52593 | 452,594
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52594 | 452,595
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52595 | 452,596
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52596 | 452,597
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52597 | 452,598
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52598 | 452,599
64 | 53 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52599 | 452,600
64 | 53 | 20 | Digital Output Slow | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 37504 | 437,505
64 | 54 | 2 | Digital Output Slow | 6 | Time Base Type | Set the output control type used by PID control. | Fixed Time Base (34) | Fixed Time Base (34) | Enumeration | R/W | 37508 | 437,509
64 | 54 | 3 | Digital Output Slow | 6 | Fixed Time Base | Set the time base for fixed-time-base control. | 5.0 to 60.0 | 20.0 | IEEE Float | R/W | 37510 | 437,511
64 | 54 | 5 | Digital Output Slow | 6 | Function | Set what function will drive this output. | Off (62), Analog Input (142), Alarm (6), Cool Power (161), Heat Power (160), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Linearization (238), Math (240), Process Value (241), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Limit (126), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Cascade Cool Power (1795), Cascade Heat Power (1794) | Off (62) | Enumeration | R/W | 37514 | 437,515
64 | 54 | 6 | Digital Output Slow | 6 | Output Function Instance | Set the instance of the function which will drive this output. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 37516 | 437,517
64 | 54 | 7 | Digital Output Slow | 6 | Output State | Monitor the state of the output. | On (63), Off (62) |  | Enumeration | R | 37518 | 437,519
64 | 54 | 8 | Digital Output Slow | 6 | Output Power | Monitor the power applied to this output. |  |  | IEEE Float | R | 37520 | 437,521
64 | 54 | 9 | Digital Output Slow | 6 | Low Power Scale | Set the minimum power supplied to output. | 0.0 to 100.0 | 0.0 | IEEE Float | R/W | 37522 | 437,523
64 | 54 | 10 | Digital Output Slow | 6 | High Power Scale | Set the maximum power supplied to output. | 0.0 to 100.0 | 100.0 | IEEE Float | R/W | 37524 | 437,525
64 | 54 | 12 | Digital Output Slow | 6 | Output Source Zone | Set the zone of the function which will drive this output. 0 = inside same unit. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 37528 | 437,529
64 | 54 | 13 | Digital Output Slow | 6 | Source Value A | Monitor the value of the source driving this output. |  |  | IEEE Float | R | 37530 | 437,531
64 | 54 | 15 | Digital Output Slow | 6 | Error | Monitor the input source for errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | Enumeration | R | 37534 | 437,535
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52600 | 452,601
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52601 | 452,602
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52602 | 452,603
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52603 | 452,604
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52604 | 452,605
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52605 | 452,606
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52606 | 452,607
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52607 | 452,608
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52608 | 452,609
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52609 | 452,610
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52610 | 452,611
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52611 | 452,612
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52612 | 452,613
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52613 | 452,614
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52614 | 452,615
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52615 | 452,616
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52616 | 452,617
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52617 | 452,618
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52618 | 452,619
64 | 54 | 19 | Digital Output Slow | 6 | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52619 | 452,620
64 | 54 | 20 | Digital Output Slow | 6 | Output Type | Monitor the hardware type of this output. | Form A Mechanical Relay (10029), Form A Mechanical Relay w/ Shared Common (10030), Form C Mechanical Relay (10028), NO-ARC Relay (10031) |  | Enumeration | R | 37544 | 437,545
69 | 1 | 1 | Modbus | 6 | Display Units | Set the units for temperature measurement via comms. | F (30), C (15) | F (30) | Enumeration | R/W | 14080 | 414,081
69 | 1 | 2 | Modbus | 6 | Non-Volatile Save | Set to save/not save changes via comms. | No (59), Yes (106) | No (59) | Enumeration | R/W | 14082 | 414,083
69 | 1 | 3 | Modbus | 6 | Baud Rate | Set the baud rate to match device connected. | 9600 (188), 19200 (189), 38400 (190) | 9600 (188) | Enumeration | R/W | 14084 | 414,085
69 | 1 | 4 | Modbus | 6 | Parity | Set the parity to match device connected. | None (61), Even (191), Odd (192) | None (61) | Enumeration | R/W | 14086 | 414,087
69 | 1 | 5 | Modbus | 6 | Modbus Address | Set the Modbus ID for unique number on network. | 1 to 247 | 1 | Unsigned 8-bit | R/W | 14088 | 414,089
69 | 1 | 7 | Modbus | 6 | Modbus Word Order | Set the Modbus Word Order. | High Low (1330), Low High (1331) | Low High (1331) | Enumeration | R/W | 14092 | 414,093
69 | 1 | 8 | Modbus | 6 | Data Map | Set which Modbus mapping to apply. | 1 to 2 | 1 | Unsigned 8-bit | R/W | 14094 | 414,095
70 | 1 | 1 | Ethernet | Base | Display Units | Set the units for temperature measurement via comms. | F (30), C (15) | F (30) | Enumeration | R/W | 6730 | 406,731
70 | 1 | 2 | Ethernet | Base | Non-Volatile Save | Set to save/not save changes via comms. | No (59), Yes (106) | No (59) | Enumeration | R/W | 6732 | 406,733
70 | 1 | 3 | Ethernet | Base | Modbus TCP Enable | Set to enable Modbus TCP protocol communications. | No (59), Yes (106) | Yes (106) | Enumeration | R/W | 6734 | 406,735
70 | 1 | 4 | Ethernet | Base | Modbus Word Order | Set the Modbus Word Order. | High Low (1330), Low High (1331) | Low High (1331) | Enumeration | R/W | 6736 | 406,737
70 | 1 | 5 | Ethernet | Base | EtherNet/IP Enable | Set to enable EtherNet/IP protocol communications. | No (59), Yes (106) | Yes (106) | Enumeration | R/W | 6738 | 406,739
70 | 1 | 6 | Ethernet | Base | Data Map | Set which Modbus mapping to apply. | 1 to 2 | 1 | Unsigned 8-bit | R/W | 6740 | 406,741
70 | 1 | 16 | Ethernet | Base | IP Address Mode | Set for IP address assignment method. | DHCP (1281), Fixed (1284) | DHCP (1281) | Enumeration | R/W | 6760 | 406,761
70 | 1 | 17 | Ethernet | Base | IP Fixed Address Part 1 | Set the IP address of this module when fixed. | 0 to 255 | 192 | Unsigned 8-bit | R/W | 6762 | 406,763
70 | 1 | 18 | Ethernet | Base | IP Fixed Address Part 2 | Set the IP address of this module when fixed. | 0 to 255 | 168 | Unsigned 8-bit | R/W | 6764 | 406,765
70 | 1 | 19 | Ethernet | Base | IP Fixed Address Part 3 | Set the IP address of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 6766 | 406,767
70 | 1 | 20 | Ethernet | Base | IP Fixed Address Part 4 | Set the IP address of this module when fixed. | 0 to 255 | 222 | Unsigned 8-bit | R/W | 6768 | 406,769
70 | 1 | 21 | Ethernet | Base | IP Fixed Address Part 5 | Set the IP address of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 6770 | 406,771
70 | 1 | 22 | Ethernet | Base | IP Fixed Address Part 6 | Set the IP address of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 6772 | 406,773
70 | 1 | 23 | Ethernet | Base | IP Fixed Subnet Part 1 | Set the IP address subnet of this module when fixed. | 0 to 255 | 255 | Unsigned 8-bit | R/W | 6774 | 406,775
70 | 1 | 24 | Ethernet | Base | IP Fixed Subnet Part 2 | Set the IP address subnet of this module when fixed. | 0 to 255 | 255 | Unsigned 8-bit | R/W | 6776 | 406,777
70 | 1 | 25 | Ethernet | Base | IP Fixed Subnet Part 3 | Set the IP address subnet of this module when fixed. | 0 to 255 | 255 | Unsigned 8-bit | R/W | 6778 | 406,779
70 | 1 | 26 | Ethernet | Base | IP Fixed Subnet Part 4 | Set the IP address subnet of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 6780 | 406,781
70 | 1 | 27 | Ethernet | Base | IP Fixed Subnet Part 5 | Set the IP address subnet of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 6782 | 406,783
70 | 1 | 28 | Ethernet | Base | IP Fixed Subnet Part 6 | Set the IP address subnet of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 6784 | 406,785
70 | 1 | 29 | Ethernet | Base | Fixed IP Gateway Part 1 | Set the IP gateway of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 6786 | 406,787
70 | 1 | 30 | Ethernet | Base | Fixed IP Gateway Part 2 | Set the IP gateway of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 6788 | 406,789
70 | 1 | 31 | Ethernet | Base | Fixed IP Gateway Part 3 | Set the IP gateway of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 6790 | 406,791
70 | 1 | 32 | Ethernet | Base | Fixed IP Gateway Part 4 | Set the IP gateway of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 6792 | 406,793
70 | 1 | 33 | Ethernet | Base | Fixed IP Gateway Part 5 | Set the IP gateway of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 6794 | 406,795
70 | 1 | 34 | Ethernet | Base | Fixed IP Gateway Part 6 | Set the IP gateway of this module when fixed. | 0 to 255 | 0 | Unsigned 8-bit | R/W | 6796 | 406,797
70 | 1 | 35 | Ethernet | Base | Actual IP Addressing Mode | Monitor the actual IP address assignment method. | None (61), DHCP (1281), Fixed (1284), Fail (32) | Fixed (1284) | Enumeration | R | 6798 | 406,799
70 | 1 | 39 | Ethernet | Base | IP Actual Address Part 1 | Monitor the actual IP address assigned. | 0 to 255 | 0 | Unsigned 8-bit | R | 6806 | 406,807
70 | 1 | 40 | Ethernet | Base | IP Actual Address Part 2 | Monitor the actual IP address assigned. | 0 to 255 | 0 | Unsigned 8-bit | R | 6808 | 406,809
70 | 1 | 41 | Ethernet | Base | IP Actual Address Part 3 | Monitor the actual IP address assigned. | 0 to 255 | 0 | Unsigned 8-bit | R | 6810 | 406,811
70 | 1 | 42 | Ethernet | Base | IP Actual Address Part 4 | Monitor the actual IP address assigned. | 0 to 255 | 0 | Unsigned 8-bit | R | 6812 | 406,813
70 | 1 | 43 | Ethernet | Base | IP Actual Address Part 5 | Monitor the actual IP address assigned. | 0 to 255 | 0 | Unsigned 8-bit | R | 6814 | 406,815
70 | 1 | 44 | Ethernet | Base | IP Actual Address Part 6 | Monitor the actual IP address assigned. | 0 to 255 | 0 | Unsigned 8-bit | R | 6816 | 406,817
70 | 1 | 45 | Ethernet | Base | MAC Address | Monitor the Media Access Control ID. | 0 to 255 | 0 | Unsigned 8-bit | R | 6818 | 406,819
70 | 1 | 46 | Ethernet | Base | MAC Address | Monitor the Media Access Control ID. | 0 to 255 | 0 | Unsigned 8-bit | R | 6820 | 406,821
70 | 1 | 47 | Ethernet | Base | MAC Address | Monitor the Media Access Control ID. | 0 to 255 | 0 | Unsigned 8-bit | R | 6822 | 406,823
70 | 1 | 48 | Ethernet | Base | MAC Address | Monitor the Media Access Control ID. | 0 to 255 | 0 | Unsigned 8-bit | R | 6824 | 406,825
70 | 1 | 49 | Ethernet | Base | MAC Address | Monitor the Media Access Control ID. | 0 to 255 | 0 | Unsigned 8-bit | R | 6826 | 406,827
70 | 1 | 50 | Ethernet | Base | MAC Address | Monitor the Media Access Control ID. | 0 to 255 | 0 | Unsigned 8-bit | R | 6828 | 406,829
70 | 1 | 52 | Ethernet | Base | IP Version | Monitor the IP version in effect. | IP Version 4 (1279), IP Version 6 (1280) | IP Version 4 (1279) | Enumeration | R/W | 6832 | 406,833
74 | 1 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 1330 | 401,331
74 | 1 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 1332 | 401,333
74 | 1 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 1334 | 401,335
74 | 1 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 1336 | 401,337
74 | 1 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 1338 | 401,339
74 | 1 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1340 | 401,341
74 | 1 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 1342 | 401,343
74 | 1 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 1344 | 401,345
74 | 1 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 1346 | 401,347
74 | 1 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 1348 | 401,349
74 | 1 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 1350 | 401,351
74 | 1 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 1352 | 401,353
74 | 1 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 1354 | 401,355
74 | 1 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 1356 | 401,357
74 | 1 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 1358 | 401,359
74 | 1 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 1360 | 401,361
74 | 1 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 1362 | 401,363
74 | 1 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1364 | 401,365
74 | 1 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1366 | 401,367
74 | 1 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1368 | 401,369
74 | 1 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1370 | 401,371
74 | 1 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1372 | 401,373
74 | 1 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1374 | 401,375
74 | 1 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1376 | 401,377
74 | 1 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1378 | 401,379
74 | 1 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1380 | 401,381
74 | 1 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1382 | 401,383
74 | 1 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1384 | 401,385
74 | 1 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 1386 | 401,387
74 | 1 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 1388 | 401,389
74 | 1 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1390 | 401,391
74 | 1 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1392 | 401,393
74 | 1 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1394 | 401,395
74 | 1 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 1396 | 401,397
74 | 1 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 1398 | 401,399
74 | 1 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1400 | 401,401
74 | 1 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1402 | 401,403
74 | 1 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1404 | 401,405
74 | 1 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 1406 | 401,407
74 | 1 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 1408 | 401,409
74 | 1 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1414 | 401,415
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52620 | 452,621
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52621 | 452,622
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52622 | 452,623
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52623 | 452,624
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52624 | 452,625
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52625 | 452,626
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52626 | 452,627
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52627 | 452,628
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52628 | 452,629
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52629 | 452,630
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52630 | 452,631
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52631 | 452,632
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52632 | 452,633
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52633 | 452,634
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52634 | 452,635
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52635 | 452,636
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52636 | 452,637
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52637 | 452,638
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52638 | 452,639
74 | 1 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52639 | 452,640
74 | 1 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 1418 | 401,419
74 | 2 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 1430 | 401,431
74 | 2 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 1432 | 401,433
74 | 2 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 1434 | 401,435
74 | 2 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 1436 | 401,437
74 | 2 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 1438 | 401,439
74 | 2 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1440 | 401,441
74 | 2 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 1442 | 401,443
74 | 2 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 1444 | 401,445
74 | 2 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 1446 | 401,447
74 | 2 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 1448 | 401,449
74 | 2 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 1450 | 401,451
74 | 2 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 1452 | 401,453
74 | 2 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 1454 | 401,455
74 | 2 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 1456 | 401,457
74 | 2 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 1458 | 401,459
74 | 2 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 1460 | 401,461
74 | 2 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 1462 | 401,463
74 | 2 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1464 | 401,465
74 | 2 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1466 | 401,467
74 | 2 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1468 | 401,469
74 | 2 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1470 | 401,471
74 | 2 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1472 | 401,473
74 | 2 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1474 | 401,475
74 | 2 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1476 | 401,477
74 | 2 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1478 | 401,479
74 | 2 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1480 | 401,481
74 | 2 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1482 | 401,483
74 | 2 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1484 | 401,485
74 | 2 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 1486 | 401,487
74 | 2 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 1488 | 401,489
74 | 2 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1490 | 401,491
74 | 2 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1492 | 401,493
74 | 2 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1494 | 401,495
74 | 2 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 1496 | 401,497
74 | 2 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 1498 | 401,499
74 | 2 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1500 | 401,501
74 | 2 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1502 | 401,503
74 | 2 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1504 | 401,505
74 | 2 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 1506 | 401,507
74 | 2 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 1508 | 401,509
74 | 2 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1514 | 401,515
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52640 | 452,641
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52641 | 452,642
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52642 | 452,643
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52643 | 452,644
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52644 | 452,645
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52645 | 452,646
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52646 | 452,647
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52647 | 452,648
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52648 | 452,649
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52649 | 452,650
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52650 | 452,651
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52651 | 452,652
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52652 | 452,653
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52653 | 452,654
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52654 | 452,655
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52655 | 452,656
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52656 | 452,657
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52657 | 452,658
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52658 | 452,659
74 | 2 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52659 | 452,660
74 | 2 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 1518 | 401,519
74 | 3 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 1530 | 401,531
74 | 3 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 1532 | 401,533
74 | 3 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 1534 | 401,535
74 | 3 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 1536 | 401,537
74 | 3 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 1538 | 401,539
74 | 3 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1540 | 401,541
74 | 3 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 1542 | 401,543
74 | 3 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 1544 | 401,545
74 | 3 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 1546 | 401,547
74 | 3 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 1548 | 401,549
74 | 3 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 1550 | 401,551
74 | 3 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 1552 | 401,553
74 | 3 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 1554 | 401,555
74 | 3 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 1556 | 401,557
74 | 3 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 1558 | 401,559
74 | 3 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 1560 | 401,561
74 | 3 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 1562 | 401,563
74 | 3 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1564 | 401,565
74 | 3 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1566 | 401,567
74 | 3 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1568 | 401,569
74 | 3 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1570 | 401,571
74 | 3 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1572 | 401,573
74 | 3 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1574 | 401,575
74 | 3 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1576 | 401,577
74 | 3 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1578 | 401,579
74 | 3 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1580 | 401,581
74 | 3 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1582 | 401,583
74 | 3 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1584 | 401,585
74 | 3 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 1586 | 401,587
74 | 3 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 1588 | 401,589
74 | 3 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1590 | 401,591
74 | 3 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1592 | 401,593
74 | 3 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1594 | 401,595
74 | 3 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 1596 | 401,597
74 | 3 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 1598 | 401,599
74 | 3 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1600 | 401,601
74 | 3 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1602 | 401,603
74 | 3 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1604 | 401,605
74 | 3 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 1606 | 401,607
74 | 3 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 1608 | 401,609
74 | 3 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1614 | 401,615
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52660 | 452,661
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52661 | 452,662
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52662 | 452,663
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52663 | 452,664
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52664 | 452,665
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52665 | 452,666
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52666 | 452,667
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52667 | 452,668
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52668 | 452,669
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52669 | 452,670
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52670 | 452,671
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52671 | 452,672
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52672 | 452,673
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52673 | 452,674
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52674 | 452,675
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52675 | 452,676
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52676 | 452,677
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52677 | 452,678
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52678 | 452,679
74 | 3 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52679 | 452,680
74 | 3 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 1618 | 401,619
74 | 4 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 1630 | 401,631
74 | 4 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 1632 | 401,633
74 | 4 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 1634 | 401,635
74 | 4 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 1636 | 401,637
74 | 4 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 1638 | 401,639
74 | 4 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1640 | 401,641
74 | 4 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 1642 | 401,643
74 | 4 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 1644 | 401,645
74 | 4 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 1646 | 401,647
74 | 4 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 1648 | 401,649
74 | 4 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 1650 | 401,651
74 | 4 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 1652 | 401,653
74 | 4 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 1654 | 401,655
74 | 4 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 1656 | 401,657
74 | 4 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 1658 | 401,659
74 | 4 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 1660 | 401,661
74 | 4 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 1662 | 401,663
74 | 4 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1664 | 401,665
74 | 4 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1666 | 401,667
74 | 4 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1668 | 401,669
74 | 4 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1670 | 401,671
74 | 4 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1672 | 401,673
74 | 4 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1674 | 401,675
74 | 4 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1676 | 401,677
74 | 4 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1678 | 401,679
74 | 4 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1680 | 401,681
74 | 4 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1682 | 401,683
74 | 4 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1684 | 401,685
74 | 4 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 1686 | 401,687
74 | 4 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 1688 | 401,689
74 | 4 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1690 | 401,691
74 | 4 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1692 | 401,693
74 | 4 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1694 | 401,695
74 | 4 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 1696 | 401,697
74 | 4 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 1698 | 401,699
74 | 4 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1700 | 401,701
74 | 4 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1702 | 401,703
74 | 4 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1704 | 401,705
74 | 4 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 1706 | 401,707
74 | 4 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 1708 | 401,709
74 | 4 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1714 | 401,715
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52680 | 452,681
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52681 | 452,682
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52682 | 452,683
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52683 | 452,684
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52684 | 452,685
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52685 | 452,686
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52686 | 452,687
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52687 | 452,688
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52688 | 452,689
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52689 | 452,690
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52690 | 452,691
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52691 | 452,692
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52692 | 452,693
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52693 | 452,694
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52694 | 452,695
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52695 | 452,696
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52696 | 452,697
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52697 | 452,698
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52698 | 452,699
74 | 4 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52699 | 452,700
74 | 4 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 1718 | 401,719
74 | 5 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 1730 | 401,731
74 | 5 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 1732 | 401,733
74 | 5 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 1734 | 401,735
74 | 5 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 1736 | 401,737
74 | 5 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 1738 | 401,739
74 | 5 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1740 | 401,741
74 | 5 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 1742 | 401,743
74 | 5 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 1744 | 401,745
74 | 5 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 1746 | 401,747
74 | 5 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 1748 | 401,749
74 | 5 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 1750 | 401,751
74 | 5 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 1752 | 401,753
74 | 5 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 1754 | 401,755
74 | 5 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 1756 | 401,757
74 | 5 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 1758 | 401,759
74 | 5 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 1760 | 401,761
74 | 5 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 1762 | 401,763
74 | 5 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1764 | 401,765
74 | 5 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1766 | 401,767
74 | 5 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1768 | 401,769
74 | 5 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1770 | 401,771
74 | 5 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1772 | 401,773
74 | 5 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1774 | 401,775
74 | 5 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1776 | 401,777
74 | 5 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1778 | 401,779
74 | 5 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1780 | 401,781
74 | 5 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1782 | 401,783
74 | 5 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1784 | 401,785
74 | 5 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 1786 | 401,787
74 | 5 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 1788 | 401,789
74 | 5 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1790 | 401,791
74 | 5 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1792 | 401,793
74 | 5 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1794 | 401,795
74 | 5 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 1796 | 401,797
74 | 5 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 1798 | 401,799
74 | 5 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1800 | 401,801
74 | 5 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1802 | 401,803
74 | 5 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1804 | 401,805
74 | 5 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 1806 | 401,807
74 | 5 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 1808 | 401,809
74 | 5 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1814 | 401,815
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52700 | 452,701
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52701 | 452,702
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52702 | 452,703
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52703 | 452,704
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52704 | 452,705
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52705 | 452,706
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52706 | 452,707
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52707 | 452,708
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52708 | 452,709
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52709 | 452,710
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52710 | 452,711
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52711 | 452,712
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52712 | 452,713
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52713 | 452,714
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52714 | 452,715
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52715 | 452,716
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52716 | 452,717
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52717 | 452,718
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52718 | 452,719
74 | 5 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52719 | 452,720
74 | 5 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 1818 | 401,819
74 | 6 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 1830 | 401,831
74 | 6 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 1832 | 401,833
74 | 6 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 1834 | 401,835
74 | 6 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 1836 | 401,837
74 | 6 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 1838 | 401,839
74 | 6 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1840 | 401,841
74 | 6 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 1842 | 401,843
74 | 6 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 1844 | 401,845
74 | 6 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 1846 | 401,847
74 | 6 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 1848 | 401,849
74 | 6 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 1850 | 401,851
74 | 6 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 1852 | 401,853
74 | 6 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 1854 | 401,855
74 | 6 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 1856 | 401,857
74 | 6 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 1858 | 401,859
74 | 6 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 1860 | 401,861
74 | 6 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 1862 | 401,863
74 | 6 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1864 | 401,865
74 | 6 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1866 | 401,867
74 | 6 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1868 | 401,869
74 | 6 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1870 | 401,871
74 | 6 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1872 | 401,873
74 | 6 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1874 | 401,875
74 | 6 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1876 | 401,877
74 | 6 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1878 | 401,879
74 | 6 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1880 | 401,881
74 | 6 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1882 | 401,883
74 | 6 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1884 | 401,885
74 | 6 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 1886 | 401,887
74 | 6 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 1888 | 401,889
74 | 6 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1890 | 401,891
74 | 6 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1892 | 401,893
74 | 6 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1894 | 401,895
74 | 6 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 1896 | 401,897
74 | 6 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 1898 | 401,899
74 | 6 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1900 | 401,901
74 | 6 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1902 | 401,903
74 | 6 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1904 | 401,905
74 | 6 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 1906 | 401,907
74 | 6 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 1908 | 401,909
74 | 6 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 1914 | 401,915
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52720 | 452,721
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52721 | 452,722
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52722 | 452,723
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52723 | 452,724
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52724 | 452,725
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52725 | 452,726
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52726 | 452,727
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52727 | 452,728
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52728 | 452,729
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52729 | 452,730
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52730 | 452,731
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52731 | 452,732
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52732 | 452,733
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52733 | 452,734
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52734 | 452,735
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52735 | 452,736
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52736 | 452,737
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52737 | 452,738
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52738 | 452,739
74 | 6 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52739 | 452,740
74 | 6 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 1918 | 401,919
74 | 7 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 1930 | 401,931
74 | 7 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 1932 | 401,933
74 | 7 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 1934 | 401,935
74 | 7 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 1936 | 401,937
74 | 7 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 1938 | 401,939
74 | 7 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 1940 | 401,941
74 | 7 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 1942 | 401,943
74 | 7 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 1944 | 401,945
74 | 7 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 1946 | 401,947
74 | 7 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 1948 | 401,949
74 | 7 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 1950 | 401,951
74 | 7 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 1952 | 401,953
74 | 7 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 1954 | 401,955
74 | 7 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 1956 | 401,957
74 | 7 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 1958 | 401,959
74 | 7 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 1960 | 401,961
74 | 7 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 1962 | 401,963
74 | 7 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1964 | 401,965
74 | 7 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1966 | 401,967
74 | 7 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1968 | 401,969
74 | 7 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1970 | 401,971
74 | 7 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 1972 | 401,973
74 | 7 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1974 | 401,975
74 | 7 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1976 | 401,977
74 | 7 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 1978 | 401,979
74 | 7 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1980 | 401,981
74 | 7 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1982 | 401,983
74 | 7 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1984 | 401,985
74 | 7 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 1986 | 401,987
74 | 7 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 1988 | 401,989
74 | 7 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 1990 | 401,991
74 | 7 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 1992 | 401,993
74 | 7 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 1994 | 401,995
74 | 7 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 1996 | 401,997
74 | 7 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 1998 | 401,999
74 | 7 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2000 | 402,001
74 | 7 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2002 | 402,003
74 | 7 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2004 | 402,005
74 | 7 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 2006 | 402,007
74 | 7 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 2008 | 402,009
74 | 7 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 2014 | 402,015
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52740 | 452,741
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52741 | 452,742
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52742 | 452,743
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52743 | 452,744
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52744 | 452,745
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52745 | 452,746
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52746 | 452,747
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52747 | 452,748
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52748 | 452,749
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52749 | 452,750
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52750 | 452,751
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52751 | 452,752
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52752 | 452,753
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52753 | 452,754
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52754 | 452,755
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52755 | 452,756
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52756 | 452,757
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52757 | 452,758
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52758 | 452,759
74 | 7 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52759 | 452,760
74 | 7 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 2018 | 402,019
74 | 8 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 2030 | 402,031
74 | 8 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 2032 | 402,033
74 | 8 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 2034 | 402,035
74 | 8 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 2036 | 402,037
74 | 8 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 2038 | 402,039
74 | 8 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 2040 | 402,041
74 | 8 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 2042 | 402,043
74 | 8 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 2044 | 402,045
74 | 8 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 2046 | 402,047
74 | 8 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 2048 | 402,049
74 | 8 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 2050 | 402,051
74 | 8 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 2052 | 402,053
74 | 8 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 2054 | 402,055
74 | 8 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 2056 | 402,057
74 | 8 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 2058 | 402,059
74 | 8 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 2060 | 402,061
74 | 8 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 2062 | 402,063
74 | 8 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 2064 | 402,065
74 | 8 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2066 | 402,067
74 | 8 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2068 | 402,069
74 | 8 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2070 | 402,071
74 | 8 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 2072 | 402,073
74 | 8 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2074 | 402,075
74 | 8 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2076 | 402,077
74 | 8 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2078 | 402,079
74 | 8 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2080 | 402,081
74 | 8 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2082 | 402,083
74 | 8 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2084 | 402,085
74 | 8 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 2086 | 402,087
74 | 8 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 2088 | 402,089
74 | 8 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2090 | 402,091
74 | 8 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2092 | 402,093
74 | 8 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2094 | 402,095
74 | 8 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 2096 | 402,097
74 | 8 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 2098 | 402,099
74 | 8 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2100 | 402,101
74 | 8 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2102 | 402,103
74 | 8 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2104 | 402,105
74 | 8 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 2106 | 402,107
74 | 8 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 2108 | 402,109
74 | 8 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 2114 | 402,115
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52760 | 452,761
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52761 | 452,762
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52762 | 452,763
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52763 | 452,764
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52764 | 452,765
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52765 | 452,766
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52766 | 452,767
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52767 | 452,768
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52768 | 452,769
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52769 | 452,770
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52770 | 452,771
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52771 | 452,772
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52772 | 452,773
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52773 | 452,774
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52774 | 452,775
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52775 | 452,776
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52776 | 452,777
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52777 | 452,778
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52778 | 452,779
74 | 8 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52779 | 452,780
74 | 8 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 2118 | 402,119
74 | 9 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 2130 | 402,131
74 | 9 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 2132 | 402,133
74 | 9 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 2134 | 402,135
74 | 9 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 2136 | 402,137
74 | 9 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 2138 | 402,139
74 | 9 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 2140 | 402,141
74 | 9 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 2142 | 402,143
74 | 9 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 2144 | 402,145
74 | 9 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 2146 | 402,147
74 | 9 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 2148 | 402,149
74 | 9 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 2150 | 402,151
74 | 9 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 2152 | 402,153
74 | 9 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 2154 | 402,155
74 | 9 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 2156 | 402,157
74 | 9 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 2158 | 402,159
74 | 9 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 2160 | 402,161
74 | 9 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 2162 | 402,163
74 | 9 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 2164 | 402,165
74 | 9 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2166 | 402,167
74 | 9 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2168 | 402,169
74 | 9 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2170 | 402,171
74 | 9 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 2172 | 402,173
74 | 9 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2174 | 402,175
74 | 9 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2176 | 402,177
74 | 9 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2178 | 402,179
74 | 9 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2180 | 402,181
74 | 9 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2182 | 402,183
74 | 9 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2184 | 402,185
74 | 9 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 2186 | 402,187
74 | 9 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 2188 | 402,189
74 | 9 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2190 | 402,191
74 | 9 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2192 | 402,193
74 | 9 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2194 | 402,195
74 | 9 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 2196 | 402,197
74 | 9 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 2198 | 402,199
74 | 9 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2200 | 402,201
74 | 9 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2202 | 402,203
74 | 9 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2204 | 402,205
74 | 9 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 2206 | 402,207
74 | 9 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 2208 | 402,209
74 | 9 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 2214 | 402,215
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52780 | 452,781
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52781 | 452,782
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52782 | 452,783
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52783 | 452,784
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52784 | 452,785
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52785 | 452,786
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52786 | 452,787
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52787 | 452,788
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52788 | 452,789
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52789 | 452,790
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52790 | 452,791
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52791 | 452,792
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52792 | 452,793
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52793 | 452,794
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52794 | 452,795
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52795 | 452,796
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52796 | 452,797
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52797 | 452,798
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52798 | 452,799
74 | 9 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52799 | 452,800
74 | 9 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 2218 | 402,219
74 | 10 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 2230 | 402,231
74 | 10 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 2232 | 402,233
74 | 10 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 2234 | 402,235
74 | 10 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 2236 | 402,237
74 | 10 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 2238 | 402,239
74 | 10 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 2240 | 402,241
74 | 10 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 2242 | 402,243
74 | 10 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 2244 | 402,245
74 | 10 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 2246 | 402,247
74 | 10 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 2248 | 402,249
74 | 10 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 2250 | 402,251
74 | 10 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 2252 | 402,253
74 | 10 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 2254 | 402,255
74 | 10 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 2256 | 402,257
74 | 10 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 2258 | 402,259
74 | 10 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 2260 | 402,261
74 | 10 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 2262 | 402,263
74 | 10 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 2264 | 402,265
74 | 10 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2266 | 402,267
74 | 10 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2268 | 402,269
74 | 10 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2270 | 402,271
74 | 10 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 2272 | 402,273
74 | 10 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2274 | 402,275
74 | 10 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2276 | 402,277
74 | 10 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2278 | 402,279
74 | 10 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2280 | 402,281
74 | 10 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2282 | 402,283
74 | 10 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2284 | 402,285
74 | 10 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 2286 | 402,287
74 | 10 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 2288 | 402,289
74 | 10 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2290 | 402,291
74 | 10 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2292 | 402,293
74 | 10 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2294 | 402,295
74 | 10 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 2296 | 402,297
74 | 10 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 2298 | 402,299
74 | 10 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2300 | 402,301
74 | 10 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2302 | 402,303
74 | 10 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2304 | 402,305
74 | 10 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 2306 | 402,307
74 | 10 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 2308 | 402,309
74 | 10 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 2314 | 402,315
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52800 | 452,801
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52801 | 452,802
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52802 | 452,803
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52803 | 452,804
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52804 | 452,805
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52805 | 452,806
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52806 | 452,807
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52807 | 452,808
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52808 | 452,809
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52809 | 452,810
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52810 | 452,811
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52811 | 452,812
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52812 | 452,813
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52813 | 452,814
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52814 | 452,815
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52815 | 452,816
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52816 | 452,817
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52817 | 452,818
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52818 | 452,819
74 | 10 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52819 | 452,820
74 | 10 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 2318 | 402,319
74 | 11 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 2330 | 402,331
74 | 11 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 2332 | 402,333
74 | 11 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 2334 | 402,335
74 | 11 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 2336 | 402,337
74 | 11 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 2338 | 402,339
74 | 11 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 2340 | 402,341
74 | 11 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 2342 | 402,343
74 | 11 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 2344 | 402,345
74 | 11 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 2346 | 402,347
74 | 11 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 2348 | 402,349
74 | 11 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 2350 | 402,351
74 | 11 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 2352 | 402,353
74 | 11 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 2354 | 402,355
74 | 11 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 2356 | 402,357
74 | 11 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 2358 | 402,359
74 | 11 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 2360 | 402,361
74 | 11 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 2362 | 402,363
74 | 11 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 2364 | 402,365
74 | 11 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2366 | 402,367
74 | 11 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2368 | 402,369
74 | 11 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2370 | 402,371
74 | 11 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 2372 | 402,373
74 | 11 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2374 | 402,375
74 | 11 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2376 | 402,377
74 | 11 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2378 | 402,379
74 | 11 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2380 | 402,381
74 | 11 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2382 | 402,383
74 | 11 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2384 | 402,385
74 | 11 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 2386 | 402,387
74 | 11 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 2388 | 402,389
74 | 11 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2390 | 402,391
74 | 11 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2392 | 402,393
74 | 11 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2394 | 402,395
74 | 11 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 2396 | 402,397
74 | 11 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 2398 | 402,399
74 | 11 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2400 | 402,401
74 | 11 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2402 | 402,403
74 | 11 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2404 | 402,405
74 | 11 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 2406 | 402,407
74 | 11 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 2408 | 402,409
74 | 11 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 2414 | 402,415
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52820 | 452,821
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52821 | 452,822
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52822 | 452,823
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52823 | 452,824
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52824 | 452,825
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52825 | 452,826
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52826 | 452,827
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52827 | 452,828
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52828 | 452,829
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52829 | 452,830
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52830 | 452,831
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52831 | 452,832
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52832 | 452,833
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52833 | 452,834
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52834 | 452,835
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52835 | 452,836
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52836 | 452,837
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52837 | 452,838
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52838 | 452,839
74 | 11 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52839 | 452,840
74 | 11 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 2418 | 402,419
74 | 12 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 2430 | 402,431
74 | 12 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 2432 | 402,433
74 | 12 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 2434 | 402,435
74 | 12 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 2436 | 402,437
74 | 12 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 2438 | 402,439
74 | 12 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 2440 | 402,441
74 | 12 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 2442 | 402,443
74 | 12 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 2444 | 402,445
74 | 12 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 2446 | 402,447
74 | 12 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 2448 | 402,449
74 | 12 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 2450 | 402,451
74 | 12 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 2452 | 402,453
74 | 12 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 2454 | 402,455
74 | 12 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 2456 | 402,457
74 | 12 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 2458 | 402,459
74 | 12 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 2460 | 402,461
74 | 12 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 2462 | 402,463
74 | 12 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 2464 | 402,465
74 | 12 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2466 | 402,467
74 | 12 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2468 | 402,469
74 | 12 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2470 | 402,471
74 | 12 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 2472 | 402,473
74 | 12 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2474 | 402,475
74 | 12 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2476 | 402,477
74 | 12 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2478 | 402,479
74 | 12 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2480 | 402,481
74 | 12 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2482 | 402,483
74 | 12 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2484 | 402,485
74 | 12 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 2486 | 402,487
74 | 12 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 2488 | 402,489
74 | 12 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2490 | 402,491
74 | 12 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2492 | 402,493
74 | 12 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2494 | 402,495
74 | 12 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 2496 | 402,497
74 | 12 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 2498 | 402,499
74 | 12 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2500 | 402,501
74 | 12 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2502 | 402,503
74 | 12 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2504 | 402,505
74 | 12 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 2506 | 402,507
74 | 12 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 2508 | 402,509
74 | 12 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 2514 | 402,515
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52840 | 452,841
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52841 | 452,842
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52842 | 452,843
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52843 | 452,844
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52844 | 452,845
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52845 | 452,846
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52846 | 452,847
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52847 | 452,848
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52848 | 452,849
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52849 | 452,850
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52850 | 452,851
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52851 | 452,852
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52852 | 452,853
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52853 | 452,854
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52854 | 452,855
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52855 | 452,856
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52856 | 452,857
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52857 | 452,858
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52858 | 452,859
74 | 12 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52859 | 452,860
74 | 12 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 2518 | 402,519
74 | 13 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 2530 | 402,531
74 | 13 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 2532 | 402,533
74 | 13 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 2534 | 402,535
74 | 13 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 2536 | 402,537
74 | 13 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 2538 | 402,539
74 | 13 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 2540 | 402,541
74 | 13 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 2542 | 402,543
74 | 13 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 2544 | 402,545
74 | 13 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 2546 | 402,547
74 | 13 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 2548 | 402,549
74 | 13 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 2550 | 402,551
74 | 13 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 2552 | 402,553
74 | 13 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 2554 | 402,555
74 | 13 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 2556 | 402,557
74 | 13 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 2558 | 402,559
74 | 13 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 2560 | 402,561
74 | 13 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 2562 | 402,563
74 | 13 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 2564 | 402,565
74 | 13 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2566 | 402,567
74 | 13 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2568 | 402,569
74 | 13 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2570 | 402,571
74 | 13 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 2572 | 402,573
74 | 13 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2574 | 402,575
74 | 13 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2576 | 402,577
74 | 13 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2578 | 402,579
74 | 13 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2580 | 402,581
74 | 13 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2582 | 402,583
74 | 13 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2584 | 402,585
74 | 13 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 2586 | 402,587
74 | 13 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 2588 | 402,589
74 | 13 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2590 | 402,591
74 | 13 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2592 | 402,593
74 | 13 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2594 | 402,595
74 | 13 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 2596 | 402,597
74 | 13 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 2598 | 402,599
74 | 13 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2600 | 402,601
74 | 13 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2602 | 402,603
74 | 13 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2604 | 402,605
74 | 13 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 2606 | 402,607
74 | 13 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 2608 | 402,609
74 | 13 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 2614 | 402,615
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52860 | 452,861
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52861 | 452,862
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52862 | 452,863
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52863 | 452,864
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52864 | 452,865
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52865 | 452,866
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52866 | 452,867
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52867 | 452,868
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52868 | 452,869
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52869 | 452,870
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52870 | 452,871
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52871 | 452,872
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52872 | 452,873
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52873 | 452,874
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52874 | 452,875
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52875 | 452,876
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52876 | 452,877
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52877 | 452,878
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52878 | 452,879
74 | 13 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52879 | 452,880
74 | 13 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 2618 | 402,619
74 | 14 | 1 | Alarm | Base | Type | Set whether the alarm trigger is a fixed value or relative to control loop set point. | Off (62), Process Alarm (76), Deviation Alarm (24) | Off (62) | Enumeration | R/W | 2630 | 402,631
74 | 14 | 2 | Alarm | Base | Sides | Set which side or sides will trigger this alarm. | Both (13), High (37), Low (53) | Both (13) | Enumeration | R/W | 2632 | 402,633
74 | 14 | 3 | Alarm | Base | High Set Point | Set high trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 300.0 | IEEE Float | R/W | 2634 | 402,635
74 | 14 | 4 | Alarm | Base | Low Set Point | Set low trip point as an absolute or relative value based on alarm type. | -99,999.0 to 99,999.0 | 32.0 | IEEE Float | R/W | 2636 | 402,637
74 | 14 | 5 | Alarm | Base | Hysteresis | Set the differential that must occur in reading before the alarms will/can be cleared. | 0.001 to 9,999.000 | 1.0 | IEEE Float | R/W | 2638 | 402,639
74 | 14 | 6 | Alarm | Base | Silencing | Set to allow the user to disable an active alarm while alarm condition still exist. | Off (62), On (63) | Off (62) | Enumeration | R/W | 2640 | 402,641
74 | 14 | 7 | Alarm | Base | Latching | Set to self-clear or hold alarm for user to clear once activated. | Non-Latching (60), Latching (49) | Non-Latching (60) | Enumeration | R/W | 2642 | 402,643
74 | 14 | 8 | Alarm | Base | Blocking | Set to prevent alarm from occurring when first alarm condition is met. Once within alarm set points, alarm will arm for next occurrence. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 2644 | 402,645
74 | 14 | 9 | Alarm | Base | Logic | Set the output condition during an alarm. | Close On Alarm (17), Open On Alarm (66) | Close On Alarm (17) | Enumeration | R/W | 2646 | 402,647
74 | 14 | 10 | Alarm | Base | Delay Time | Set the span of time that the alarm will be delayed after the process value exceeds the alarm set point. | 0 to 9,999 | 0 | Unsigned 16-bit | R/W | 2648 | 402,649
74 | 14 | 11 | Alarm | Base | Output Value | Monitor the alarm output value. | On (63), Off (62) |  | Enumeration | R | 2650 | 402,651
74 | 14 | 12 | Alarm | Base | Clear Alarm | Request a latched alarm to be cleared. | Ignore (204), Clear (129) | Ignore (204) | Enumeration | R/W | 2652 | 402,653
74 | 14 | 13 | Alarm | Base | Silence Alarm | Request to silence an alarm while alarm condition is still active. Alarm silencing must be enabled. | Ignore (204), Silence Alarms (108) | Ignore (204) | Enumeration | R/W | 2654 | 402,655
74 | 14 | 14 | Alarm | Base | Alarm State | Monitor alarm state. | Startup (88), None (61), Blocked (12), Alarm Low (8), Alarm High (7), Error (28) | Startup (88) | Enumeration | R | 2656 | 402,657
74 | 14 | 15 | Alarm | Base | Alarm Latched | Monitor if alarm is latched. | No (59), Yes (106) | No (59) | Enumeration | R | 2658 | 402,659
74 | 14 | 16 | Alarm | Base | Alarm Silenced | Monitor if alarm is silenced. | No (59), Yes (106) | No (59) | Enumeration | R | 2660 | 402,661
74 | 14 | 17 | Alarm | Base | Alarm Clearable | Monitor if alarm may be cleared with an alarm request. | No (59), Yes (106) | No (59) | Enumeration | R | 2662 | 402,663
74 | 14 | 18 | Alarm | Base | Alarm Source | Set what source will trigger this alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 2664 | 402,665
74 | 14 | 19 | Alarm | Base | Alarm Source Instance | Set what source instance will trigger this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2666 | 402,667
74 | 14 | 20 | Alarm | Base | Alarm Source Zone | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2668 | 402,669
74 | 14 | 21 | Alarm | Base | Alarm Working Process Value | Monitor the value the alarm is comparing against alarm set points. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2670 | 402,671
74 | 14 | 22 | Alarm | Base | Source Function B | Set what source will be used as a relative value for a deviation alarm. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 2672 | 402,673
74 | 14 | 23 | Alarm | Base | Source Instance B | Set what source instance will be used as a relative value for a deviation alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2674 | 402,675
74 | 14 | 24 | Alarm | Base | Source Zone B | Set what source zone will be used as a relative value for a deviation alarm. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2676 | 402,677
74 | 14 | 25 | Alarm | Base | Source Value B | Monitor the CTR source value. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2678 | 402,679
74 | 14 | 26 | Alarm | Base | Source Function C | Set what source will silence this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2680 | 402,681
74 | 14 | 27 | Alarm | Base | Source Instance C | Set what source instance will silence this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2682 | 402,683
74 | 14 | 28 | Alarm | Base | Source Zone C | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2684 | 402,685
74 | 14 | 29 | Alarm | Base | Source Value C | Monitor the level of the silence source. | On (63), Off (62) |  | Enumeration | R | 2686 | 402,687
74 | 14 | 30 | Alarm | Base | Silence Active Level | Set the level that triggers the alarm silencing. | High (37), Low (53) | High (37) | Enumeration | R/W | 2688 | 402,689
74 | 14 | 31 | Alarm | Base | Source Function D | Set what source will clear this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2690 | 402,691
74 | 14 | 32 | Alarm | Base | Source Instance D | Set what source instance will clear this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2692 | 402,693
74 | 14 | 33 | Alarm | Base | Source Zone D | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2694 | 402,695
74 | 14 | 34 | Alarm | Base | Source Value D | Monitor the level of the clear source. | On (63), Off (62) |  | Enumeration | R | 2696 | 402,697
74 | 14 | 35 | Alarm | Base | Clear Active Level | Set the level that triggers the alarm clearing. | High (37), Low (53) | High (37) | Enumeration | R/W | 2698 | 402,699
74 | 14 | 36 | Alarm | Base | Source Function E | Set what source will disable this alarm. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 2700 | 402,701
74 | 14 | 37 | Alarm | Base | Source Instance E | Set what source instance will disable this alarm. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 2702 | 402,703
74 | 14 | 38 | Alarm | Base | Source Zone E | Set the zone of the function source. 0=inside this module | 0 to 24 | 0 | Unsigned 8-bit | R/W | 2704 | 402,705
74 | 14 | 39 | Alarm | Base | Source Value E | Monitor the level of the disable source. | On (63), Off (62) |  | Enumeration | R | 2706 | 402,707
74 | 14 | 40 | Alarm | Base | Off Active Level | Set the level that triggers the alarm disabling. | High (37), Low (53) | High (37) | Enumeration | R/W | 2708 | 402,709
74 | 14 | 43 | Alarm | Base | Error | Monitor the alarm error status. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 2714 | 402,715
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52880 | 452,881
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52881 | 452,882
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52882 | 452,883
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52883 | 452,884
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52884 | 452,885
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52885 | 452,886
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52886 | 452,887
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52887 | 452,888
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52888 | 452,889
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52889 | 452,890
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52890 | 452,891
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52891 | 452,892
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52892 | 452,893
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52893 | 452,894
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52894 | 452,895
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52895 | 452,896
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52896 | 452,897
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52897 | 452,898
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52898 | 452,899
74 | 14 | 44 | Alarm | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52899 | 452,900
74 | 14 | 45 | Alarm | Base | Display | Set whether alarms are displayed when active. | Off (62), On (63) | On (63) | Enumeration | R/W | 2718 | 402,719
75 | 1 | 1 | Control Loop | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 2730 | 402,731
75 | 1 | 2 | Control Loop | Base | Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 2732 | 402,733
75 | 1 | 3 | Control Loop | Base | Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 2734 | 402,735
75 | 1 | 4 | Control Loop | Base | Integral 1 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2736 | 402,737
75 | 1 | 5 | Control Loop | Base | Derivative 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2738 | 402,739
75 | 1 | 6 | Control Loop | Base | Dead Band | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 2740 | 402,741
75 | 1 | 7 | Control Loop | Base | Heat Proportional Band 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2742 | 402,743
75 | 1 | 8 | Control Loop | Base | On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 2744 | 402,745
75 | 1 | 9 | Control Loop | Base | Cool Proportional Band 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2746 | 402,747
75 | 1 | 10 | Control Loop | Base | On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 2748 | 402,749
75 | 1 | 11 | Control Loop | Base | TRU-TUNE+ Enable | Set to enable or disable the TRU-TUNE+® adaptive tuning feature. | No (59), Yes (106) | No (59) | Enumeration | R/W | 2872 | 402,873
75 | 1 | 12 | Control Loop | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | Enumeration | R/W | 2750 | 402,751
75 | 1 | 13 | Control Loop | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | IEEE Float | R/W | 2752 | 402,753
75 | 1 | 14 | Control Loop | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | Enumeration | R/W | 2754 | 402,755
75 | 1 | 15 | Control Loop | Base | TRU-TUNE+ Band | Set the range, centered on the set point, within which TRU-TUNE+® will be in effect. | 0 to 100 | 0 | Unsigned 16-bit | R/W | 2756 | 402,757
75 | 1 | 16 | Control Loop | Base | TRU-TUNE+ Gain | Set the responsiveness of the TRU-TUNE+® adaptive tuning calculations. | 1 to 6 | 3 | Unsigned 8-bit | R/W | 2758 | 402,759
75 | 1 | 18 | Control Loop | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | Enumeration | R/W | 2760 | 402,761
75 | 1 | 19 | Control Loop | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | Enumeration | R/W | 2762 | 402,763
75 | 1 | 20 | Control Loop | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | Unsigned 16-bit | R/W | 2764 | 402,765
75 | 1 | 21 | Control Loop | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 2766 | 402,767
75 | 1 | 22 | Control Loop | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | Enumeration | R | 2768 | 402,769
75 | 1 | 23 | Control Loop | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 2770 | 402,771
75 | 1 | 24 | Control Loop | Base | Peltier Delay | Set a value that will cause a delay when switching from heat PID mode to cool PID mode. | 0.0 to 5.0 | 0.0 | IEEE Float | R/W | 2772 | 402,773
75 | 1 | 25 | Control Loop | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 2774 | 402,775
75 | 1 | 26 | Control Loop | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 2776 | 402,777
75 | 1 | 27 | Control Loop | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | IEEE Float | R/W | 2778 | 402,779
75 | 1 | 28 | Control Loop | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | IEEE Float | R/W | 2780 | 402,781
75 | 1 | 29 | Control Loop | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | IEEE Float | R/W | 2782 | 402,783
75 | 1 | 30 | Control Loop | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | IEEE Float | R/W | 2784 | 402,785
75 | 1 | 31 | Control Loop | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | IEEE Float | R/W | 2786 | 402,787
75 | 1 | 32 | Control Loop | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 2788 | 402,789
75 | 1 | 33 | Control Loop | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 2790 | 402,791
75 | 1 | 34 | Control Loop | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | IEEE Float | R/W | 2792 | 402,793
75 | 1 | 35 | Control Loop | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 2794 | 402,795
75 | 1 | 36 | Control Loop | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | Enumeration | R/W | 2796 | 402,797
75 | 1 | 37 | Control Loop | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 2798 | 402,799
75 | 1 | 39 | Control Loop | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | Enumeration | R/W | 2800 | 402,801
75 | 1 | 40 | Control Loop | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 2802 | 402,803
75 | 1 | 41 | Control Loop | Base | Heat Power | Monitor the PID heat power. | 0.0 to 100.0 |  | IEEE Float | R | 2804 | 402,805
75 | 1 | 42 | Control Loop | Base | Cool Power | Monitor the PID cool power. | -100.0 to 0.0 |  | IEEE Float | R | 2806 | 402,807
75 | 1 | 43 | Control Loop | Base | Control Loop Output Power | Monitor the PID total power. | -100.0 to 100.0 |  | IEEE Float | R | 2808 | 402,809
75 | 1 | 44 | Control Loop | Base | Closed-Loop Set Point | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2810 | 402,811
75 | 1 | 45 | Control Loop | Base | Open-Loop Working Power | Monitor the set point used by the control loop while in manual mode. | -100.0 to 100.0 |  | IEEE Float | R | 2812 | 402,813
75 | 1 | 46 | Control Loop | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | Enumeration | R | 2814 | 402,815
75 | 1 | 47 | Control Loop | Base | Control Action | Set the control loop action. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | Enumeration | R/W | 2816 | 402,817
75 | 1 | 54 | Control Loop | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | Enumeration | R | 2818 | 402,819
75 | 1 | 66 | Control Loop | Base | Source Value A | Monitor the analog input value used by the control loop while in auto mode. |  |  | IEEE Float | R | 2820 | 402,821
75 | 1 | 70 | Control Loop | Base | Source Value B | Monitor the remote set point value. |  |  | IEEE Float | R | 2876 | 402,877
75 | 1 | 71 | Control Loop | Base | Source Function C | Set the source of remote set point for the control loop. | None (61), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778) | None (61) | Enumeration | R/W | 2822 | 402,823
75 | 1 | 74 | Control Loop | Base | Source Value C | Monitor the set point used by the control loop while a profile is active. |  |  | IEEE Float | R | 2824 | 402,825
75 | 1 | 107 | Control Loop | Base | Profile End Action | Set profile end action for control loop when end step is not specified in profile. | User (100), Off (62), Hold (47) | User (100) | Enumeration | R/W | 2874 | 402,875
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52900 | 452,901
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52901 | 452,902
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52902 | 452,903
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52903 | 452,904
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52904 | 452,905
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52905 | 452,906
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52906 | 452,907
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52907 | 452,908
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52908 | 452,909
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52909 | 452,910
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52910 | 452,911
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52911 | 452,912
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52912 | 452,913
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52913 | 452,914
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52914 | 452,915
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52915 | 452,916
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52916 | 452,917
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52917 | 452,918
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52918 | 452,919
75 | 1 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52919 | 452,920
75 | 1 | 114 | Control Loop | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | Enumeration | R/W | 2826 | 402,827
75 | 1 | 115 | Control Loop | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 2828 | 402,829
75 | 1 | 116 | Control Loop | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 2830 | 402,831
75 | 1 | 117 | Control Loop | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 2832 | 402,833
75 | 1 | 118 | Control Loop | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 2834 | 402,835
75 | 1 | 119 | Control Loop | Base | PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | Unsigned 8-bit | R | 2836 | 402,837
75 | 1 | 120 | Control Loop | Base | Heat Proportional Band 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2838 | 402,839
75 | 1 | 121 | Control Loop | Base | Cool Proportional Band 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2840 | 402,841
75 | 1 | 122 | Control Loop | Base | Integral 2 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2842 | 402,843
75 | 1 | 123 | Control Loop | Base | Derivative 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2844 | 402,845
75 | 1 | 124 | Control Loop | Base | Heat Proportional Band 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2846 | 402,847
75 | 1 | 125 | Control Loop | Base | Cool Proportional Band 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2848 | 402,849
75 | 1 | 126 | Control Loop | Base | Integral 3 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2850 | 402,851
75 | 1 | 127 | Control Loop | Base | Derivative 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2852 | 402,853
75 | 1 | 128 | Control Loop | Base | Heat Proportional Band 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2854 | 402,855
75 | 1 | 129 | Control Loop | Base | Cool Proportional Band 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2856 | 402,857
75 | 1 | 130 | Control Loop | Base | Integral 4 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2858 | 402,859
75 | 1 | 131 | Control Loop | Base | Derivative 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2860 | 402,861
75 | 1 | 132 | Control Loop | Base | Heat Proportional Band 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2862 | 402,863
75 | 1 | 133 | Control Loop | Base | Cool Proportional Band 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2864 | 402,865
75 | 1 | 134 | Control Loop | Base | Integral 5 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2866 | 402,867
75 | 1 | 135 | Control Loop | Base | Derivative 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2868 | 402,869
75 | 1 | 136 | Control Loop | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | Unsigned 8-bit | R/W | 2870 | 402,871
75 | 1 | 137 | Control Loop | Base | Control Loop Control Mode Is Off | Monitor the Control Loop Control Mode is Off. | On (63), Off (62) |  | Enumeration | R | 2878 | 402,879
75 | 1 | 138 | Control Loop | Base | Set Point | Moniotr the closed loop set point. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2880 | 402,881
75 | 2 | 1 | Control Loop | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 2890 | 402,891
75 | 2 | 2 | Control Loop | Base | Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 2892 | 402,893
75 | 2 | 3 | Control Loop | Base | Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 2894 | 402,895
75 | 2 | 4 | Control Loop | Base | Integral 1 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 2896 | 402,897
75 | 2 | 5 | Control Loop | Base | Derivative 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 2898 | 402,899
75 | 2 | 6 | Control Loop | Base | Dead Band | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 2900 | 402,901
75 | 2 | 7 | Control Loop | Base | Heat Proportional Band 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2902 | 402,903
75 | 2 | 8 | Control Loop | Base | On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 2904 | 402,905
75 | 2 | 9 | Control Loop | Base | Cool Proportional Band 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2906 | 402,907
75 | 2 | 10 | Control Loop | Base | On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 2908 | 402,909
75 | 2 | 11 | Control Loop | Base | TRU-TUNE+ Enable | Set to enable or disable the TRU-TUNE+® adaptive tuning feature. | No (59), Yes (106) | No (59) | Enumeration | R/W | 3032 | 403,033
75 | 2 | 12 | Control Loop | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | Enumeration | R/W | 2910 | 402,911
75 | 2 | 13 | Control Loop | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | IEEE Float | R/W | 2912 | 402,913
75 | 2 | 14 | Control Loop | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | Enumeration | R/W | 2914 | 402,915
75 | 2 | 15 | Control Loop | Base | TRU-TUNE+ Band | Set the range, centered on the set point, within which TRU-TUNE+® will be in effect. | 0 to 100 | 0 | Unsigned 16-bit | R/W | 2916 | 402,917
75 | 2 | 16 | Control Loop | Base | TRU-TUNE+ Gain | Set the responsiveness of the TRU-TUNE+® adaptive tuning calculations. | 1 to 6 | 3 | Unsigned 8-bit | R/W | 2918 | 402,919
75 | 2 | 18 | Control Loop | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | Enumeration | R/W | 2920 | 402,921
75 | 2 | 19 | Control Loop | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | Enumeration | R/W | 2922 | 402,923
75 | 2 | 20 | Control Loop | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | Unsigned 16-bit | R/W | 2924 | 402,925
75 | 2 | 21 | Control Loop | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 2926 | 402,927
75 | 2 | 22 | Control Loop | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | Enumeration | R | 2928 | 402,929
75 | 2 | 23 | Control Loop | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 2930 | 402,931
75 | 2 | 24 | Control Loop | Base | Peltier Delay | Set a value that will cause a delay when switching from heat PID mode to cool PID mode. | 0.0 to 5.0 | 0.0 | IEEE Float | R/W | 2932 | 402,933
75 | 2 | 25 | Control Loop | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 2934 | 402,935
75 | 2 | 26 | Control Loop | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 2936 | 402,937
75 | 2 | 27 | Control Loop | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | IEEE Float | R/W | 2938 | 402,939
75 | 2 | 28 | Control Loop | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | IEEE Float | R/W | 2940 | 402,941
75 | 2 | 29 | Control Loop | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | IEEE Float | R/W | 2942 | 402,943
75 | 2 | 30 | Control Loop | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | IEEE Float | R/W | 2944 | 402,945
75 | 2 | 31 | Control Loop | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | IEEE Float | R/W | 2946 | 402,947
75 | 2 | 32 | Control Loop | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 2948 | 402,949
75 | 2 | 33 | Control Loop | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 2950 | 402,951
75 | 2 | 34 | Control Loop | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | IEEE Float | R/W | 2952 | 402,953
75 | 2 | 35 | Control Loop | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 2954 | 402,955
75 | 2 | 36 | Control Loop | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | Enumeration | R/W | 2956 | 402,957
75 | 2 | 37 | Control Loop | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 2958 | 402,959
75 | 2 | 39 | Control Loop | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | Enumeration | R/W | 2960 | 402,961
75 | 2 | 40 | Control Loop | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 2962 | 402,963
75 | 2 | 41 | Control Loop | Base | Heat Power | Monitor the PID heat power. | 0.0 to 100.0 |  | IEEE Float | R | 2964 | 402,965
75 | 2 | 42 | Control Loop | Base | Cool Power | Monitor the PID cool power. | -100.0 to 0.0 |  | IEEE Float | R | 2966 | 402,967
75 | 2 | 43 | Control Loop | Base | Control Loop Output Power | Monitor the PID total power. | -100.0 to 100.0 |  | IEEE Float | R | 2968 | 402,969
75 | 2 | 44 | Control Loop | Base | Closed-Loop Set Point | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 2970 | 402,971
75 | 2 | 45 | Control Loop | Base | Open-Loop Working Power | Monitor the set point used by the control loop while in manual mode. | -100.0 to 100.0 |  | IEEE Float | R | 2972 | 402,973
75 | 2 | 46 | Control Loop | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | Enumeration | R | 2974 | 402,975
75 | 2 | 47 | Control Loop | Base | Control Action | Set the control loop action. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | Enumeration | R/W | 2976 | 402,977
75 | 2 | 54 | Control Loop | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | Enumeration | R | 2978 | 402,979
75 | 2 | 66 | Control Loop | Base | Source Value A | Monitor the analog input value used by the control loop while in auto mode. |  |  | IEEE Float | R | 2980 | 402,981
75 | 2 | 70 | Control Loop | Base | Source Value B | Monitor the remote set point value. |  |  | IEEE Float | R | 3036 | 403,037
75 | 2 | 71 | Control Loop | Base | Source Function C | Set the source of remote set point for the control loop. | None (61), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778) | None (61) | Enumeration | R/W | 2982 | 402,983
75 | 2 | 74 | Control Loop | Base | Source Value C | Monitor the set point used by the control loop while a profile is active. |  |  | IEEE Float | R | 2984 | 402,985
75 | 2 | 107 | Control Loop | Base | Profile End Action | Set profile end action for control loop when end step is not specified in profile. | User (100), Off (62), Hold (47) | User (100) | Enumeration | R/W | 3034 | 403,035
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52920 | 452,921
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52921 | 452,922
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52922 | 452,923
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52923 | 452,924
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52924 | 452,925
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52925 | 452,926
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52926 | 452,927
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52927 | 452,928
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52928 | 452,929
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52929 | 452,930
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52930 | 452,931
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52931 | 452,932
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52932 | 452,933
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52933 | 452,934
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52934 | 452,935
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52935 | 452,936
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52936 | 452,937
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52937 | 452,938
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52938 | 452,939
75 | 2 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52939 | 452,940
75 | 2 | 114 | Control Loop | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | Enumeration | R/W | 2986 | 402,987
75 | 2 | 115 | Control Loop | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 2988 | 402,989
75 | 2 | 116 | Control Loop | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 2990 | 402,991
75 | 2 | 117 | Control Loop | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 2992 | 402,993
75 | 2 | 118 | Control Loop | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 2994 | 402,995
75 | 2 | 119 | Control Loop | Base | PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | Unsigned 8-bit | R | 2996 | 402,997
75 | 2 | 120 | Control Loop | Base | Heat Proportional Band 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 2998 | 402,999
75 | 2 | 121 | Control Loop | Base | Cool Proportional Band 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3000 | 403,001
75 | 2 | 122 | Control Loop | Base | Integral 2 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 3002 | 403,003
75 | 2 | 123 | Control Loop | Base | Derivative 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 3004 | 403,005
75 | 2 | 124 | Control Loop | Base | Heat Proportional Band 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3006 | 403,007
75 | 2 | 125 | Control Loop | Base | Cool Proportional Band 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3008 | 403,009
75 | 2 | 126 | Control Loop | Base | Integral 3 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 3010 | 403,011
75 | 2 | 127 | Control Loop | Base | Derivative 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 3012 | 403,013
75 | 2 | 128 | Control Loop | Base | Heat Proportional Band 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3014 | 403,015
75 | 2 | 129 | Control Loop | Base | Cool Proportional Band 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3016 | 403,017
75 | 2 | 130 | Control Loop | Base | Integral 4 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 3018 | 403,019
75 | 2 | 131 | Control Loop | Base | Derivative 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 3020 | 403,021
75 | 2 | 132 | Control Loop | Base | Heat Proportional Band 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3022 | 403,023
75 | 2 | 133 | Control Loop | Base | Cool Proportional Band 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3024 | 403,025
75 | 2 | 134 | Control Loop | Base | Integral 5 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 3026 | 403,027
75 | 2 | 135 | Control Loop | Base | Derivative 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 3028 | 403,029
75 | 2 | 136 | Control Loop | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | Unsigned 8-bit | R/W | 3030 | 403,031
75 | 2 | 137 | Control Loop | Base | Control Loop Control Mode Is Off | Monitor the Control Loop Control Mode is Off. | On (63), Off (62) |  | Enumeration | R | 3038 | 403,039
75 | 2 | 138 | Control Loop | Base | Set Point | Monitor the control mode is in Off state. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 3040 | 403,041
75 | 3 | 1 | Control Loop | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 3050 | 403,051
75 | 3 | 2 | Control Loop | Base | Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 3052 | 403,053
75 | 3 | 3 | Control Loop | Base | Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 3054 | 403,055
75 | 3 | 4 | Control Loop | Base | Integral 1 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 3056 | 403,057
75 | 3 | 5 | Control Loop | Base | Derivative 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 3058 | 403,059
75 | 3 | 6 | Control Loop | Base | Dead Band | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 3060 | 403,061
75 | 3 | 7 | Control Loop | Base | Heat Proportional Band 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3062 | 403,063
75 | 3 | 8 | Control Loop | Base | On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 3064 | 403,065
75 | 3 | 9 | Control Loop | Base | Cool Proportional Band 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3066 | 403,067
75 | 3 | 10 | Control Loop | Base | On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 3068 | 403,069
75 | 3 | 11 | Control Loop | Base | TRU-TUNE+ Enable | Set to enable or disable the TRU-TUNE+® adaptive tuning feature. | No (59), Yes (106) | No (59) | Enumeration | R/W | 3192 | 403,193
75 | 3 | 12 | Control Loop | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | Enumeration | R/W | 3070 | 403,071
75 | 3 | 13 | Control Loop | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | IEEE Float | R/W | 3072 | 403,073
75 | 3 | 14 | Control Loop | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | Enumeration | R/W | 3074 | 403,075
75 | 3 | 15 | Control Loop | Base | TRU-TUNE+ Band | Set the range, centered on the set point, within which TRU-TUNE+® will be in effect. | 0 to 100 | 0 | Unsigned 16-bit | R/W | 3076 | 403,077
75 | 3 | 16 | Control Loop | Base | TRU-TUNE+ Gain | Set the responsiveness of the TRU-TUNE+® adaptive tuning calculations. | 1 to 6 | 3 | Unsigned 8-bit | R/W | 3078 | 403,079
75 | 3 | 18 | Control Loop | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | Enumeration | R/W | 3080 | 403,081
75 | 3 | 19 | Control Loop | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | Enumeration | R/W | 3082 | 403,083
75 | 3 | 20 | Control Loop | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | Unsigned 16-bit | R/W | 3084 | 403,085
75 | 3 | 21 | Control Loop | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 3086 | 403,087
75 | 3 | 22 | Control Loop | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | Enumeration | R | 3088 | 403,089
75 | 3 | 23 | Control Loop | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 3090 | 403,091
75 | 3 | 24 | Control Loop | Base | Peltier Delay | Set a value that will cause a delay when switching from heat PID mode to cool PID mode. | 0.0 to 5.0 | 0.0 | IEEE Float | R/W | 3092 | 403,093
75 | 3 | 25 | Control Loop | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 3094 | 403,095
75 | 3 | 26 | Control Loop | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 3096 | 403,097
75 | 3 | 27 | Control Loop | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | IEEE Float | R/W | 3098 | 403,099
75 | 3 | 28 | Control Loop | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | IEEE Float | R/W | 3100 | 403,101
75 | 3 | 29 | Control Loop | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | IEEE Float | R/W | 3102 | 403,103
75 | 3 | 30 | Control Loop | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | IEEE Float | R/W | 3104 | 403,105
75 | 3 | 31 | Control Loop | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | IEEE Float | R/W | 3106 | 403,107
75 | 3 | 32 | Control Loop | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 3108 | 403,109
75 | 3 | 33 | Control Loop | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 3110 | 403,111
75 | 3 | 34 | Control Loop | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | IEEE Float | R/W | 3112 | 403,113
75 | 3 | 35 | Control Loop | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 3114 | 403,115
75 | 3 | 36 | Control Loop | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | Enumeration | R/W | 3116 | 403,117
75 | 3 | 37 | Control Loop | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 3118 | 403,119
75 | 3 | 39 | Control Loop | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | Enumeration | R/W | 3120 | 403,121
75 | 3 | 40 | Control Loop | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 3122 | 403,123
75 | 3 | 41 | Control Loop | Base | Heat Power | Monitor the PID heat power. | 0.0 to 100.0 |  | IEEE Float | R | 3124 | 403,125
75 | 3 | 42 | Control Loop | Base | Cool Power | Monitor the PID cool power. | -100.0 to 0.0 |  | IEEE Float | R | 3126 | 403,127
75 | 3 | 43 | Control Loop | Base | Control Loop Output Power | Monitor the PID total power. | -100.0 to 100.0 |  | IEEE Float | R | 3128 | 403,129
75 | 3 | 44 | Control Loop | Base | Closed-Loop Set Point | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 3130 | 403,131
75 | 3 | 45 | Control Loop | Base | Open-Loop Working Power | Monitor the set point used by the control loop while in manual mode. | -100.0 to 100.0 |  | IEEE Float | R | 3132 | 403,133
75 | 3 | 46 | Control Loop | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | Enumeration | R | 3134 | 403,135
75 | 3 | 47 | Control Loop | Base | Control Action | Set the control loop action. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | Enumeration | R/W | 3136 | 403,137
75 | 3 | 54 | Control Loop | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | Enumeration | R | 3138 | 403,139
75 | 3 | 66 | Control Loop | Base | Source Value A | Monitor the analog input value used by the control loop while in auto mode. |  |  | IEEE Float | R | 3140 | 403,141
75 | 3 | 70 | Control Loop | Base | Source Value B | Monitor the remote set point value. |  |  | IEEE Float | R | 3196 | 403,197
75 | 3 | 71 | Control Loop | Base | Source Function C | Set the source of remote set point for the control loop. | None (61), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778) | None (61) | Enumeration | R/W | 3142 | 403,143
75 | 3 | 74 | Control Loop | Base | Source Value C | Monitor the set point used by the control loop while a profile is active. |  |  | IEEE Float | R | 3144 | 403,145
75 | 3 | 107 | Control Loop | Base | Profile End Action | Set profile end action for control loop when end step is not specified. | User (100), Off (62), Hold (47) | User (100) | Enumeration | R/W | 3194 | 403,195
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52940 | 452,941
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52941 | 452,942
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52942 | 452,943
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52943 | 452,944
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52944 | 452,945
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52945 | 452,946
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52946 | 452,947
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52947 | 452,948
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52948 | 452,949
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52949 | 452,950
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52950 | 452,951
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52951 | 452,952
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52952 | 452,953
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52953 | 452,954
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52954 | 452,955
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52955 | 452,956
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52956 | 452,957
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52957 | 452,958
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52958 | 452,959
75 | 3 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52959 | 452,960
75 | 3 | 114 | Control Loop | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | Enumeration | R/W | 3146 | 403,147
75 | 3 | 115 | Control Loop | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 3148 | 403,149
75 | 3 | 116 | Control Loop | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 3150 | 403,151
75 | 3 | 117 | Control Loop | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 3152 | 403,153
75 | 3 | 118 | Control Loop | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 3154 | 403,155
75 | 3 | 119 | Control Loop | Base | PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | Unsigned 8-bit | R | 3156 | 403,157
75 | 3 | 120 | Control Loop | Base | Heat Proportional Band 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3158 | 403,159
75 | 3 | 121 | Control Loop | Base | Cool Proportional Band 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3160 | 403,161
75 | 3 | 122 | Control Loop | Base | Integral 2 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 3162 | 403,163
75 | 3 | 123 | Control Loop | Base | Derivative 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 3164 | 403,165
75 | 3 | 124 | Control Loop | Base | Heat Proportional Band 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3166 | 403,167
75 | 3 | 125 | Control Loop | Base | Cool Proportional Band 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3168 | 403,169
75 | 3 | 126 | Control Loop | Base | Integral 3 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 3170 | 403,171
75 | 3 | 127 | Control Loop | Base | Derivative 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 3172 | 403,173
75 | 3 | 128 | Control Loop | Base | Heat Proportional Band 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3174 | 403,175
75 | 3 | 129 | Control Loop | Base | Cool Proportional Band 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3176 | 403,177
75 | 3 | 130 | Control Loop | Base | Integral 4 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 3178 | 403,179
75 | 3 | 131 | Control Loop | Base | Derivative 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 3180 | 403,181
75 | 3 | 132 | Control Loop | Base | Heat Proportional Band 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3182 | 403,183
75 | 3 | 133 | Control Loop | Base | Cool Proportional Band 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3184 | 403,185
75 | 3 | 134 | Control Loop | Base | Integral 5 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 3186 | 403,187
75 | 3 | 135 | Control Loop | Base | Derivative 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 3188 | 403,189
75 | 3 | 136 | Control Loop | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | Unsigned 8-bit | R/W | 3190 | 403,191
75 | 3 | 137 | Control Loop | Base | Control Loop Control Mode Is Off | Monitor the Control Loop Control Mode is Off. | On (63), Off (62) |  | Enumeration | R | 3198 | 403,199
75 | 3 | 138 | Control Loop | Base | Set Point | Monitor the control mode is in Off state. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 3200 | 403,201
75 | 4 | 1 | Control Loop | Base | Control Mode | Set the method that this loop will use to control. | Off (62), Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 3210 | 403,211
75 | 4 | 2 | Control Loop | Base | Heat Algorithm | Set the heat control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 3212 | 403,213
75 | 4 | 3 | Control Loop | Base | Cool Algorithm | Set the cool control method. | PID (71), On / Off (64) | PID (71) | Enumeration | R/W | 3214 | 403,215
75 | 4 | 4 | Control Loop | Base | Integral 1 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 3216 | 403,217
75 | 4 | 5 | Control Loop | Base | Derivative 1 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 3218 | 403,219
75 | 4 | 6 | Control Loop | Base | Dead Band | Set the offset to the proportional band. | -1,000.0 to 1,000.0 | 0.0 | IEEE Float | R/W | 3220 | 403,221
75 | 4 | 7 | Control Loop | Base | Heat Proportional Band 1 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3222 | 403,223
75 | 4 | 8 | Control Loop | Base | On/Off Heat Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 3224 | 403,225
75 | 4 | 9 | Control Loop | Base | Cool Proportional Band 1 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3226 | 403,227
75 | 4 | 10 | Control Loop | Base | On/Off Cool Hysteresis | Set the control switching hysteresis for on-off control. | 0.001 to 99,999.0 | 3.0 | IEEE Float | R/W | 3228 | 403,229
75 | 4 | 11 | Control Loop | Base | TRU-TUNE+ Enable | Set to enable or disable the TRU-TUNE+® adaptive tuning feature. | No (59), Yes (106) | No (59) | Enumeration | R/W | 3352 | 403,353
75 | 4 | 12 | Control Loop | Base | Autotune Aggressiveness | Set the aggressiveness of the autotuning calculations. | Under (99), Critical (21), Over (69) | Critical (21) | Enumeration | R/W | 3230 | 403,231
75 | 4 | 13 | Control Loop | Base | Autotune Set Point | Set the set point that the autotune will use, as a percentage of the current set point. | 50.0 to 200.0 | 90.0 | IEEE Float | R/W | 3232 | 403,233
75 | 4 | 14 | Control Loop | Base | Autotune | Set to start an autotune. | No (59), Yes (106) | No (59) | Enumeration | R/W | 3234 | 403,235
75 | 4 | 15 | Control Loop | Base | TRU-TUNE+ Band | Set the range, centered on the set point, within which TRU-TUNE+® will be in effect. | 0 to 100 | 0 | Unsigned 16-bit | R/W | 3236 | 403,237
75 | 4 | 16 | Control Loop | Base | TRU-TUNE+ Gain | Set the responsiveness of the TRU-TUNE+® adaptive tuning calculations. | 1 to 6 | 3 | Unsigned 8-bit | R/W | 3238 | 403,239
75 | 4 | 18 | Control Loop | Base | Cool Output Curve | Set a cool output curve to change the responsiveness of the system. | Off (62), Non-linear curve 1 (214), Non-linear curve 2 (215) | Off (62) | Enumeration | R/W | 3240 | 403,241
75 | 4 | 19 | Control Loop | Base | Open Loop Detect Enable | Set to detect conditions that prevent the process from changing in specified time frame when PID power is at 100%. | No (59), Yes (106) | No (59) | Enumeration | R/W | 3242 | 403,243
75 | 4 | 20 | Control Loop | Base | Open Loop Detect Time | Set detect time used when open loop detect is enabled. | 0 to 9,999 | 240 | Unsigned 16-bit | R/W | 3244 | 403,245
75 | 4 | 21 | Control Loop | Base | Open Loop Detect Deviation | Set a deviation value used when open loop detect is enabled. | -99,999.0 to 99,999.0 | 10.0 | IEEE Float | R/W | 3246 | 403,247
75 | 4 | 22 | Control Loop | Base | Control Loop Error | Monitor open loop status when open loop detect is enabled. | None (61), Open Loop (1274), Reversed Loop (1275) |  | Enumeration | R | 3248 | 403,249
75 | 4 | 23 | Control Loop | Base | Clear Error | Request clear of open loop detect when open loop detect is enabled. | Clear (129), Ignore (204) | Ignore (204) | Enumeration | R/W | 3250 | 403,251
75 | 4 | 24 | Control Loop | Base | Peltier Delay | Set a value that will cause a delay when switching from heat PID mode to cool PID mode. | 0.0 to 5.0 | 0.0 | IEEE Float | R/W | 3252 | 403,253
75 | 4 | 25 | Control Loop | Base | Minimum Set Point | Set the minimum value of the closed loop set point range. | -99,999.0 to 99,999.0 | -99,999.0 | IEEE Float | R/W | 3254 | 403,255
75 | 4 | 26 | Control Loop | Base | Maximum Set Point | Set the maximum value of the closed loop set point range. | -99,999.0 to 99,999.0 | 99,999.0 | IEEE Float | R/W | 3256 | 403,257
75 | 4 | 27 | Control Loop | Base | Minimum Manual Power | Set the minimum value of the open-loop set point range. | -100.0 to 100.0 | -100.0 | IEEE Float | R/W | 3258 | 403,259
75 | 4 | 28 | Control Loop | Base | Maximum Manual Power | Set the maximum value of the open-loop set point range. | -100.0 to 100.0 | 100.0 | IEEE Float | R/W | 3260 | 403,261
75 | 4 | 29 | Control Loop | Base | Set Point | Set the set point that the controller will automatically control to. |  | 75.0 | IEEE Float | R/W | 3262 | 403,263
75 | 4 | 30 | Control Loop | Base | Manual Power | Set a fixed level of output power when in manual (open-loop) mode. |  | 0.0 | IEEE Float | R/W | 3264 | 403,265
75 | 4 | 31 | Control Loop | Base | Idle Set Point | Set a closed loop set point that can be triggered by a digital state. This is a secondary set point enabled. |  | 75.0 | IEEE Float | R/W | 3266 | 403,267
75 | 4 | 32 | Control Loop | Base | Auto-to-Manual Power | Set what the controller outputs will do when the user switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 3268 | 403,269
75 | 4 | 33 | Control Loop | Base | Input Error Power | Set what the controller outputs will do when an input error switches control to manual mode. | Off (62), Bumpless Transfer (14), Fixed Power (33), User (100) | User (100) | Enumeration | R/W | 3270 | 403,271
75 | 4 | 34 | Control Loop | Base | Fixed Power | Set the manual output power level that will take effect if an analog input error failure occurs while Input Error Power is set to Fixed Power or the user switches to Manual Power and Auto-to-Manual is set to Fixed Power. |  | 0.0 | IEEE Float | R/W | 3272 | 403,273
75 | 4 | 35 | Control Loop | Base | Ramp Action | Set when the controller's set point will ramp to the defined end set point. | Off (62), Startup (88), Set Point (85), Both (13) | Off (62) | Enumeration | R/W | 3274 | 403,275
75 | 4 | 36 | Control Loop | Base | Ramp Scale | Set the scale of the ramp rate when ramp action is enabled.. | Hours (39), Minutes (57) | Minutes (57) | Enumeration | R/W | 3276 | 403,277
75 | 4 | 37 | Control Loop | Base | Ramp Rate | Set the ramp rate when ramp action is enabled.. | 0 to 99,999.0 | 1.0 | IEEE Float | R/W | 3278 | 403,279
75 | 4 | 39 | Control Loop | Base | Remote Set Point | Set to enable remote set point. | No (59), Yes (106) | No (59) | Enumeration | R/W | 3280 | 403,281
75 | 4 | 40 | Control Loop | Base | Remote Set Point Type | Set the control mode that remote set point affects. | Auto (10), Manual (54) | Auto (10) | Enumeration | R/W | 3282 | 403,283
75 | 4 | 41 | Control Loop | Base | Heat Power | Monitor the PID heat power. | 0.0 to 100.0 |  | IEEE Float | R | 3284 | 403,285
75 | 4 | 42 | Control Loop | Base | Cool Power | Monitor the PID cool power. | -100.0 to 0.0 |  | IEEE Float | R | 3286 | 403,287
75 | 4 | 43 | Control Loop | Base | Control Loop Output Power | Monitor the PID total power. | -100.0 to 100.0 |  | IEEE Float | R | 3288 | 403,289
75 | 4 | 44 | Control Loop | Base | Closed-Loop Set Point | Monitor the set point used by the control loop while in auto mode. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 3290 | 403,291
75 | 4 | 45 | Control Loop | Base | Open-Loop Working Power | Monitor the set point used by the control loop while in manual mode. | -100.0 to 100.0 |  | IEEE Float | R | 3292 | 403,293
75 | 4 | 46 | Control Loop | Base | Control Mode Active | Monitor the active control mode. | Off (62), Auto (10), Manual (54) |  | Enumeration | R | 3294 | 403,295
75 | 4 | 47 | Control Loop | Base | Control Action | Set the control loop action. | Off (62), Cool (20), Heat (36), Both (13) | Heat (36) | Enumeration | R/W | 3296 | 403,297
75 | 4 | 54 | Control Loop | Base | Autotune Status | Monitor the autotune progress. | Off (62), Waiting For Cross 1+ (119), Waiting For Cross 1- (120), Waiting For Cross 2+ (121), Waiting For Cross 2- (122), Waiting For Cross 3+ (123), Waiting For Cross 3- (150), Measuring Max Peak (151), Measuring Min Peak (152), Calculating (153), Complete (18), Timeout (118) |  | Enumeration | R | 3298 | 403,299
75 | 4 | 66 | Control Loop | Base | Source Value A | Monitor the analog input value used by the control loop while in auto mode. |  |  | IEEE Float | R | 3300 | 403,301
75 | 4 | 70 | Control Loop | Base | Source Value B | Monitor the remote set point value. |  |  | IEEE Float | R | 3356 | 403,357
75 | 4 | 71 | Control Loop | Base | Source Function C | Set the source of remote set point for the control loop. | None (61), Profile Set Point A (1775), Profile Set Point B (1776), Profile Set Point C (1777), Profile Set Point D (1778) | None (61) | Enumeration | R/W | 3302 | 403,303
75 | 4 | 74 | Control Loop | Base | Source Value C | Monitor the set point used by the control loop while a profile is active. |  |  | IEEE Float | R | 3304 | 403,305
75 | 4 | 107 | Control Loop | Base | Profile End Action | Set profile end action for control loop when end step is not specified. | User (100), Off (62), Hold (47) | User (100) | Enumeration | R/W | 3354 | 403,355
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52960 | 452,961
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52961 | 452,962
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52962 | 452,963
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52963 | 452,964
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52964 | 452,965
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52965 | 452,966
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52966 | 452,967
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52967 | 452,968
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52968 | 452,969
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52969 | 452,970
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52970 | 452,971
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52971 | 452,972
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52972 | 452,973
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52973 | 452,974
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52974 | 452,975
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52975 | 452,976
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52976 | 452,977
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52977 | 452,978
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52978 | 452,979
75 | 4 | 113 | Control Loop | Base | Name | Set name assigned to function block. | 1 byte (UTF-8) |  | String | R/W | 52979 | 452,980
75 | 4 | 114 | Control Loop | Base | PID Set Crossover | Set what causes PID crossover for each set. | Process Value (241), Set Point (85) | Process Value (241) | Enumeration | R/W | 3306 | 403,307
75 | 4 | 115 | Control Loop | Base | PID Set 1 to 2 Crossover | Set the value that causes PID set 1 to be replaced by PID set 2. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 3308 | 403,309
75 | 4 | 116 | Control Loop | Base | PID Set 2 to 3 Crossover | Set the value that causes PID set 2 to be replaced by PID set 3. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 3310 | 403,311
75 | 4 | 117 | Control Loop | Base | PID Set 3 to 4 Crossover | Set the value that causes PID set 3 to be replaced by PID set 4. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 3312 | 403,313
75 | 4 | 118 | Control Loop | Base | PID Set 4 to 5 Crossover | Set the value that causes PID set 4 to be replaced by PID set 5. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 3314 | 403,315
75 | 4 | 119 | Control Loop | Base | PID Set Active | Monitor the active PID set utilized. | 1 to 5 |  | Unsigned 8-bit | R | 3316 | 403,317
75 | 4 | 120 | Control Loop | Base | Heat Proportional Band 2 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3318 | 403,319
75 | 4 | 121 | Control Loop | Base | Cool Proportional Band 2 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3320 | 403,321
75 | 4 | 122 | Control Loop | Base | Integral 2 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 3322 | 403,323
75 | 4 | 123 | Control Loop | Base | Derivative 2 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 3324 | 403,325
75 | 4 | 124 | Control Loop | Base | Heat Proportional Band 3 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3326 | 403,327
75 | 4 | 125 | Control Loop | Base | Cool Proportional Band 3 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3328 | 403,329
75 | 4 | 126 | Control Loop | Base | Integral 3 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 3330 | 403,331
75 | 4 | 127 | Control Loop | Base | Derivative 3 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 3332 | 403,333
75 | 4 | 128 | Control Loop | Base | Heat Proportional Band 4 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3334 | 403,335
75 | 4 | 129 | Control Loop | Base | Cool Proportional Band 4 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3336 | 403,337
75 | 4 | 130 | Control Loop | Base | Integral 4 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 3338 | 403,339
75 | 4 | 131 | Control Loop | Base | Derivative 4 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 3340 | 403,341
75 | 4 | 132 | Control Loop | Base | Heat Proportional Band 5 | Set the PID proportional band for the heat outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3342 | 403,343
75 | 4 | 133 | Control Loop | Base | Cool Proportional Band 5 | Set the PID proportional band for the cool outputs. | 0.001 to 99,999.0 | 25.0 | IEEE Float | R/W | 3344 | 403,345
75 | 4 | 134 | Control Loop | Base | Integral 5 | Set the PID integral for the outputs. | 0.0 to 99,999.0 | 180.0 | IEEE Float | R/W | 3346 | 403,347
75 | 4 | 135 | Control Loop | Base | Derivative 5 | Set the PID derivative time for the outputs. | 0.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 3348 | 403,349
75 | 4 | 136 | Control Loop | Base | Number of PID Sets | Set the number of PID set to be used. | 1 to 5 | 1 | Unsigned 8-bit | R/W | 3350 | 403,351
75 | 4 | 137 | Control Loop | Base | Control Loop Control Mode Is Off | Monitor the Control Loop Control Mode is Off. | On (63), Off (62) |  | Enumeration | R | 3358 | 403,359
75 | 4 | 138 | Control Loop | Base | Set Point | Monitor the control mode is in Off state. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 3360 | 403,361
79 | 1 | 1 | Profile | Base | Units | Monitor units applied to PV1 receiver of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | Enumeration | R | 16536 | 416,537
79 | 1 | 2 | Profile | Base | Units | Monitor units applied to PV2 receiver of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | Enumeration | R | 16538 | 416,539
79 | 1 | 3 | Profile | Base | Units | Monitor units applied to PV3 receiver of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | Enumeration | R | 16540 | 416,541
79 | 1 | 4 | Profile | Base | Units | Monitor units applied to PV4 receiver of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | Enumeration | R | 16542 | 416,543
79 | 1 | 5 | Profile | Base | Units | Monitor units applied to EVT1 receiver when analog of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | Enumeration | R | 16544 | 416,545
79 | 1 | 6 | Profile | Base | Units | Monitor units applied to EVT2 receiver when analog of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | Enumeration | R | 16546 | 416,547
79 | 1 | 7 | Profile | Base | Units | Monitor units applied to EVT3 receiver when analog of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | Enumeration | R | 16548 | 416,549
79 | 1 | 8 | Profile | Base | Units | Monitor units applied to EVT4 receiver when analog of profile function block. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) |  | Enumeration | R | 16550 | 416,551
79 | 1 | 12 | Profile | Base | Start Profile | Enter Profile number to queue for start or calendar start via Profile Action Request. | 1 to 40 | 1 | Unsigned 16-bit | R/W | 16558 | 416,559
79 | 1 | 13 | Profile | Base | Start Step | Enter Profile Step number to queue for start via Profile Action Request. |  | 1 | Unsigned 16-bit | R/W | 16560 | 416,561
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 16562 | 416,563
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18486 | 418,487
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18488 | 418,489
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18490 | 418,491
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18492 | 418,493
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18494 | 418,495
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18496 | 418,497
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18498 | 418,499
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18500 | 418,501
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18502 | 418,503
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18504 | 418,505
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18506 | 418,507
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18508 | 418,509
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18510 | 418,511
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18512 | 418,513
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18514 | 418,515
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18516 | 418,517
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18518 | 418,519
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18520 | 418,521
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18522 | 418,523
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18524 | 418,525
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18526 | 418,527
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18528 | 418,529
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18530 | 418,531
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18532 | 418,533
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18534 | 418,535
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18536 | 418,537
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18538 | 418,539
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18540 | 418,541
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18542 | 418,543
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18544 | 418,545
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18546 | 418,547
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18548 | 418,549
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18550 | 418,551
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18552 | 418,553
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18554 | 418,555
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18556 | 418,557
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18558 | 418,559
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18560 | 418,561
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18562 | 418,563
79 | 1 | 14 | Profile | Base | Profile Action Request | Start or Calendar Start the profile or step previously queued. | None (61), Start (1782), Calendar Start (1783) | None (61) | Enumeration | R/W | 18564 | 418,565
79 | 1 | 15 | Profile | Base | Profile Action Request | Resume a profile previously paused. | None (61), Resume (147) | None (61) | Enumeration | R/W | 16564 | 416,565
79 | 1 | 16 | Profile | Base | Profile Action Request | Pause running profile or terminate running profile. | None (61), Pause (146), Terminate (148) | None (61) | Enumeration | R/W | 16566 | 416,567
79 | 1 | 17 | Profile | Base | Profile State | Monitor state of profile. | Off (62), Running (149), Pause (146), Not Started (251), Completed Normal (252), Terminated (253), Calendar Start (1783) |  | Enumeration | R | 16568 | 416,569
79 | 1 | 18 | Profile | Base | Minutes | Monitor time remaining in profile (minutes portion). | 0 to 59 |  | Unsigned 8-bit | R | 16570 | 416,571
79 | 1 | 19 | Profile | Base | Hours | Monitor time remaining in profile (hours portion). | 0 to 9,999 |  | Unsigned 16-bit | R | 16572 | 416,573
79 | 1 | 20 | Profile | Base | Power Out Minutes | Set power out time (minutes portion). | 0 to 59 |  | Unsigned 8-bit | R/W | 16574 | 416,575
79 | 1 | 21 | Profile | Base | Power Out Hours | Set power out time (hours portion). | 0 to 99 |  | Unsigned 8-bit | R/W | 16576 | 416,577
79 | 1 | 23 | Profile | Base | Calendar Start Minute | Set Calendar Start time (minutes portion) for this profile. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 16580 | 416,581
79 | 1 | 24 | Profile | Base | Calendar Start Hour | Set Calendar Start time (hours portion) for this profile. | 0 to 23 | 0 | Unsigned 8-bit | R/W | 16582 | 416,583
79 | 1 | 25 | Profile | Base | Calendar Start Day | Set Calendar Start time (day of week portion) for this profile. | Sunday (1565), Monday (1559), Tuesday (1560), Wednesday (1561), Thursday (1562), Friday (1563), Saturday (1564) | Monday (1559) | Enumeration | R/W | 16584 | 416,585
79 | 1 | 27 | Profile | Base | Current Profile | Monitor current file loaded in memory. | 0 to 40 | 1 | Unsigned 16-bit | R | 16588 | 416,589
79 | 1 | 28 | Profile | Base | Current Step | Monitor current step loaded in memory. |  | 1 | Unsigned 16-bit | R | 16590 | 416,591
79 | 1 | 29 | Profile | Base | Step Type | Monitor current step type loaded in memory. | Soak (87), Wait For (1542), Instant Change (1927), Jump (116), Ramp Time (1928), Ramp Rate (81), End (27) |  | Enumeration | R | 16592 | 416,593
79 | 1 | 30 | Profile | Base | Event 1 | Monitor/change current step Event Output 1 transmitter (ENT1) loaded in memory. | Off (62), On (63) | Off (62) | Enumeration | R/W | 16594 | 416,595
79 | 1 | 31 | Profile | Base | Event 2 | Monitor/change current step Event Output 2 transmitter (ENT2) loaded in memory. | Off (62), On (63) | Off (62) | Enumeration | R/W | 16596 | 416,597
79 | 1 | 32 | Profile | Base | Event 3 | Monitor/change current step Event Output 3 transmitter (ENT3) loaded in memory. | Off (62), On (63) | Off (62) | Enumeration | R/W | 16598 | 416,599
79 | 1 | 33 | Profile | Base | Event 4 | Monitor/change current step Event Output 4 transmitter (ENT4) loaded in memory. | Off (62), On (63) | Off (62) | Enumeration | R/W | 16600 | 416,601
79 | 1 | 34 | Profile | Base | Target Set Point Loop 1 | Monitor/Set Target Set Point Loop 1 for current step. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 16602 | 416,603
79 | 1 | 35 | Profile | Base | Target Set Point Loop 2 | Monitor/Set Target Set Point Loop 2 for current step. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 16604 | 416,605
79 | 1 | 36 | Profile | Base | Target Set Point Loop 3 | Monitor/Set Target Set Point Loop 3 for current step. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 16606 | 416,607
79 | 1 | 37 | Profile | Base | Target Set Point Loop 4 | Monitor/Set Target Set Point Loop 4 for current step. | -99,999.0 to 99,999.0 |  | IEEE Float | R/W | 16608 | 416,609
79 | 1 | 38 | Profile | Base | Produced Set Point 1 | Monitor Produced Set Point 1 for current step. (SP1) | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R | 16610 | 416,611
79 | 1 | 39 | Profile | Base | Produced Set Point 2 | Monitor Produced Set Point 2 for current step. (SP2) | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R | 16612 | 416,613
79 | 1 | 40 | Profile | Base | Produced Set Point 3 | Monitor Produced Set Point 3 for current step. (SP3) | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R | 16614 | 416,615
79 | 1 | 41 | Profile | Base | Produced Set Point 4 | Monitor Produced Set Point 4 for current step. (SP4) | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R | 16616 | 416,617
79 | 1 | 42 | Profile | Base | Status | Monitor the Wait-for Status, Returns bit values for Event 1, 2, 3 and 4. If condition is met, appropriate bit is 1. Possible returned values are 1 to 16 if all four events inputs are connected. | 0 to 65,535 | 0 | Unsigned 16-bit | R | 16618 | 416,619
79 | 1 | 43 | Profile | Base | Step Time Remaining | Monitor the current total Step Time remaining in seconds. | 0.0 to 3,600,000.0 | 0.0 | IEEE Float | R | 16620 | 416,621
79 | 1 | 44 | Profile | Base | Seconds | Monitor the current Step Time remaining (seconds portion). | 0 to 59 | 0 | Unsigned 8-bit | R/W | 16622 | 416,623
79 | 1 | 45 | Profile | Base | Minutes | Monitor the current total Step Time remaining (minutes portion). | 0 to 59 | 0 | Unsigned 8-bit | R/W | 16624 | 416,625
79 | 1 | 46 | Profile | Base | Hours | Monitor the current total Step Time remaining (hours portion). | 0 to 999 | 0 | Unsigned 16-bit | R/W | 16626 | 416,627
79 | 1 | 53 | Profile | Base | Source Function A | Set source to PV1 receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16640 | 416,641
79 | 1 | 54 | Profile | Base | Source Function B | Set source to PV2 receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16642 | 416,643
79 | 1 | 55 | Profile | Base | Source Function C | Set source to PV3 receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16644 | 416,645
79 | 1 | 56 | Profile | Base | Source Function D | Set source to PV4 receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16646 | 416,647
79 | 1 | 57 | Profile | Base | Source Instance A | Set source instance to PV1 receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16648 | 416,649
79 | 1 | 58 | Profile | Base | Source Instance B | Set source instance to PV2 receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16650 | 416,651
79 | 1 | 59 | Profile | Base | Source Instance C | Set source instance to PV3 receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16652 | 416,653
79 | 1 | 60 | Profile | Base | Source Instance D | Set source instance to PV4 receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16654 | 416,655
79 | 1 | 61 | Profile | Base | Source Zone A | Set source ZONE to PV1 receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16656 | 416,657
79 | 1 | 62 | Profile | Base | Source Zone B | Set source ZONE to PV2 receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16658 | 416,659
79 | 1 | 63 | Profile | Base | Source Zone C | Set source ZONE to PV3 receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16660 | 416,661
79 | 1 | 64 | Profile | Base | Source Zone D | Set source ZONE to PV4 receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16662 | 416,663
79 | 1 | 65 | Profile | Base | Source Value A | Monitor analog source value of PV1 source. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 16664 | 416,665
79 | 1 | 66 | Profile | Base | Source Value B | Monitor analog source value of PV2 source. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 16666 | 416,667
79 | 1 | 67 | Profile | Base | Source Value C | Monitor analog source value of PV3 source. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 16668 | 416,669
79 | 1 | 68 | Profile | Base | Source Value D | Monitor analog source value of PV4 source. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 16670 | 416,671
79 | 1 | 69 | Profile | Base | Source Function A | Set source to EVT1 receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16672 | 416,673
79 | 1 | 70 | Profile | Base | Source Function B | Set source to EVT2 receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16674 | 416,675
79 | 1 | 71 | Profile | Base | Source Function C | Set source to EVT3 receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16676 | 416,677
79 | 1 | 72 | Profile | Base | Source Function D | Set source to EVT4 receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Profile Running (1780), Profile Paused (1781), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16678 | 416,679
79 | 1 | 73 | Profile | Base | Source Instance A | Set source instance to ENT1 receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16680 | 416,681
79 | 1 | 74 | Profile | Base | Source Instance B | Set source instance to ENT2 receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16682 | 416,683
79 | 1 | 75 | Profile | Base | Source Instance C | Set source instance to ENT3 receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16684 | 416,685
79 | 1 | 76 | Profile | Base | Source Instance D | Set source instance to ENT4 receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16686 | 416,687
79 | 1 | 77 | Profile | Base | Source Zone A | Set source zone to ENT1 receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16688 | 416,689
79 | 1 | 78 | Profile | Base | Source Zone B | Set source zone to ENT2 receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16690 | 416,691
79 | 1 | 79 | Profile | Base | Source Zone C | Set source zone to ENT3 receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16692 | 416,693
79 | 1 | 80 | Profile | Base | Source Zone D | Set source zone to ENT4 receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16694 | 416,695
79 | 1 | 81 | Profile | Base | Source Value A | Monitor Wait-for source value applied to EVT1 receiver when digital of profile function block. | On (63), Off (62) | [n/a] | Enumeration | R | 16696 | 416,697
79 | 1 | 82 | Profile | Base | Source Value B | Monitor Wait-for source value applied to EVT2 receiver when digital of profile function block. | On (63), Off (62) | [n/a] | Enumeration | R | 16698 | 416,699
79 | 1 | 83 | Profile | Base | Source Value C | Monitor Wait-for source value applied to EVT3 receiver when digital of profile function block. | On (63), Off (62) | [n/a] | Enumeration | R | 16700 | 416,701
79 | 1 | 84 | Profile | Base | Source Value D | Monitor Wait-for source value applied to EVT4 receiver when digital of profile function block. | On (63), Off (62) | [n/a] | Enumeration | R | 16702 | 416,703
79 | 1 | 85 | Profile | Base | Source Function E | Set source to S/T receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16704 | 416,705
79 | 1 | 86 | Profile | Base | Source Function F | Set source to STRT receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16706 | 416,707
79 | 1 | 87 | Profile | Base | Source Function G | Set source to P/R receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16708 | 416,709
79 | 1 | 88 | Profile | Base | Source Function H | Set source to DIS receiver on profile function block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | Enumeration | R/W | 16710 | 416,711
79 | 1 | 89 | Profile | Base | Source Instance E | Set source instance to S/T receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16712 | 416,713
79 | 1 | 90 | Profile | Base | Source Instance F | Set source instance to STRT receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16714 | 416,715
79 | 1 | 91 | Profile | Base | Source Instance G | Set source instance to P/R receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16716 | 416,717
79 | 1 | 92 | Profile | Base | Source Instance H | Set source instance to DIS receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16718 | 416,719
79 | 1 | 93 | Profile | Base | Source Zone E | Set source zone to S/T receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16720 | 416,721
79 | 1 | 94 | Profile | Base | Source Zone F | Set source zone to STRT receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16722 | 416,723
79 | 1 | 95 | Profile | Base | Source Zone G | Set source zone to P/R receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16724 | 416,725
79 | 1 | 96 | Profile | Base | Source Zone H | Set source zone to DIS receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16726 | 416,727
79 | 1 | 97 | Profile | Base | Source Value E | Monitor source value to S/T receiver on profile function block. | On (63), Off (62) |  | Enumeration | R | 16728 | 416,729
79 | 1 | 98 | Profile | Base | Source Value F | Monitor source value to STRT receiver on profile function block. | On (63), Off (62) |  | Enumeration | R | 16730 | 416,731
79 | 1 | 99 | Profile | Base | Source Value G | Monitor source value to P/R receiver on profile function block. | On (63), Off (62) |  | Enumeration | R | 16732 | 416,733
79 | 1 | 100 | Profile | Base | Source Value H | Monitor source value to DIS receiver on profile function block. | On (63), Off (62) |  | Enumeration | R | 16734 | 416,735
79 | 1 | 101 | Profile | Base | Start / Stop Active Level | Set Active Level for S/T receiver on profile function block. | High (37), Low (53) | High (37) | Enumeration | R/W | 16736 | 416,737
79 | 1 | 102 | Profile | Base | Start Active Level | Set Active Level for STRT receiver on profile function block. | High (37), Low (53) | High (37) | Enumeration | R/W | 16738 | 416,739
79 | 1 | 103 | Profile | Base | Pause / Resume Active Level | Set Active Level for P/R receiver on profile function block. | High (37), Low (53) | High (37) | Enumeration | R/W | 16740 | 416,741
79 | 1 | 104 | Profile | Base | Disable Active Level | Set Active Level for DIS receiver on profile function block. | High (37), Low (53) | High (37) | Enumeration | R/W | 16742 | 416,743
79 | 1 | 105 | Profile | Base | Source Function A | Set source to PRF receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16744 | 416,745
79 | 1 | 106 | Profile | Base | Source Function B | Set source to STP receiver on profile function block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | Enumeration | R/W | 16746 | 416,747
79 | 1 | 107 | Profile | Base | Source Instance A | Set source instance to PRF receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16748 | 416,749
79 | 1 | 108 | Profile | Base | Source Instance B | Set source instance to STP receiver on profile function block. | 1 to 250 | 1 | Unsigned 8-bit | R/W | 16750 | 416,751
79 | 1 | 109 | Profile | Base | Source Zone A | Set source zone to PRF receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16752 | 416,753
79 | 1 | 110 | Profile | Base | Source Zone B | Set source zone to STP receiver on profile function block. | 0 to 24 | 0 | Unsigned 8-bit | R/W | 16754 | 416,755
79 | 1 | 111 | Profile | Base | Source Value A | Monitor profile number source value to PRF receiver on profile function block. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 16756 | 416,757
79 | 1 | 112 | Profile | Base | Source Value B | Monitor step number source value to STP receiver on profile function block. | -99,999.0 to 99,999.0 |  | IEEE Float | R | 16758 | 416,759
79 | 1 | 113 | Profile | Base | Rate | If step type is rate, monitor/change ramp rate for control loop 1. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 16760 | 416,761
79 | 1 | 114 | Profile | Base | Rate | If step type is rate, monitor/change ramp rate for control loop 2. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 16762 | 416,763
79 | 1 | 115 | Profile | Base | Rate | If step type is rate, monitor/change ramp rate for control loop 3. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 16764 | 416,765
79 | 1 | 116 | Profile | Base | Rate | If step type is rate, monitor/change ramp rate for control loop 4. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 16766 | 416,767
79 | 1 | 117 | Profile | Base | Unknown | Monitor the x location of the Profile block on the canvas. | 0 to 65,535 | 0 | Unsigned 16-bit | R/W | 16768 | 416,769
79 | 1 | 118 | Profile | Base | Unknown | Monitor the y location of the Profile block on the canvas. | 0 to 65,535 | 0 | Unsigned 16-bit | R/W | 16770 | 416,771
79 | 1 | 119 | Profile | Base | Profile Running | Monitor profile running status. | On (63), Off (62) |  | Enumeration | R | 16772 | 416,773
79 | 1 | 120 | Profile | Base | Profile Paused | Monitor profile paused status. | On (63), Off (62) |  | Enumeration | R | 16774 | 416,775
79 | 1 | 125 | Profile | Base | Error | Monitor error status for produced set point 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16784 | 416,785
79 | 1 | 126 | Profile | Base | Error | Monitor error status for produced set point 2. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16786 | 416,787
79 | 1 | 127 | Profile | Base | Error | Monitor error status for produced set point 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16788 | 416,789
79 | 1 | 128 | Profile | Base | Error | Monitor error status for produced set point 1. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16790 | 416,791
79 | 1 | 129 | Profile | Base | Error | Monitor error status for produced event output 1 transmitter (EVT1). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16792 | 416,793
79 | 1 | 130 | Profile | Base | Error | Monitor error status for produced event output 2 transmitter (EVT2). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16794 | 416,795
79 | 1 | 131 | Profile | Base | Error | Monitor error status for produced event output 3 transmitter (EVT3). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16796 | 416,797
79 | 1 | 132 | Profile | Base | Error | Monitor error status for produced event output 4 transmitter (EVT4). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16798 | 416,799
79 | 1 | 133 | Profile | Base | Error | Monitor error status for profile running. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16800 | 416,801
79 | 1 | 134 | Profile | Base | Error | Monitor error status for profile paused. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16802 | 416,803
79 | 1 | 135 | Profile | Base | Error | Monitor error status for current profile. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16804 | 416,805
79 | 1 | 136 | Profile | Base | Error | Monitor error status for current profile step. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16806 | 416,807
79 | 1 | 137 | Profile | Base | Unknown | Monitor control loop 1 precision. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) |  | Enumeration | R | 16808 | 416,809
79 | 1 | 138 | Profile | Base | Unknown | Monitor control loop 2 precision. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) |  | Enumeration | R | 16810 | 416,811
79 | 1 | 139 | Profile | Base | Unknown | Monitor control loop 3 precision. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) |  | Enumeration | R | 16812 | 416,813
79 | 1 | 140 | Profile | Base | Unknown | Monitor control loop 4 precision. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) |  | Enumeration | R | 16814 | 416,815
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18566 | 418,567
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18567 | 418,568
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18568 | 418,569
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18569 | 418,570
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18570 | 418,571
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18571 | 418,572
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18572 | 418,573
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18573 | 418,574
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18574 | 418,575
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18575 | 418,576
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18576 | 418,577
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18577 | 418,578
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18578 | 418,579
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18579 | 418,580
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18580 | 418,581
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18581 | 418,582
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18582 | 418,583
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18583 | 418,584
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18584 | 418,585
79 | 1 | 141 | Profile | Base | Name | Monitor profile name. | 1 byte (UTF-8) |  | String | R | 18585 | 418,586
79 | 1 | 142 | Profile | Base | Profile State | Monitor the profile status. | Off (62), Running (149), Pause (146), Not Started (251), Completed Normal (252), Terminated (253), Calendar Start (1783) | Off (62) | Enumeration | R | 16818 | 416,819
79 | 1 | 143 | Profile | Base |  | Monitor the number of steps for profile loaded in memory. | 0 to 50 | 0 | Unsigned 16-bit | R | 16820 | 416,821
79 | 1 | 144 | Profile | Base | Event 5 | Monitor/change current step Event Output 5 transmitter (EVT5) loaded in memory. | Off (62), On (63) | Off (62) | Enumeration | R/W | 16822 | 416,823
79 | 1 | 145 | Profile | Base | Event 6 | Monitor/change current step Event Output 6 transmitter (EVT6) loaded in memory. | Off (62), On (63) | Off (62) | Enumeration | R/W | 16824 | 416,825
79 | 1 | 146 | Profile | Base | Event 7 | Monitor/change current step Event Output 7 transmitter (EVT7) loaded in memory. | Off (62), On (63) | Off (62) | Enumeration | R/W | 16826 | 416,827
79 | 1 | 147 | Profile | Base | Event 8 | Monitor/change current step Event Output 8 transmitter (EVT8) loaded in memory. | Off (62), On (63) | Off (62) | Enumeration | R/W | 16828 | 416,829
79 | 1 | 152 | Profile | Base | Error | Monitor error status for produced Event Output 5 transmitter (EVT5). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16838 | 416,839
79 | 1 | 153 | Profile | Base | Error | Monitor error status for produced Event Output 6 transmitter (EVT6). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16840 | 416,841
79 | 1 | 154 | Profile | Base | Error | Monitor error status for produced Event Output 7 transmitter (EVT7). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16842 | 416,843
79 | 1 | 155 | Profile | Base | Error | Monitor error status for produced Event Output 8 transmitter (EVT8). | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | Enumeration | R | 16844 | 416,845
80 | 0 | 0 | Profile | Base |  | Profile Active Attribute Enable. |  |  |  |  | 18646 | 418,647
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48000 | 448,001
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48002 | 448,003
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48004 | 448,005
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48006 | 448,007
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48008 | 448,009
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48010 | 448,011
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48012 | 448,013
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48014 | 448,015
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48016 | 448,017
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48018 | 448,019
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48020 | 448,021
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48022 | 448,023
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48024 | 448,025
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48026 | 448,027
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48028 | 448,029
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48030 | 448,031
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48032 | 448,033
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48034 | 448,035
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48036 | 448,037
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48038 | 448,039
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48040 | 448,041
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48042 | 448,043
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48044 | 448,045
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48046 | 448,047
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48048 | 448,049
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48050 | 448,051
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48052 | 448,053
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48054 | 448,055
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48056 | 448,057
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48058 | 448,059
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48060 | 448,061
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48062 | 448,063
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48064 | 448,065
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48066 | 448,067
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48068 | 448,069
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48070 | 448,071
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48072 | 448,073
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48074 | 448,075
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48076 | 448,077
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48078 | 448,079
80 | 1 | 1 | Profile | Base |  | Monitor to determine where each profile is located in memory. | 1 to 40 |  | List of Ints | R | 48080 | 448,081
80 | 1 | 2 | Profile | Base | Profile Number | Set the profile number to work with. | 1 to 40 | 1 | Unsigned 16-bit | R/W | 18888 | 418,889
80 | 1 | 3 | Profile | Base | Profile Action Request | Set the profile edit action. | Edit (1770), Add (1375), Delete (1772) | Edit (1770) | Enumeration | R/W | 18890 | 418,891
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16886 | 416,887
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16887 | 416,888
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16888 | 416,889
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16889 | 416,890
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16890 | 416,891
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16891 | 416,892
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16892 | 416,893
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16893 | 416,894
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16894 | 416,895
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16895 | 416,896
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16896 | 416,897
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16897 | 416,898
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16898 | 416,899
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16899 | 416,900
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16900 | 416,901
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16901 | 416,902
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16902 | 416,903
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16903 | 416,904
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16904 | 416,905
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16905 | 416,906
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16926 | 416,927
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16927 | 416,928
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16928 | 416,929
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16929 | 416,930
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16930 | 416,931
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16931 | 416,932
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16932 | 416,933
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16933 | 416,934
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16934 | 416,935
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16935 | 416,936
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16936 | 416,937
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16937 | 416,938
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16938 | 416,939
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16939 | 416,940
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16940 | 416,941
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16941 | 416,942
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16942 | 416,943
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16943 | 416,944
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16944 | 416,945
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16945 | 416,946
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16966 | 416,967
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16967 | 416,968
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16968 | 416,969
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16969 | 416,970
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16970 | 416,971
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16971 | 416,972
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16972 | 416,973
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16973 | 416,974
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16974 | 416,975
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16975 | 416,976
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16976 | 416,977
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16977 | 416,978
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16978 | 416,979
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16979 | 416,980
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16980 | 416,981
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16981 | 416,982
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16982 | 416,983
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16983 | 416,984
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16984 | 416,985
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 16985 | 416,986
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17006 | 417,007
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17007 | 417,008
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17008 | 417,009
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17009 | 417,010
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17010 | 417,011
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17011 | 417,012
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17012 | 417,013
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17013 | 417,014
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17014 | 417,015
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17015 | 417,016
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17016 | 417,017
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17017 | 417,018
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17018 | 417,019
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17019 | 417,020
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17020 | 417,021
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17021 | 417,022
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17022 | 417,023
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17023 | 417,024
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17024 | 417,025
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17025 | 417,026
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17046 | 417,047
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17047 | 417,048
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17048 | 417,049
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17049 | 417,050
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17050 | 417,051
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17051 | 417,052
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17052 | 417,053
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17053 | 417,054
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17054 | 417,055
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17055 | 417,056
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17056 | 417,057
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17057 | 417,058
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17058 | 417,059
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17059 | 417,060
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17060 | 417,061
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17061 | 417,062
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17062 | 417,063
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17063 | 417,064
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17064 | 417,065
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17065 | 417,066
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17086 | 417,087
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17087 | 417,088
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17088 | 417,089
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17089 | 417,090
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17090 | 417,091
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17091 | 417,092
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17092 | 417,093
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17093 | 417,094
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17094 | 417,095
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17095 | 417,096
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17096 | 417,097
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17097 | 417,098
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17098 | 417,099
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17099 | 417,100
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17100 | 417,101
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17101 | 417,102
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17102 | 417,103
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17103 | 417,104
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17104 | 417,105
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17105 | 417,106
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17126 | 417,127
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17127 | 417,128
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17128 | 417,129
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17129 | 417,130
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17130 | 417,131
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17131 | 417,132
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17132 | 417,133
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17133 | 417,134
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17134 | 417,135
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17135 | 417,136
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17136 | 417,137
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17137 | 417,138
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17138 | 417,139
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17139 | 417,140
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17140 | 417,141
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17141 | 417,142
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17142 | 417,143
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17143 | 417,144
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17144 | 417,145
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17145 | 417,146
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17166 | 417,167
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17167 | 417,168
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17168 | 417,169
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17169 | 417,170
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17170 | 417,171
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17171 | 417,172
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17172 | 417,173
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17173 | 417,174
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17174 | 417,175
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17175 | 417,176
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17176 | 417,177
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17177 | 417,178
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17178 | 417,179
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17179 | 417,180
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17180 | 417,181
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17181 | 417,182
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17182 | 417,183
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17183 | 417,184
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17184 | 417,185
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17185 | 417,186
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17206 | 417,207
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17207 | 417,208
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17208 | 417,209
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17209 | 417,210
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17210 | 417,211
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17211 | 417,212
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17212 | 417,213
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17213 | 417,214
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17214 | 417,215
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17215 | 417,216
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17216 | 417,217
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17217 | 417,218
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17218 | 417,219
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17219 | 417,220
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17220 | 417,221
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17221 | 417,222
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17222 | 417,223
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17223 | 417,224
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17224 | 417,225
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17225 | 417,226
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17246 | 417,247
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17247 | 417,248
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17248 | 417,249
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17249 | 417,250
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17250 | 417,251
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17251 | 417,252
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17252 | 417,253
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17253 | 417,254
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17254 | 417,255
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17255 | 417,256
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17256 | 417,257
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17257 | 417,258
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17258 | 417,259
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17259 | 417,260
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17260 | 417,261
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17261 | 417,262
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17262 | 417,263
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17263 | 417,264
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17264 | 417,265
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17265 | 417,266
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17286 | 417,287
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17287 | 417,288
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17288 | 417,289
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17289 | 417,290
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17290 | 417,291
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17291 | 417,292
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17292 | 417,293
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17293 | 417,294
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17294 | 417,295
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17295 | 417,296
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17296 | 417,297
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17297 | 417,298
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17298 | 417,299
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17299 | 417,300
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17300 | 417,301
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17301 | 417,302
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17302 | 417,303
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17303 | 417,304
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17304 | 417,305
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17305 | 417,306
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17326 | 417,327
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17327 | 417,328
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17328 | 417,329
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17329 | 417,330
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17330 | 417,331
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17331 | 417,332
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17332 | 417,333
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17333 | 417,334
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17334 | 417,335
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17335 | 417,336
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17336 | 417,337
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17337 | 417,338
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17338 | 417,339
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17339 | 417,340
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17340 | 417,341
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17341 | 417,342
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17342 | 417,343
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17343 | 417,344
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17344 | 417,345
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17345 | 417,346
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17366 | 417,367
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17367 | 417,368
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17368 | 417,369
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17369 | 417,370
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17370 | 417,371
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17371 | 417,372
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17372 | 417,373
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17373 | 417,374
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17374 | 417,375
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17375 | 417,376
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17376 | 417,377
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17377 | 417,378
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17378 | 417,379
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17379 | 417,380
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17380 | 417,381
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17381 | 417,382
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17382 | 417,383
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17383 | 417,384
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17384 | 417,385
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17385 | 417,386
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17406 | 417,407
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17407 | 417,408
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17408 | 417,409
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17409 | 417,410
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17410 | 417,411
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17411 | 417,412
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17412 | 417,413
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17413 | 417,414
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17414 | 417,415
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17415 | 417,416
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17416 | 417,417
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17417 | 417,418
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17418 | 417,419
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17419 | 417,420
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17420 | 417,421
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17421 | 417,422
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17422 | 417,423
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17423 | 417,424
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17424 | 417,425
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17425 | 417,426
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17446 | 417,447
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17447 | 417,448
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17448 | 417,449
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17449 | 417,450
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17450 | 417,451
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17451 | 417,452
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17452 | 417,453
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17453 | 417,454
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17454 | 417,455
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17455 | 417,456
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17456 | 417,457
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17457 | 417,458
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17458 | 417,459
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17459 | 417,460
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17460 | 417,461
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17461 | 417,462
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17462 | 417,463
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17463 | 417,464
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17464 | 417,465
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17465 | 417,466
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17486 | 417,487
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17487 | 417,488
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17488 | 417,489
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17489 | 417,490
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17490 | 417,491
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17491 | 417,492
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17492 | 417,493
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17493 | 417,494
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17494 | 417,495
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17495 | 417,496
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17496 | 417,497
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17497 | 417,498
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17498 | 417,499
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17499 | 417,500
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17500 | 417,501
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17501 | 417,502
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17502 | 417,503
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17503 | 417,504
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17504 | 417,505
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17505 | 417,506
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17526 | 417,527
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17527 | 417,528
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17528 | 417,529
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17529 | 417,530
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17530 | 417,531
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17531 | 417,532
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17532 | 417,533
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17533 | 417,534
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17534 | 417,535
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17535 | 417,536
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17536 | 417,537
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17537 | 417,538
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17538 | 417,539
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17539 | 417,540
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17540 | 417,541
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17541 | 417,542
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17542 | 417,543
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17543 | 417,544
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17544 | 417,545
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17545 | 417,546
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17566 | 417,567
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17567 | 417,568
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17568 | 417,569
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17569 | 417,570
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17570 | 417,571
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17571 | 417,572
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17572 | 417,573
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17573 | 417,574
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17574 | 417,575
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17575 | 417,576
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17576 | 417,577
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17577 | 417,578
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17578 | 417,579
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17579 | 417,580
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17580 | 417,581
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17581 | 417,582
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17582 | 417,583
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17583 | 417,584
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17584 | 417,585
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17585 | 417,586
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17606 | 417,607
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17607 | 417,608
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17608 | 417,609
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17609 | 417,610
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17610 | 417,611
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17611 | 417,612
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17612 | 417,613
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17613 | 417,614
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17614 | 417,615
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17615 | 417,616
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17616 | 417,617
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17617 | 417,618
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17618 | 417,619
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17619 | 417,620
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17620 | 417,621
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17621 | 417,622
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17622 | 417,623
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17623 | 417,624
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17624 | 417,625
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17625 | 417,626
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17646 | 417,647
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17647 | 417,648
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17648 | 417,649
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17649 | 417,650
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17650 | 417,651
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17651 | 417,652
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17652 | 417,653
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17653 | 417,654
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17654 | 417,655
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17655 | 417,656
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17656 | 417,657
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17657 | 417,658
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17658 | 417,659
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17659 | 417,660
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17660 | 417,661
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17661 | 417,662
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17662 | 417,663
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17663 | 417,664
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17664 | 417,665
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17665 | 417,666
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17686 | 417,687
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17687 | 417,688
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17688 | 417,689
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17689 | 417,690
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17690 | 417,691
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17691 | 417,692
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17692 | 417,693
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17693 | 417,694
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17694 | 417,695
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17695 | 417,696
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17696 | 417,697
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17697 | 417,698
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17698 | 417,699
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17699 | 417,700
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17700 | 417,701
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17701 | 417,702
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17702 | 417,703
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17703 | 417,704
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17704 | 417,705
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17705 | 417,706
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17726 | 417,727
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17727 | 417,728
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17728 | 417,729
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17729 | 417,730
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17730 | 417,731
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17731 | 417,732
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17732 | 417,733
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17733 | 417,734
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17734 | 417,735
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17735 | 417,736
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17736 | 417,737
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17737 | 417,738
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17738 | 417,739
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17739 | 417,740
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17740 | 417,741
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17741 | 417,742
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17742 | 417,743
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17743 | 417,744
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17744 | 417,745
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17745 | 417,746
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17766 | 417,767
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17767 | 417,768
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17768 | 417,769
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17769 | 417,770
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17770 | 417,771
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17771 | 417,772
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17772 | 417,773
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17773 | 417,774
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17774 | 417,775
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17775 | 417,776
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17776 | 417,777
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17777 | 417,778
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17778 | 417,779
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17779 | 417,780
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17780 | 417,781
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17781 | 417,782
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17782 | 417,783
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17783 | 417,784
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17784 | 417,785
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17785 | 417,786
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17806 | 417,807
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17807 | 417,808
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17808 | 417,809
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17809 | 417,810
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17810 | 417,811
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17811 | 417,812
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17812 | 417,813
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17813 | 417,814
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17814 | 417,815
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17815 | 417,816
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17816 | 417,817
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17817 | 417,818
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17818 | 417,819
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17819 | 417,820
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17820 | 417,821
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17821 | 417,822
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17822 | 417,823
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17823 | 417,824
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17824 | 417,825
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17825 | 417,826
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17846 | 417,847
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17847 | 417,848
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17848 | 417,849
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17849 | 417,850
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17850 | 417,851
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17851 | 417,852
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17852 | 417,853
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17853 | 417,854
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17854 | 417,855
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17855 | 417,856
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17856 | 417,857
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17857 | 417,858
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17858 | 417,859
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17859 | 417,860
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17860 | 417,861
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17861 | 417,862
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17862 | 417,863
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17863 | 417,864
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17864 | 417,865
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17865 | 417,866
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17886 | 417,887
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17887 | 417,888
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17888 | 417,889
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17889 | 417,890
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17890 | 417,891
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17891 | 417,892
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17892 | 417,893
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17893 | 417,894
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17894 | 417,895
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17895 | 417,896
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17896 | 417,897
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17897 | 417,898
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17898 | 417,899
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17899 | 417,900
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17900 | 417,901
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17901 | 417,902
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17902 | 417,903
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17903 | 417,904
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17904 | 417,905
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17905 | 417,906
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17926 | 417,927
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17927 | 417,928
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17928 | 417,929
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17929 | 417,930
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17930 | 417,931
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17931 | 417,932
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17932 | 417,933
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17933 | 417,934
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17934 | 417,935
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17935 | 417,936
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17936 | 417,937
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17937 | 417,938
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17938 | 417,939
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17939 | 417,940
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17940 | 417,941
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17941 | 417,942
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17942 | 417,943
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17943 | 417,944
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17944 | 417,945
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17945 | 417,946
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17966 | 417,967
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17967 | 417,968
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17968 | 417,969
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17969 | 417,970
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17970 | 417,971
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17971 | 417,972
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17972 | 417,973
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17973 | 417,974
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17974 | 417,975
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17975 | 417,976
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17976 | 417,977
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17977 | 417,978
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17978 | 417,979
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17979 | 417,980
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17980 | 417,981
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17981 | 417,982
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17982 | 417,983
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17983 | 417,984
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17984 | 417,985
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 17985 | 417,986
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18006 | 418,007
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18007 | 418,008
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18008 | 418,009
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18009 | 418,010
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18010 | 418,011
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18011 | 418,012
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18012 | 418,013
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18013 | 418,014
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18014 | 418,015
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18015 | 418,016
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18016 | 418,017
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18017 | 418,018
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18018 | 418,019
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18019 | 418,020
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18020 | 418,021
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18021 | 418,022
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18022 | 418,023
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18023 | 418,024
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18024 | 418,025
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18025 | 418,026
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18046 | 418,047
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18047 | 418,048
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18048 | 418,049
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18049 | 418,050
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18050 | 418,051
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18051 | 418,052
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18052 | 418,053
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18053 | 418,054
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18054 | 418,055
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18055 | 418,056
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18056 | 418,057
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18057 | 418,058
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18058 | 418,059
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18059 | 418,060
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18060 | 418,061
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18061 | 418,062
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18062 | 418,063
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18063 | 418,064
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18064 | 418,065
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18065 | 418,066
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18086 | 418,087
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18087 | 418,088
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18088 | 418,089
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18089 | 418,090
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18090 | 418,091
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18091 | 418,092
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18092 | 418,093
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18093 | 418,094
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18094 | 418,095
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18095 | 418,096
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18096 | 418,097
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18097 | 418,098
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18098 | 418,099
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18099 | 418,100
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18100 | 418,101
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18101 | 418,102
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18102 | 418,103
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18103 | 418,104
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18104 | 418,105
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18105 | 418,106
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18126 | 418,127
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18127 | 418,128
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18128 | 418,129
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18129 | 418,130
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18130 | 418,131
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18131 | 418,132
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18132 | 418,133
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18133 | 418,134
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18134 | 418,135
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18135 | 418,136
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18136 | 418,137
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18137 | 418,138
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18138 | 418,139
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18139 | 418,140
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18140 | 418,141
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18141 | 418,142
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18142 | 418,143
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18143 | 418,144
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18144 | 418,145
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18145 | 418,146
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18166 | 418,167
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18167 | 418,168
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18168 | 418,169
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18169 | 418,170
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18170 | 418,171
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18171 | 418,172
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18172 | 418,173
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18173 | 418,174
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18174 | 418,175
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18175 | 418,176
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18176 | 418,177
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18177 | 418,178
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18178 | 418,179
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18179 | 418,180
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18180 | 418,181
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18181 | 418,182
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18182 | 418,183
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18183 | 418,184
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18184 | 418,185
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18185 | 418,186
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18206 | 418,207
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18207 | 418,208
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18208 | 418,209
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18209 | 418,210
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18210 | 418,211
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18211 | 418,212
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18212 | 418,213
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18213 | 418,214
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18214 | 418,215
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18215 | 418,216
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18216 | 418,217
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18217 | 418,218
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18218 | 418,219
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18219 | 418,220
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18220 | 418,221
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18221 | 418,222
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18222 | 418,223
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18223 | 418,224
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18224 | 418,225
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18225 | 418,226
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18246 | 418,247
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18247 | 418,248
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18248 | 418,249
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18249 | 418,250
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18250 | 418,251
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18251 | 418,252
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18252 | 418,253
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18253 | 418,254
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18254 | 418,255
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18255 | 418,256
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18256 | 418,257
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18257 | 418,258
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18258 | 418,259
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18259 | 418,260
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18260 | 418,261
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18261 | 418,262
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18262 | 418,263
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18263 | 418,264
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18264 | 418,265
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18265 | 418,266
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18286 | 418,287
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18287 | 418,288
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18288 | 418,289
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18289 | 418,290
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18290 | 418,291
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18291 | 418,292
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18292 | 418,293
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18293 | 418,294
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18294 | 418,295
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18295 | 418,296
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18296 | 418,297
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18297 | 418,298
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18298 | 418,299
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18299 | 418,300
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18300 | 418,301
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18301 | 418,302
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18302 | 418,303
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18303 | 418,304
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18304 | 418,305
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18305 | 418,306
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18326 | 418,327
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18327 | 418,328
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18328 | 418,329
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18329 | 418,330
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18330 | 418,331
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18331 | 418,332
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18332 | 418,333
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18333 | 418,334
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18334 | 418,335
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18335 | 418,336
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18336 | 418,337
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18337 | 418,338
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18338 | 418,339
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18339 | 418,340
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18340 | 418,341
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18341 | 418,342
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18342 | 418,343
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18343 | 418,344
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18344 | 418,345
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18345 | 418,346
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18366 | 418,367
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18367 | 418,368
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18368 | 418,369
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18369 | 418,370
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18370 | 418,371
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18371 | 418,372
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18372 | 418,373
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18373 | 418,374
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18374 | 418,375
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18375 | 418,376
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18376 | 418,377
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18377 | 418,378
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18378 | 418,379
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18379 | 418,380
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18380 | 418,381
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18381 | 418,382
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18382 | 418,383
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18383 | 418,384
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18384 | 418,385
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18385 | 418,386
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18406 | 418,407
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18407 | 418,408
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18408 | 418,409
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18409 | 418,410
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18410 | 418,411
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18411 | 418,412
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18412 | 418,413
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18413 | 418,414
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18414 | 418,415
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18415 | 418,416
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18416 | 418,417
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18417 | 418,418
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18418 | 418,419
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18419 | 418,420
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18420 | 418,421
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18421 | 418,422
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18422 | 418,423
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18423 | 418,424
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18424 | 418,425
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18425 | 418,426
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18446 | 418,447
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18447 | 418,448
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18448 | 418,449
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18449 | 418,450
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18450 | 418,451
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18451 | 418,452
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18452 | 418,453
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18453 | 418,454
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18454 | 418,455
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18455 | 418,456
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18456 | 418,457
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18457 | 418,458
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18458 | 418,459
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18459 | 418,460
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18460 | 418,461
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18461 | 418,462
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18462 | 418,463
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18463 | 418,464
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18464 | 418,465
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18465 | 418,466
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18606 | 418,607
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18607 | 418,608
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18608 | 418,609
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18609 | 418,610
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18610 | 418,611
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18611 | 418,612
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18612 | 418,613
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18613 | 418,614
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18614 | 418,615
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18615 | 418,616
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18616 | 418,617
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18617 | 418,618
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18618 | 418,619
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18619 | 418,620
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18620 | 418,621
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18621 | 418,622
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18622 | 418,623
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18623 | 418,624
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18624 | 418,625
80 | 1 | 4 | Profile | Base | Name | Set the file name. | 1 byte (UTF-8) |  | String | R/W | 18625 | 418,626
80 | 1 | 5 | Profile | Base | Units | Set the units for the control loop. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) | Not Sourced (246) | Enumeration | R/W | 18894 | 418,895
80 | 1 | 6 | Profile | Base | Units | Set the units for the control loop. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) | Not Sourced (246) | Enumeration | R/W | 18896 | 418,897
80 | 1 | 7 | Profile | Base | Units | Set the units for the control loop. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) | Not Sourced (246) | Enumeration | R/W | 18898 | 418,899
80 | 1 | 8 | Profile | Base | Units | Set the units for the control loop. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) | Not Sourced (246) | Enumeration | R/W | 18900 | 418,901
80 | 1 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 18902 | 418,903
80 | 1 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19086 | 419,087
80 | 1 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 18904 | 418,905
80 | 1 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19088 | 419,089
80 | 1 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 18906 | 418,907
80 | 1 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19090 | 419,091
80 | 1 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 18908 | 418,909
80 | 1 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19092 | 419,093
80 | 1 | 14 | Profile | Base | Units | Set the unit used for the wait for steps. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) | Not Sourced (246) | Enumeration | R/W | 18912 | 418,913
80 | 1 | 15 | Profile | Base | Units | Set the unit used for the wait for steps. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) | Not Sourced (246) | Enumeration | R/W | 18914 | 418,915
80 | 1 | 16 | Profile | Base | Units | Set the unit used for the wait for steps. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) | Not Sourced (246) | Enumeration | R/W | 18916 | 418,917
80 | 1 | 17 | Profile | Base | Units | Set the unit used for the wait for steps. | Not Sourced (246), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Relative Humidity (1538), Process (75), Current (22) | Not Sourced (246) | Enumeration | R/W | 18918 | 418,919
80 | 1 | 18 | Profile | Base | Count | Monitor the number of steps for profile loaded in memory. | 1 to 50 | 1 | Unsigned 8-bit | R | 18920 | 418,921
80 | 1 | 19 | Profile | Base |  | Set the step action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 18922 | 418,923
80 | 1 | 19 | Profile | Base |  | Set the step action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 19178 | 419,179
80 | 1 | 20 | Profile | Base | Current Step | Current step. |  | 1 | Unsigned 16-bit | R/W | 18924 | 418,925
80 | 1 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 18926 | 418,927
80 | 1 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 19094 | 419,095
80 | 1 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 18928 | 418,929
80 | 1 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 19096 | 419,097
80 | 1 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 18930 | 418,931
80 | 1 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 19098 | 419,099
80 | 1 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 18932 | 418,933
80 | 1 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 19100 | 419,101
80 | 1 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 18934 | 418,935
80 | 1 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 19102 | 419,103
80 | 1 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 18936 | 418,937
80 | 1 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 19104 | 419,105
80 | 1 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 18938 | 418,939
80 | 1 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19106 | 419,107
80 | 1 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 18940 | 418,941
80 | 1 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19108 | 419,109
80 | 1 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 18942 | 418,943
80 | 1 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19110 | 419,111
80 | 1 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 18944 | 418,945
80 | 1 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19112 | 419,113
80 | 1 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 18946 | 418,947
80 | 1 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19114 | 419,115
80 | 1 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 18948 | 418,949
80 | 1 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19116 | 419,117
80 | 1 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 18950 | 418,951
80 | 1 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19118 | 419,119
80 | 1 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 18952 | 418,953
80 | 1 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19120 | 419,121
80 | 1 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 18954 | 418,955
80 | 1 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19122 | 419,123
80 | 1 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 18956 | 418,957
80 | 1 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19124 | 419,125
80 | 1 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 18958 | 418,959
80 | 1 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19126 | 419,127
80 | 1 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 18960 | 418,961
80 | 1 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19128 | 419,129
80 | 1 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 18962 | 418,963
80 | 1 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19130 | 419,131
80 | 1 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 18964 | 418,965
80 | 1 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19132 | 419,133
80 | 1 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 18966 | 418,967
80 | 1 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19134 | 419,135
80 | 1 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 18968 | 418,969
80 | 1 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19136 | 419,137
80 | 1 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 18970 | 418,971
80 | 1 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19138 | 419,139
80 | 1 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 18972 | 418,973
80 | 1 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19140 | 419,141
80 | 1 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 18974 | 418,975
80 | 1 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19142 | 419,143
80 | 1 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 18976 | 418,977
80 | 1 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19144 | 419,145
80 | 1 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 18978 | 418,979
80 | 1 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19146 | 419,147
80 | 1 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 18980 | 418,981
80 | 1 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19148 | 419,149
80 | 1 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 18982 | 418,983
80 | 1 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19150 | 419,151
80 | 1 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 18984 | 418,985
80 | 1 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19152 | 419,153
80 | 1 | 64 | Profile | Base |  | Monitor to see if profile is available to be Setmed. | Yes (106), No (59) |  | Enumeration | R/W | 19012 | 419,013
80 | 1 | 65 | Profile | Base | Unknown | Set display units. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 19014 | 419,015
80 | 1 | 66 | Profile | Base | Unknown | Set display units. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 19016 | 419,017
80 | 1 | 67 | Profile | Base | Unknown | Set display units. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 19018 | 419,019
80 | 1 | 68 | Profile | Base | Unknown | Set display units. | Digital (1220), Whole (105), Tenths (94), Hundredths (40), Thousandths (96) | Whole (105) | Enumeration | R/W | 19020 | 419,021
80 | 1 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19022 | 419,023
80 | 1 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19162 | 419,163
80 | 1 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19024 | 419,025
80 | 1 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19164 | 419,165
80 | 1 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19026 | 419,027
80 | 1 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19166 | 419,167
80 | 1 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19028 | 419,029
80 | 1 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19168 | 419,169
80 | 1 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19030 | 419,031
80 | 1 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19170 | 419,171
80 | 1 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19032 | 419,033
80 | 1 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19172 | 419,173
80 | 1 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19034 | 419,035
80 | 1 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19174 | 419,175
80 | 1 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19036 | 419,037
80 | 1 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19176 | 419,177
80 | 1 | 77 | Profile | Base | Log Data | Set to enable data log in profile. | No (59), Yes (106) | No (59) | Enumeration | R/W | 19038 | 419,039
80 | 2 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19256 | 419,257
80 | 2 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19258 | 419,259
80 | 2 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19260 | 419,261
80 | 2 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19262 | 419,263
80 | 2 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 19348 | 419,349
80 | 2 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 19264 | 419,265
80 | 2 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 19266 | 419,267
80 | 2 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 19268 | 419,269
80 | 2 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 19270 | 419,271
80 | 2 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 19272 | 419,273
80 | 2 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 19274 | 419,275
80 | 2 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19276 | 419,277
80 | 2 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19278 | 419,279
80 | 2 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19280 | 419,281
80 | 2 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19282 | 419,283
80 | 2 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19284 | 419,285
80 | 2 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19286 | 419,287
80 | 2 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19288 | 419,289
80 | 2 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19290 | 419,291
80 | 2 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19292 | 419,293
80 | 2 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19294 | 419,295
80 | 2 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19296 | 419,297
80 | 2 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19298 | 419,299
80 | 2 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19300 | 419,301
80 | 2 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19302 | 419,303
80 | 2 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19304 | 419,305
80 | 2 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19306 | 419,307
80 | 2 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19308 | 419,309
80 | 2 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19310 | 419,311
80 | 2 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19312 | 419,313
80 | 2 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19314 | 419,315
80 | 2 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19316 | 419,317
80 | 2 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19318 | 419,319
80 | 2 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19320 | 419,321
80 | 2 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19322 | 419,323
80 | 2 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19332 | 419,333
80 | 2 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19334 | 419,335
80 | 2 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19336 | 419,337
80 | 2 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19338 | 419,339
80 | 2 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19340 | 419,341
80 | 2 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19342 | 419,343
80 | 2 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19344 | 419,345
80 | 2 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19346 | 419,347
80 | 3 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19426 | 419,427
80 | 3 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19428 | 419,429
80 | 3 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19430 | 419,431
80 | 3 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19432 | 419,433
80 | 3 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 19518 | 419,519
80 | 3 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 19434 | 419,435
80 | 3 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 19436 | 419,437
80 | 3 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 19438 | 419,439
80 | 3 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 19440 | 419,441
80 | 3 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 19442 | 419,443
80 | 3 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 19444 | 419,445
80 | 3 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19446 | 419,447
80 | 3 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19448 | 419,449
80 | 3 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19450 | 419,451
80 | 3 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19452 | 419,453
80 | 3 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19454 | 419,455
80 | 3 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19456 | 419,457
80 | 3 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19458 | 419,459
80 | 3 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19460 | 419,461
80 | 3 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19462 | 419,463
80 | 3 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19464 | 419,465
80 | 3 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19466 | 419,467
80 | 3 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19468 | 419,469
80 | 3 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19470 | 419,471
80 | 3 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19472 | 419,473
80 | 3 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19474 | 419,475
80 | 3 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19476 | 419,477
80 | 3 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19478 | 419,479
80 | 3 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19480 | 419,481
80 | 3 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19482 | 419,483
80 | 3 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19484 | 419,485
80 | 3 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19486 | 419,487
80 | 3 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19488 | 419,489
80 | 3 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19490 | 419,491
80 | 3 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19492 | 419,493
80 | 3 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19502 | 419,503
80 | 3 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19504 | 419,505
80 | 3 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19506 | 419,507
80 | 3 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19508 | 419,509
80 | 3 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19510 | 419,511
80 | 3 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19512 | 419,513
80 | 3 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19514 | 419,515
80 | 3 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19516 | 419,517
80 | 4 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19596 | 419,597
80 | 4 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19598 | 419,599
80 | 4 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19600 | 419,601
80 | 4 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19602 | 419,603
80 | 4 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 19688 | 419,689
80 | 4 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 19604 | 419,605
80 | 4 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 19606 | 419,607
80 | 4 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 19608 | 419,609
80 | 4 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 19610 | 419,611
80 | 4 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 19612 | 419,613
80 | 4 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 19614 | 419,615
80 | 4 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19616 | 419,617
80 | 4 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19618 | 419,619
80 | 4 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19620 | 419,621
80 | 4 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19622 | 419,623
80 | 4 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19624 | 419,625
80 | 4 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19626 | 419,627
80 | 4 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19628 | 419,629
80 | 4 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19630 | 419,631
80 | 4 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19632 | 419,633
80 | 4 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19634 | 419,635
80 | 4 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19636 | 419,637
80 | 4 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19638 | 419,639
80 | 4 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19640 | 419,641
80 | 4 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19642 | 419,643
80 | 4 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19644 | 419,645
80 | 4 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19646 | 419,647
80 | 4 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19648 | 419,649
80 | 4 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19650 | 419,651
80 | 4 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19652 | 419,653
80 | 4 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19654 | 419,655
80 | 4 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19656 | 419,657
80 | 4 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19658 | 419,659
80 | 4 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19660 | 419,661
80 | 4 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19662 | 419,663
80 | 4 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19672 | 419,673
80 | 4 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19674 | 419,675
80 | 4 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19676 | 419,677
80 | 4 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19678 | 419,679
80 | 4 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19680 | 419,681
80 | 4 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19682 | 419,683
80 | 4 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19684 | 419,685
80 | 4 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19686 | 419,687
80 | 5 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19766 | 419,767
80 | 5 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19768 | 419,769
80 | 5 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19770 | 419,771
80 | 5 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19772 | 419,773
80 | 5 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 19858 | 419,859
80 | 5 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 19774 | 419,775
80 | 5 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 19776 | 419,777
80 | 5 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 19778 | 419,779
80 | 5 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 19780 | 419,781
80 | 5 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 19782 | 419,783
80 | 5 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 19784 | 419,785
80 | 5 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19786 | 419,787
80 | 5 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19788 | 419,789
80 | 5 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19790 | 419,791
80 | 5 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19792 | 419,793
80 | 5 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19794 | 419,795
80 | 5 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19796 | 419,797
80 | 5 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19798 | 419,799
80 | 5 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19800 | 419,801
80 | 5 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19802 | 419,803
80 | 5 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19804 | 419,805
80 | 5 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19806 | 419,807
80 | 5 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19808 | 419,809
80 | 5 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19810 | 419,811
80 | 5 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19812 | 419,813
80 | 5 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19814 | 419,815
80 | 5 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19816 | 419,817
80 | 5 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19818 | 419,819
80 | 5 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19820 | 419,821
80 | 5 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19822 | 419,823
80 | 5 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19824 | 419,825
80 | 5 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19826 | 419,827
80 | 5 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19828 | 419,829
80 | 5 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19830 | 419,831
80 | 5 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19832 | 419,833
80 | 5 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19842 | 419,843
80 | 5 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19844 | 419,845
80 | 5 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19846 | 419,847
80 | 5 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19848 | 419,849
80 | 5 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19850 | 419,851
80 | 5 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19852 | 419,853
80 | 5 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19854 | 419,855
80 | 5 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 19856 | 419,857
80 | 6 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19936 | 419,937
80 | 6 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19938 | 419,939
80 | 6 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19940 | 419,941
80 | 6 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 19942 | 419,943
80 | 6 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 20028 | 420,029
80 | 6 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 19944 | 419,945
80 | 6 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 19946 | 419,947
80 | 6 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 19948 | 419,949
80 | 6 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 19950 | 419,951
80 | 6 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 19952 | 419,953
80 | 6 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 19954 | 419,955
80 | 6 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19956 | 419,957
80 | 6 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19958 | 419,959
80 | 6 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19960 | 419,961
80 | 6 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19962 | 419,963
80 | 6 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19964 | 419,965
80 | 6 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19966 | 419,967
80 | 6 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19968 | 419,969
80 | 6 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 19970 | 419,971
80 | 6 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19972 | 419,973
80 | 6 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19974 | 419,975
80 | 6 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19976 | 419,977
80 | 6 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19978 | 419,979
80 | 6 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19980 | 419,981
80 | 6 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19982 | 419,983
80 | 6 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 19984 | 419,985
80 | 6 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 19986 | 419,987
80 | 6 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19988 | 419,989
80 | 6 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19990 | 419,991
80 | 6 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19992 | 419,993
80 | 6 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 19994 | 419,995
80 | 6 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19996 | 419,997
80 | 6 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 19998 | 419,999
80 | 6 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20000 | 420,001
80 | 6 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20002 | 420,003
80 | 6 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20012 | 420,013
80 | 6 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20014 | 420,015
80 | 6 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20016 | 420,017
80 | 6 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20018 | 420,019
80 | 6 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20020 | 420,021
80 | 6 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20022 | 420,023
80 | 6 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20024 | 420,025
80 | 6 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20026 | 420,027
80 | 7 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20106 | 420,107
80 | 7 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20108 | 420,109
80 | 7 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20110 | 420,111
80 | 7 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20112 | 420,113
80 | 7 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 20198 | 420,199
80 | 7 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 20114 | 420,115
80 | 7 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 20116 | 420,117
80 | 7 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 20118 | 420,119
80 | 7 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 20120 | 420,121
80 | 7 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 20122 | 420,123
80 | 7 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 20124 | 420,125
80 | 7 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20126 | 420,127
80 | 7 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20128 | 420,129
80 | 7 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20130 | 420,131
80 | 7 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20132 | 420,133
80 | 7 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20134 | 420,135
80 | 7 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20136 | 420,137
80 | 7 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20138 | 420,139
80 | 7 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20140 | 420,141
80 | 7 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20142 | 420,143
80 | 7 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20144 | 420,145
80 | 7 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20146 | 420,147
80 | 7 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20148 | 420,149
80 | 7 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20150 | 420,151
80 | 7 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20152 | 420,153
80 | 7 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20154 | 420,155
80 | 7 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20156 | 420,157
80 | 7 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20158 | 420,159
80 | 7 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20160 | 420,161
80 | 7 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20162 | 420,163
80 | 7 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20164 | 420,165
80 | 7 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20166 | 420,167
80 | 7 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20168 | 420,169
80 | 7 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20170 | 420,171
80 | 7 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20172 | 420,173
80 | 7 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20182 | 420,183
80 | 7 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20184 | 420,185
80 | 7 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20186 | 420,187
80 | 7 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20188 | 420,189
80 | 7 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20190 | 420,191
80 | 7 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20192 | 420,193
80 | 7 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20194 | 420,195
80 | 7 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20196 | 420,197
80 | 8 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20276 | 420,277
80 | 8 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20278 | 420,279
80 | 8 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20280 | 420,281
80 | 8 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20282 | 420,283
80 | 8 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 20368 | 420,369
80 | 8 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 20284 | 420,285
80 | 8 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 20286 | 420,287
80 | 8 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 20288 | 420,289
80 | 8 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 20290 | 420,291
80 | 8 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 20292 | 420,293
80 | 8 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 20294 | 420,295
80 | 8 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20296 | 420,297
80 | 8 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20298 | 420,299
80 | 8 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20300 | 420,301
80 | 8 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20302 | 420,303
80 | 8 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20304 | 420,305
80 | 8 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20306 | 420,307
80 | 8 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20308 | 420,309
80 | 8 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20310 | 420,311
80 | 8 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20312 | 420,313
80 | 8 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20314 | 420,315
80 | 8 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20316 | 420,317
80 | 8 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20318 | 420,319
80 | 8 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20320 | 420,321
80 | 8 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20322 | 420,323
80 | 8 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20324 | 420,325
80 | 8 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20326 | 420,327
80 | 8 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20328 | 420,329
80 | 8 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20330 | 420,331
80 | 8 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20332 | 420,333
80 | 8 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20334 | 420,335
80 | 8 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20336 | 420,337
80 | 8 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20338 | 420,339
80 | 8 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20340 | 420,341
80 | 8 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20342 | 420,343
80 | 8 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20352 | 420,353
80 | 8 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20354 | 420,355
80 | 8 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20356 | 420,357
80 | 8 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20358 | 420,359
80 | 8 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20360 | 420,361
80 | 8 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20362 | 420,363
80 | 8 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20364 | 420,365
80 | 8 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20366 | 420,367
80 | 9 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20446 | 420,447
80 | 9 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20448 | 420,449
80 | 9 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20450 | 420,451
80 | 9 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20452 | 420,453
80 | 9 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 20538 | 420,539
80 | 9 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 20454 | 420,455
80 | 9 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 20456 | 420,457
80 | 9 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 20458 | 420,459
80 | 9 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 20460 | 420,461
80 | 9 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 20462 | 420,463
80 | 9 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 20464 | 420,465
80 | 9 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20466 | 420,467
80 | 9 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20468 | 420,469
80 | 9 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20470 | 420,471
80 | 9 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20472 | 420,473
80 | 9 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20474 | 420,475
80 | 9 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20476 | 420,477
80 | 9 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20478 | 420,479
80 | 9 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20480 | 420,481
80 | 9 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20482 | 420,483
80 | 9 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20484 | 420,485
80 | 9 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20486 | 420,487
80 | 9 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20488 | 420,489
80 | 9 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20490 | 420,491
80 | 9 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20492 | 420,493
80 | 9 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20494 | 420,495
80 | 9 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20496 | 420,497
80 | 9 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20498 | 420,499
80 | 9 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20500 | 420,501
80 | 9 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20502 | 420,503
80 | 9 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20504 | 420,505
80 | 9 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20506 | 420,507
80 | 9 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20508 | 420,509
80 | 9 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20510 | 420,511
80 | 9 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20512 | 420,513
80 | 9 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20522 | 420,523
80 | 9 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20524 | 420,525
80 | 9 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20526 | 420,527
80 | 9 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20528 | 420,529
80 | 9 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20530 | 420,531
80 | 9 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20532 | 420,533
80 | 9 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20534 | 420,535
80 | 9 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20536 | 420,537
80 | 10 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20616 | 420,617
80 | 10 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20618 | 420,619
80 | 10 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20620 | 420,621
80 | 10 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20622 | 420,623
80 | 10 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 20708 | 420,709
80 | 10 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 20624 | 420,625
80 | 10 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 20626 | 420,627
80 | 10 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 20628 | 420,629
80 | 10 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 20630 | 420,631
80 | 10 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 20632 | 420,633
80 | 10 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 20634 | 420,635
80 | 10 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20636 | 420,637
80 | 10 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20638 | 420,639
80 | 10 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20640 | 420,641
80 | 10 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20642 | 420,643
80 | 10 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20644 | 420,645
80 | 10 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20646 | 420,647
80 | 10 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20648 | 420,649
80 | 10 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20650 | 420,651
80 | 10 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20652 | 420,653
80 | 10 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20654 | 420,655
80 | 10 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20656 | 420,657
80 | 10 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20658 | 420,659
80 | 10 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20660 | 420,661
80 | 10 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20662 | 420,663
80 | 10 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20664 | 420,665
80 | 10 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20666 | 420,667
80 | 10 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20668 | 420,669
80 | 10 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20670 | 420,671
80 | 10 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20672 | 420,673
80 | 10 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20674 | 420,675
80 | 10 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20676 | 420,677
80 | 10 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20678 | 420,679
80 | 10 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20680 | 420,681
80 | 10 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20682 | 420,683
80 | 10 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20692 | 420,693
80 | 10 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20694 | 420,695
80 | 10 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20696 | 420,697
80 | 10 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20698 | 420,699
80 | 10 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20700 | 420,701
80 | 10 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20702 | 420,703
80 | 10 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20704 | 420,705
80 | 10 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20706 | 420,707
80 | 11 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20786 | 420,787
80 | 11 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20788 | 420,789
80 | 11 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20790 | 420,791
80 | 11 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20792 | 420,793
80 | 11 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 20878 | 420,879
80 | 11 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 20794 | 420,795
80 | 11 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 20796 | 420,797
80 | 11 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 20798 | 420,799
80 | 11 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 20800 | 420,801
80 | 11 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 20802 | 420,803
80 | 11 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 20804 | 420,805
80 | 11 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20806 | 420,807
80 | 11 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20808 | 420,809
80 | 11 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20810 | 420,811
80 | 11 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20812 | 420,813
80 | 11 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20814 | 420,815
80 | 11 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20816 | 420,817
80 | 11 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20818 | 420,819
80 | 11 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20820 | 420,821
80 | 11 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20822 | 420,823
80 | 11 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20824 | 420,825
80 | 11 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20826 | 420,827
80 | 11 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20828 | 420,829
80 | 11 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20830 | 420,831
80 | 11 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20832 | 420,833
80 | 11 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20834 | 420,835
80 | 11 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20836 | 420,837
80 | 11 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20838 | 420,839
80 | 11 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20840 | 420,841
80 | 11 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20842 | 420,843
80 | 11 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 20844 | 420,845
80 | 11 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20846 | 420,847
80 | 11 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20848 | 420,849
80 | 11 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20850 | 420,851
80 | 11 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20852 | 420,853
80 | 11 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20862 | 420,863
80 | 11 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20864 | 420,865
80 | 11 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20866 | 420,867
80 | 11 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 20868 | 420,869
80 | 11 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20870 | 420,871
80 | 11 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20872 | 420,873
80 | 11 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20874 | 420,875
80 | 11 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 20876 | 420,877
80 | 12 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20956 | 420,957
80 | 12 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20958 | 420,959
80 | 12 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20960 | 420,961
80 | 12 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 20962 | 420,963
80 | 12 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 21048 | 421,049
80 | 12 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 20964 | 420,965
80 | 12 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 20966 | 420,967
80 | 12 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 20968 | 420,969
80 | 12 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 20970 | 420,971
80 | 12 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 20972 | 420,973
80 | 12 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 20974 | 420,975
80 | 12 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20976 | 420,977
80 | 12 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20978 | 420,979
80 | 12 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20980 | 420,981
80 | 12 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20982 | 420,983
80 | 12 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20984 | 420,985
80 | 12 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20986 | 420,987
80 | 12 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20988 | 420,989
80 | 12 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 20990 | 420,991
80 | 12 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20992 | 420,993
80 | 12 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20994 | 420,995
80 | 12 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 20996 | 420,997
80 | 12 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 20998 | 420,999
80 | 12 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21000 | 421,001
80 | 12 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21002 | 421,003
80 | 12 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21004 | 421,005
80 | 12 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21006 | 421,007
80 | 12 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21008 | 421,009
80 | 12 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21010 | 421,011
80 | 12 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21012 | 421,013
80 | 12 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21014 | 421,015
80 | 12 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21016 | 421,017
80 | 12 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21018 | 421,019
80 | 12 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21020 | 421,021
80 | 12 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21022 | 421,023
80 | 12 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21032 | 421,033
80 | 12 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21034 | 421,035
80 | 12 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21036 | 421,037
80 | 12 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21038 | 421,039
80 | 12 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21040 | 421,041
80 | 12 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21042 | 421,043
80 | 12 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21044 | 421,045
80 | 12 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21046 | 421,047
80 | 13 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21126 | 421,127
80 | 13 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21128 | 421,129
80 | 13 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21130 | 421,131
80 | 13 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21132 | 421,133
80 | 13 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 21218 | 421,219
80 | 13 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 21134 | 421,135
80 | 13 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 21136 | 421,137
80 | 13 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 21138 | 421,139
80 | 13 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 21140 | 421,141
80 | 13 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 21142 | 421,143
80 | 13 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 21144 | 421,145
80 | 13 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21146 | 421,147
80 | 13 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21148 | 421,149
80 | 13 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21150 | 421,151
80 | 13 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21152 | 421,153
80 | 13 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21154 | 421,155
80 | 13 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21156 | 421,157
80 | 13 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21158 | 421,159
80 | 13 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21160 | 421,161
80 | 13 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21162 | 421,163
80 | 13 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21164 | 421,165
80 | 13 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21166 | 421,167
80 | 13 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21168 | 421,169
80 | 13 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21170 | 421,171
80 | 13 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21172 | 421,173
80 | 13 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21174 | 421,175
80 | 13 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21176 | 421,177
80 | 13 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21178 | 421,179
80 | 13 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21180 | 421,181
80 | 13 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21182 | 421,183
80 | 13 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21184 | 421,185
80 | 13 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21186 | 421,187
80 | 13 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21188 | 421,189
80 | 13 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21190 | 421,191
80 | 13 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21192 | 421,193
80 | 13 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21202 | 421,203
80 | 13 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21204 | 421,205
80 | 13 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21206 | 421,207
80 | 13 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21208 | 421,209
80 | 13 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21210 | 421,211
80 | 13 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21212 | 421,213
80 | 13 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21214 | 421,215
80 | 13 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21216 | 421,217
80 | 14 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21296 | 421,297
80 | 14 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21298 | 421,299
80 | 14 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21300 | 421,301
80 | 14 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21302 | 421,303
80 | 14 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 21388 | 421,389
80 | 14 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 21304 | 421,305
80 | 14 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 21306 | 421,307
80 | 14 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 21308 | 421,309
80 | 14 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 21310 | 421,311
80 | 14 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 21312 | 421,313
80 | 14 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 21314 | 421,315
80 | 14 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21316 | 421,317
80 | 14 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21318 | 421,319
80 | 14 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21320 | 421,321
80 | 14 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21322 | 421,323
80 | 14 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21324 | 421,325
80 | 14 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21326 | 421,327
80 | 14 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21328 | 421,329
80 | 14 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21330 | 421,331
80 | 14 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21332 | 421,333
80 | 14 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21334 | 421,335
80 | 14 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21336 | 421,337
80 | 14 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21338 | 421,339
80 | 14 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21340 | 421,341
80 | 14 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21342 | 421,343
80 | 14 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21344 | 421,345
80 | 14 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21346 | 421,347
80 | 14 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21348 | 421,349
80 | 14 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21350 | 421,351
80 | 14 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21352 | 421,353
80 | 14 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21354 | 421,355
80 | 14 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21356 | 421,357
80 | 14 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21358 | 421,359
80 | 14 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21360 | 421,361
80 | 14 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21362 | 421,363
80 | 14 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21372 | 421,373
80 | 14 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21374 | 421,375
80 | 14 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21376 | 421,377
80 | 14 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21378 | 421,379
80 | 14 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21380 | 421,381
80 | 14 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21382 | 421,383
80 | 14 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21384 | 421,385
80 | 14 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21386 | 421,387
80 | 15 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21466 | 421,467
80 | 15 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21468 | 421,469
80 | 15 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21470 | 421,471
80 | 15 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21472 | 421,473
80 | 15 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 21558 | 421,559
80 | 15 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 21474 | 421,475
80 | 15 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 21476 | 421,477
80 | 15 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 21478 | 421,479
80 | 15 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 21480 | 421,481
80 | 15 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 21482 | 421,483
80 | 15 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 21484 | 421,485
80 | 15 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21486 | 421,487
80 | 15 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21488 | 421,489
80 | 15 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21490 | 421,491
80 | 15 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21492 | 421,493
80 | 15 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21494 | 421,495
80 | 15 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21496 | 421,497
80 | 15 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21498 | 421,499
80 | 15 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21500 | 421,501
80 | 15 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21502 | 421,503
80 | 15 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21504 | 421,505
80 | 15 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21506 | 421,507
80 | 15 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21508 | 421,509
80 | 15 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21510 | 421,511
80 | 15 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21512 | 421,513
80 | 15 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21514 | 421,515
80 | 15 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21516 | 421,517
80 | 15 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21518 | 421,519
80 | 15 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21520 | 421,521
80 | 15 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21522 | 421,523
80 | 15 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21524 | 421,525
80 | 15 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21526 | 421,527
80 | 15 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21528 | 421,529
80 | 15 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21530 | 421,531
80 | 15 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21532 | 421,533
80 | 15 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21542 | 421,543
80 | 15 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21544 | 421,545
80 | 15 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21546 | 421,547
80 | 15 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21548 | 421,549
80 | 15 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21550 | 421,551
80 | 15 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21552 | 421,553
80 | 15 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21554 | 421,555
80 | 15 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21556 | 421,557
80 | 16 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21636 | 421,637
80 | 16 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21638 | 421,639
80 | 16 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21640 | 421,641
80 | 16 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21642 | 421,643
80 | 16 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 21728 | 421,729
80 | 16 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 21644 | 421,645
80 | 16 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 21646 | 421,647
80 | 16 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 21648 | 421,649
80 | 16 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 21650 | 421,651
80 | 16 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 21652 | 421,653
80 | 16 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 21654 | 421,655
80 | 16 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21656 | 421,657
80 | 16 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21658 | 421,659
80 | 16 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21660 | 421,661
80 | 16 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21662 | 421,663
80 | 16 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21664 | 421,665
80 | 16 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21666 | 421,667
80 | 16 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21668 | 421,669
80 | 16 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21670 | 421,671
80 | 16 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21672 | 421,673
80 | 16 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21674 | 421,675
80 | 16 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21676 | 421,677
80 | 16 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21678 | 421,679
80 | 16 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21680 | 421,681
80 | 16 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21682 | 421,683
80 | 16 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21684 | 421,685
80 | 16 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21686 | 421,687
80 | 16 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21688 | 421,689
80 | 16 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21690 | 421,691
80 | 16 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21692 | 421,693
80 | 16 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21694 | 421,695
80 | 16 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21696 | 421,697
80 | 16 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21698 | 421,699
80 | 16 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21700 | 421,701
80 | 16 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21702 | 421,703
80 | 16 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21712 | 421,713
80 | 16 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21714 | 421,715
80 | 16 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21716 | 421,717
80 | 16 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21718 | 421,719
80 | 16 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21720 | 421,721
80 | 16 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21722 | 421,723
80 | 16 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21724 | 421,725
80 | 16 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21726 | 421,727
80 | 17 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21806 | 421,807
80 | 17 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21808 | 421,809
80 | 17 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21810 | 421,811
80 | 17 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21812 | 421,813
80 | 17 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 21898 | 421,899
80 | 17 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 21814 | 421,815
80 | 17 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 21816 | 421,817
80 | 17 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 21818 | 421,819
80 | 17 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 21820 | 421,821
80 | 17 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 21822 | 421,823
80 | 17 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 21824 | 421,825
80 | 17 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21826 | 421,827
80 | 17 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21828 | 421,829
80 | 17 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21830 | 421,831
80 | 17 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21832 | 421,833
80 | 17 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21834 | 421,835
80 | 17 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21836 | 421,837
80 | 17 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21838 | 421,839
80 | 17 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 21840 | 421,841
80 | 17 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21842 | 421,843
80 | 17 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21844 | 421,845
80 | 17 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21846 | 421,847
80 | 17 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21848 | 421,849
80 | 17 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21850 | 421,851
80 | 17 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21852 | 421,853
80 | 17 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 21854 | 421,855
80 | 17 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21856 | 421,857
80 | 17 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21858 | 421,859
80 | 17 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21860 | 421,861
80 | 17 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21862 | 421,863
80 | 17 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 21864 | 421,865
80 | 17 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21866 | 421,867
80 | 17 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21868 | 421,869
80 | 17 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21870 | 421,871
80 | 17 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21872 | 421,873
80 | 17 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21882 | 421,883
80 | 17 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21884 | 421,885
80 | 17 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21886 | 421,887
80 | 17 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 21888 | 421,889
80 | 17 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21890 | 421,891
80 | 17 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21892 | 421,893
80 | 17 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21894 | 421,895
80 | 17 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 21896 | 421,897
80 | 18 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21976 | 421,977
80 | 18 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21978 | 421,979
80 | 18 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21980 | 421,981
80 | 18 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 21982 | 421,983
80 | 18 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 22068 | 422,069
80 | 18 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 21984 | 421,985
80 | 18 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 21986 | 421,987
80 | 18 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 21988 | 421,989
80 | 18 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 21990 | 421,991
80 | 18 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 21992 | 421,993
80 | 18 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 21994 | 421,995
80 | 18 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21996 | 421,997
80 | 18 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 21998 | 421,999
80 | 18 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22000 | 422,001
80 | 18 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22002 | 422,003
80 | 18 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22004 | 422,005
80 | 18 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22006 | 422,007
80 | 18 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22008 | 422,009
80 | 18 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22010 | 422,011
80 | 18 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22012 | 422,013
80 | 18 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22014 | 422,015
80 | 18 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22016 | 422,017
80 | 18 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22018 | 422,019
80 | 18 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22020 | 422,021
80 | 18 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22022 | 422,023
80 | 18 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22024 | 422,025
80 | 18 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22026 | 422,027
80 | 18 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22028 | 422,029
80 | 18 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22030 | 422,031
80 | 18 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22032 | 422,033
80 | 18 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22034 | 422,035
80 | 18 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22036 | 422,037
80 | 18 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22038 | 422,039
80 | 18 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22040 | 422,041
80 | 18 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22042 | 422,043
80 | 18 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22052 | 422,053
80 | 18 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22054 | 422,055
80 | 18 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22056 | 422,057
80 | 18 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22058 | 422,059
80 | 18 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22060 | 422,061
80 | 18 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22062 | 422,063
80 | 18 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22064 | 422,065
80 | 18 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22066 | 422,067
80 | 19 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22146 | 422,147
80 | 19 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22148 | 422,149
80 | 19 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22150 | 422,151
80 | 19 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22152 | 422,153
80 | 19 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 22238 | 422,239
80 | 19 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 22154 | 422,155
80 | 19 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 22156 | 422,157
80 | 19 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 22158 | 422,159
80 | 19 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 22160 | 422,161
80 | 19 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 22162 | 422,163
80 | 19 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 22164 | 422,165
80 | 19 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22166 | 422,167
80 | 19 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22168 | 422,169
80 | 19 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22170 | 422,171
80 | 19 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22172 | 422,173
80 | 19 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22174 | 422,175
80 | 19 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22176 | 422,177
80 | 19 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22178 | 422,179
80 | 19 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22180 | 422,181
80 | 19 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22182 | 422,183
80 | 19 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22184 | 422,185
80 | 19 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22186 | 422,187
80 | 19 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22188 | 422,189
80 | 19 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22190 | 422,191
80 | 19 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22192 | 422,193
80 | 19 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22194 | 422,195
80 | 19 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22196 | 422,197
80 | 19 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22198 | 422,199
80 | 19 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22200 | 422,201
80 | 19 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22202 | 422,203
80 | 19 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22204 | 422,205
80 | 19 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22206 | 422,207
80 | 19 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22208 | 422,209
80 | 19 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22210 | 422,211
80 | 19 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22212 | 422,213
80 | 19 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22222 | 422,223
80 | 19 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22224 | 422,225
80 | 19 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22226 | 422,227
80 | 19 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22228 | 422,229
80 | 19 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22230 | 422,231
80 | 19 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22232 | 422,233
80 | 19 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22234 | 422,235
80 | 19 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22236 | 422,237
80 | 20 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22316 | 422,317
80 | 20 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22318 | 422,319
80 | 20 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22320 | 422,321
80 | 20 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22322 | 422,323
80 | 20 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 22408 | 422,409
80 | 20 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 22324 | 422,325
80 | 20 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 22326 | 422,327
80 | 20 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 22328 | 422,329
80 | 20 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 22330 | 422,331
80 | 20 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 22332 | 422,333
80 | 20 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 22334 | 422,335
80 | 20 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22336 | 422,337
80 | 20 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22338 | 422,339
80 | 20 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22340 | 422,341
80 | 20 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22342 | 422,343
80 | 20 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22344 | 422,345
80 | 20 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22346 | 422,347
80 | 20 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22348 | 422,349
80 | 20 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22350 | 422,351
80 | 20 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22352 | 422,353
80 | 20 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22354 | 422,355
80 | 20 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22356 | 422,357
80 | 20 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22358 | 422,359
80 | 20 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22360 | 422,361
80 | 20 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22362 | 422,363
80 | 20 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22364 | 422,365
80 | 20 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22366 | 422,367
80 | 20 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22368 | 422,369
80 | 20 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22370 | 422,371
80 | 20 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22372 | 422,373
80 | 20 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22374 | 422,375
80 | 20 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22376 | 422,377
80 | 20 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22378 | 422,379
80 | 20 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22380 | 422,381
80 | 20 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22382 | 422,383
80 | 20 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22392 | 422,393
80 | 20 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22394 | 422,395
80 | 20 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22396 | 422,397
80 | 20 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22398 | 422,399
80 | 20 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22400 | 422,401
80 | 20 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22402 | 422,403
80 | 20 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22404 | 422,405
80 | 20 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22406 | 422,407
80 | 21 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22486 | 422,487
80 | 21 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22488 | 422,489
80 | 21 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22490 | 422,491
80 | 21 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22492 | 422,493
80 | 21 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 22578 | 422,579
80 | 21 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 22494 | 422,495
80 | 21 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 22496 | 422,497
80 | 21 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 22498 | 422,499
80 | 21 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 22500 | 422,501
80 | 21 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 22502 | 422,503
80 | 21 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 22504 | 422,505
80 | 21 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22506 | 422,507
80 | 21 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22508 | 422,509
80 | 21 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22510 | 422,511
80 | 21 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22512 | 422,513
80 | 21 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22514 | 422,515
80 | 21 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22516 | 422,517
80 | 21 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22518 | 422,519
80 | 21 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22520 | 422,521
80 | 21 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22522 | 422,523
80 | 21 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22524 | 422,525
80 | 21 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22526 | 422,527
80 | 21 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22528 | 422,529
80 | 21 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22530 | 422,531
80 | 21 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22532 | 422,533
80 | 21 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22534 | 422,535
80 | 21 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22536 | 422,537
80 | 21 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22538 | 422,539
80 | 21 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22540 | 422,541
80 | 21 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22542 | 422,543
80 | 21 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22544 | 422,545
80 | 21 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22546 | 422,547
80 | 21 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22548 | 422,549
80 | 21 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22550 | 422,551
80 | 21 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22552 | 422,553
80 | 21 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22562 | 422,563
80 | 21 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22564 | 422,565
80 | 21 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22566 | 422,567
80 | 21 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22568 | 422,569
80 | 21 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22570 | 422,571
80 | 21 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22572 | 422,573
80 | 21 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22574 | 422,575
80 | 21 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22576 | 422,577
80 | 22 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22656 | 422,657
80 | 22 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22658 | 422,659
80 | 22 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22660 | 422,661
80 | 22 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22662 | 422,663
80 | 22 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 22748 | 422,749
80 | 22 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 22664 | 422,665
80 | 22 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 22666 | 422,667
80 | 22 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 22668 | 422,669
80 | 22 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 22670 | 422,671
80 | 22 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 22672 | 422,673
80 | 22 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 22674 | 422,675
80 | 22 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22676 | 422,677
80 | 22 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22678 | 422,679
80 | 22 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22680 | 422,681
80 | 22 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22682 | 422,683
80 | 22 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22684 | 422,685
80 | 22 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22686 | 422,687
80 | 22 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22688 | 422,689
80 | 22 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22690 | 422,691
80 | 22 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22692 | 422,693
80 | 22 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22694 | 422,695
80 | 22 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22696 | 422,697
80 | 22 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22698 | 422,699
80 | 22 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22700 | 422,701
80 | 22 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22702 | 422,703
80 | 22 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22704 | 422,705
80 | 22 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22706 | 422,707
80 | 22 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22708 | 422,709
80 | 22 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22710 | 422,711
80 | 22 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22712 | 422,713
80 | 22 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22714 | 422,715
80 | 22 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22716 | 422,717
80 | 22 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22718 | 422,719
80 | 22 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22720 | 422,721
80 | 22 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22722 | 422,723
80 | 22 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22732 | 422,733
80 | 22 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22734 | 422,735
80 | 22 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22736 | 422,737
80 | 22 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22738 | 422,739
80 | 22 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22740 | 422,741
80 | 22 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22742 | 422,743
80 | 22 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22744 | 422,745
80 | 22 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22746 | 422,747
80 | 23 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22826 | 422,827
80 | 23 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22828 | 422,829
80 | 23 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22830 | 422,831
80 | 23 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22832 | 422,833
80 | 23 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 22918 | 422,919
80 | 23 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 22834 | 422,835
80 | 23 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 22836 | 422,837
80 | 23 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 22838 | 422,839
80 | 23 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 22840 | 422,841
80 | 23 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 22842 | 422,843
80 | 23 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 22844 | 422,845
80 | 23 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22846 | 422,847
80 | 23 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22848 | 422,849
80 | 23 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22850 | 422,851
80 | 23 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22852 | 422,853
80 | 23 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22854 | 422,855
80 | 23 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22856 | 422,857
80 | 23 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22858 | 422,859
80 | 23 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 22860 | 422,861
80 | 23 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22862 | 422,863
80 | 23 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22864 | 422,865
80 | 23 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22866 | 422,867
80 | 23 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22868 | 422,869
80 | 23 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22870 | 422,871
80 | 23 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22872 | 422,873
80 | 23 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 22874 | 422,875
80 | 23 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 22876 | 422,877
80 | 23 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22878 | 422,879
80 | 23 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22880 | 422,881
80 | 23 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22882 | 422,883
80 | 23 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 22884 | 422,885
80 | 23 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22886 | 422,887
80 | 23 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22888 | 422,889
80 | 23 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22890 | 422,891
80 | 23 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22892 | 422,893
80 | 23 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22902 | 422,903
80 | 23 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22904 | 422,905
80 | 23 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22906 | 422,907
80 | 23 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 22908 | 422,909
80 | 23 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22910 | 422,911
80 | 23 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22912 | 422,913
80 | 23 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22914 | 422,915
80 | 23 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 22916 | 422,917
80 | 24 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22996 | 422,997
80 | 24 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 22998 | 422,999
80 | 24 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23000 | 423,001
80 | 24 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23002 | 423,003
80 | 24 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 23088 | 423,089
80 | 24 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 23004 | 423,005
80 | 24 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 23006 | 423,007
80 | 24 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 23008 | 423,009
80 | 24 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 23010 | 423,011
80 | 24 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 23012 | 423,013
80 | 24 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 23014 | 423,015
80 | 24 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23016 | 423,017
80 | 24 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23018 | 423,019
80 | 24 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23020 | 423,021
80 | 24 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23022 | 423,023
80 | 24 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23024 | 423,025
80 | 24 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23026 | 423,027
80 | 24 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23028 | 423,029
80 | 24 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23030 | 423,031
80 | 24 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23032 | 423,033
80 | 24 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23034 | 423,035
80 | 24 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23036 | 423,037
80 | 24 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23038 | 423,039
80 | 24 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23040 | 423,041
80 | 24 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23042 | 423,043
80 | 24 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23044 | 423,045
80 | 24 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23046 | 423,047
80 | 24 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23048 | 423,049
80 | 24 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23050 | 423,051
80 | 24 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23052 | 423,053
80 | 24 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23054 | 423,055
80 | 24 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23056 | 423,057
80 | 24 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23058 | 423,059
80 | 24 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23060 | 423,061
80 | 24 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23062 | 423,063
80 | 24 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23072 | 423,073
80 | 24 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23074 | 423,075
80 | 24 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23076 | 423,077
80 | 24 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23078 | 423,079
80 | 24 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23080 | 423,081
80 | 24 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23082 | 423,083
80 | 24 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23084 | 423,085
80 | 24 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23086 | 423,087
80 | 25 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23166 | 423,167
80 | 25 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23168 | 423,169
80 | 25 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23170 | 423,171
80 | 25 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23172 | 423,173
80 | 25 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 23258 | 423,259
80 | 25 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 23174 | 423,175
80 | 25 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 23176 | 423,177
80 | 25 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 23178 | 423,179
80 | 25 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 23180 | 423,181
80 | 25 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 23182 | 423,183
80 | 25 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 23184 | 423,185
80 | 25 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23186 | 423,187
80 | 25 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23188 | 423,189
80 | 25 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23190 | 423,191
80 | 25 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23192 | 423,193
80 | 25 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23194 | 423,195
80 | 25 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23196 | 423,197
80 | 25 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23198 | 423,199
80 | 25 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23200 | 423,201
80 | 25 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23202 | 423,203
80 | 25 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23204 | 423,205
80 | 25 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23206 | 423,207
80 | 25 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23208 | 423,209
80 | 25 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23210 | 423,211
80 | 25 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23212 | 423,213
80 | 25 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23214 | 423,215
80 | 25 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23216 | 423,217
80 | 25 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23218 | 423,219
80 | 25 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23220 | 423,221
80 | 25 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23222 | 423,223
80 | 25 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23224 | 423,225
80 | 25 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23226 | 423,227
80 | 25 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23228 | 423,229
80 | 25 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23230 | 423,231
80 | 25 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23232 | 423,233
80 | 25 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23242 | 423,243
80 | 25 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23244 | 423,245
80 | 25 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23246 | 423,247
80 | 25 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23248 | 423,249
80 | 25 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23250 | 423,251
80 | 25 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23252 | 423,253
80 | 25 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23254 | 423,255
80 | 25 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23256 | 423,257
80 | 26 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23336 | 423,337
80 | 26 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23338 | 423,339
80 | 26 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23340 | 423,341
80 | 26 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23342 | 423,343
80 | 26 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 23428 | 423,429
80 | 26 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 23344 | 423,345
80 | 26 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 23346 | 423,347
80 | 26 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 23348 | 423,349
80 | 26 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 23350 | 423,351
80 | 26 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 23352 | 423,353
80 | 26 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 23354 | 423,355
80 | 26 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23356 | 423,357
80 | 26 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23358 | 423,359
80 | 26 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23360 | 423,361
80 | 26 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23362 | 423,363
80 | 26 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23364 | 423,365
80 | 26 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23366 | 423,367
80 | 26 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23368 | 423,369
80 | 26 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23370 | 423,371
80 | 26 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23372 | 423,373
80 | 26 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23374 | 423,375
80 | 26 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23376 | 423,377
80 | 26 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23378 | 423,379
80 | 26 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23380 | 423,381
80 | 26 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23382 | 423,383
80 | 26 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23384 | 423,385
80 | 26 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23386 | 423,387
80 | 26 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23388 | 423,389
80 | 26 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23390 | 423,391
80 | 26 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23392 | 423,393
80 | 26 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23394 | 423,395
80 | 26 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23396 | 423,397
80 | 26 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23398 | 423,399
80 | 26 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23400 | 423,401
80 | 26 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23402 | 423,403
80 | 26 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23412 | 423,413
80 | 26 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23414 | 423,415
80 | 26 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23416 | 423,417
80 | 26 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23418 | 423,419
80 | 26 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23420 | 423,421
80 | 26 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23422 | 423,423
80 | 26 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23424 | 423,425
80 | 26 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23426 | 423,427
80 | 27 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23506 | 423,507
80 | 27 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23508 | 423,509
80 | 27 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23510 | 423,511
80 | 27 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23512 | 423,513
80 | 27 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 23598 | 423,599
80 | 27 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 23514 | 423,515
80 | 27 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 23516 | 423,517
80 | 27 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 23518 | 423,519
80 | 27 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 23520 | 423,521
80 | 27 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 23522 | 423,523
80 | 27 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 23524 | 423,525
80 | 27 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23526 | 423,527
80 | 27 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23528 | 423,529
80 | 27 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23530 | 423,531
80 | 27 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23532 | 423,533
80 | 27 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23534 | 423,535
80 | 27 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23536 | 423,537
80 | 27 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23538 | 423,539
80 | 27 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23540 | 423,541
80 | 27 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23542 | 423,543
80 | 27 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23544 | 423,545
80 | 27 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23546 | 423,547
80 | 27 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23548 | 423,549
80 | 27 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23550 | 423,551
80 | 27 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23552 | 423,553
80 | 27 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23554 | 423,555
80 | 27 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23556 | 423,557
80 | 27 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23558 | 423,559
80 | 27 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23560 | 423,561
80 | 27 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23562 | 423,563
80 | 27 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23564 | 423,565
80 | 27 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23566 | 423,567
80 | 27 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23568 | 423,569
80 | 27 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23570 | 423,571
80 | 27 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23572 | 423,573
80 | 27 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23582 | 423,583
80 | 27 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23584 | 423,585
80 | 27 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23586 | 423,587
80 | 27 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23588 | 423,589
80 | 27 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23590 | 423,591
80 | 27 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23592 | 423,593
80 | 27 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23594 | 423,595
80 | 27 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23596 | 423,597
80 | 28 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23676 | 423,677
80 | 28 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23678 | 423,679
80 | 28 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23680 | 423,681
80 | 28 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23682 | 423,683
80 | 28 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 23768 | 423,769
80 | 28 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 23684 | 423,685
80 | 28 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 23686 | 423,687
80 | 28 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 23688 | 423,689
80 | 28 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 23690 | 423,691
80 | 28 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 23692 | 423,693
80 | 28 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 23694 | 423,695
80 | 28 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23696 | 423,697
80 | 28 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23698 | 423,699
80 | 28 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23700 | 423,701
80 | 28 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23702 | 423,703
80 | 28 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23704 | 423,705
80 | 28 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23706 | 423,707
80 | 28 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23708 | 423,709
80 | 28 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23710 | 423,711
80 | 28 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23712 | 423,713
80 | 28 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23714 | 423,715
80 | 28 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23716 | 423,717
80 | 28 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23718 | 423,719
80 | 28 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23720 | 423,721
80 | 28 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23722 | 423,723
80 | 28 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23724 | 423,725
80 | 28 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23726 | 423,727
80 | 28 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23728 | 423,729
80 | 28 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23730 | 423,731
80 | 28 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23732 | 423,733
80 | 28 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23734 | 423,735
80 | 28 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23736 | 423,737
80 | 28 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23738 | 423,739
80 | 28 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23740 | 423,741
80 | 28 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23742 | 423,743
80 | 28 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23752 | 423,753
80 | 28 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23754 | 423,755
80 | 28 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23756 | 423,757
80 | 28 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23758 | 423,759
80 | 28 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23760 | 423,761
80 | 28 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23762 | 423,763
80 | 28 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23764 | 423,765
80 | 28 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23766 | 423,767
80 | 29 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23846 | 423,847
80 | 29 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23848 | 423,849
80 | 29 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23850 | 423,851
80 | 29 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 23852 | 423,853
80 | 29 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 23938 | 423,939
80 | 29 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 23854 | 423,855
80 | 29 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 23856 | 423,857
80 | 29 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 23858 | 423,859
80 | 29 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 23860 | 423,861
80 | 29 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 23862 | 423,863
80 | 29 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 23864 | 423,865
80 | 29 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23866 | 423,867
80 | 29 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23868 | 423,869
80 | 29 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23870 | 423,871
80 | 29 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23872 | 423,873
80 | 29 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23874 | 423,875
80 | 29 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23876 | 423,877
80 | 29 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23878 | 423,879
80 | 29 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 23880 | 423,881
80 | 29 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23882 | 423,883
80 | 29 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23884 | 423,885
80 | 29 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23886 | 423,887
80 | 29 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23888 | 423,889
80 | 29 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23890 | 423,891
80 | 29 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23892 | 423,893
80 | 29 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 23894 | 423,895
80 | 29 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 23896 | 423,897
80 | 29 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23898 | 423,899
80 | 29 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23900 | 423,901
80 | 29 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23902 | 423,903
80 | 29 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 23904 | 423,905
80 | 29 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23906 | 423,907
80 | 29 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23908 | 423,909
80 | 29 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23910 | 423,911
80 | 29 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23912 | 423,913
80 | 29 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23922 | 423,923
80 | 29 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23924 | 423,925
80 | 29 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23926 | 423,927
80 | 29 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 23928 | 423,929
80 | 29 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23930 | 423,931
80 | 29 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23932 | 423,933
80 | 29 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23934 | 423,935
80 | 29 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 23936 | 423,937
80 | 30 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24016 | 424,017
80 | 30 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24018 | 424,019
80 | 30 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24020 | 424,021
80 | 30 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24022 | 424,023
80 | 30 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 24108 | 424,109
80 | 30 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 24024 | 424,025
80 | 30 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 24026 | 424,027
80 | 30 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 24028 | 424,029
80 | 30 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 24030 | 424,031
80 | 30 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 24032 | 424,033
80 | 30 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 24034 | 424,035
80 | 30 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24036 | 424,037
80 | 30 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24038 | 424,039
80 | 30 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24040 | 424,041
80 | 30 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24042 | 424,043
80 | 30 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24044 | 424,045
80 | 30 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24046 | 424,047
80 | 30 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24048 | 424,049
80 | 30 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24050 | 424,051
80 | 30 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24052 | 424,053
80 | 30 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24054 | 424,055
80 | 30 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24056 | 424,057
80 | 30 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24058 | 424,059
80 | 30 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24060 | 424,061
80 | 30 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24062 | 424,063
80 | 30 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24064 | 424,065
80 | 30 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24066 | 424,067
80 | 30 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24068 | 424,069
80 | 30 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24070 | 424,071
80 | 30 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24072 | 424,073
80 | 30 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24074 | 424,075
80 | 30 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24076 | 424,077
80 | 30 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24078 | 424,079
80 | 30 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24080 | 424,081
80 | 30 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24082 | 424,083
80 | 30 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24092 | 424,093
80 | 30 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24094 | 424,095
80 | 30 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24096 | 424,097
80 | 30 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24098 | 424,099
80 | 30 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24100 | 424,101
80 | 30 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24102 | 424,103
80 | 30 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24104 | 424,105
80 | 30 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24106 | 424,107
80 | 31 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24186 | 424,187
80 | 31 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24188 | 424,189
80 | 31 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24190 | 424,191
80 | 31 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24192 | 424,193
80 | 31 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 24278 | 424,279
80 | 31 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 24194 | 424,195
80 | 31 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 24196 | 424,197
80 | 31 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 24198 | 424,199
80 | 31 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 24200 | 424,201
80 | 31 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 24202 | 424,203
80 | 31 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 24204 | 424,205
80 | 31 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24206 | 424,207
80 | 31 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24208 | 424,209
80 | 31 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24210 | 424,211
80 | 31 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24212 | 424,213
80 | 31 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24214 | 424,215
80 | 31 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24216 | 424,217
80 | 31 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24218 | 424,219
80 | 31 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24220 | 424,221
80 | 31 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24222 | 424,223
80 | 31 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24224 | 424,225
80 | 31 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24226 | 424,227
80 | 31 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24228 | 424,229
80 | 31 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24230 | 424,231
80 | 31 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24232 | 424,233
80 | 31 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24234 | 424,235
80 | 31 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24236 | 424,237
80 | 31 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24238 | 424,239
80 | 31 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24240 | 424,241
80 | 31 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24242 | 424,243
80 | 31 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24244 | 424,245
80 | 31 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24246 | 424,247
80 | 31 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24248 | 424,249
80 | 31 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24250 | 424,251
80 | 31 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24252 | 424,253
80 | 31 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24262 | 424,263
80 | 31 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24264 | 424,265
80 | 31 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24266 | 424,267
80 | 31 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24268 | 424,269
80 | 31 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24270 | 424,271
80 | 31 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24272 | 424,273
80 | 31 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24274 | 424,275
80 | 31 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24276 | 424,277
80 | 32 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24356 | 424,357
80 | 32 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24358 | 424,359
80 | 32 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24360 | 424,361
80 | 32 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24362 | 424,363
80 | 32 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 24448 | 424,449
80 | 32 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 24364 | 424,365
80 | 32 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 24366 | 424,367
80 | 32 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 24368 | 424,369
80 | 32 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 24370 | 424,371
80 | 32 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 24372 | 424,373
80 | 32 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 24374 | 424,375
80 | 32 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24376 | 424,377
80 | 32 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24378 | 424,379
80 | 32 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24380 | 424,381
80 | 32 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24382 | 424,383
80 | 32 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24384 | 424,385
80 | 32 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24386 | 424,387
80 | 32 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24388 | 424,389
80 | 32 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24390 | 424,391
80 | 32 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24392 | 424,393
80 | 32 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24394 | 424,395
80 | 32 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24396 | 424,397
80 | 32 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24398 | 424,399
80 | 32 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24400 | 424,401
80 | 32 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24402 | 424,403
80 | 32 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24404 | 424,405
80 | 32 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24406 | 424,407
80 | 32 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24408 | 424,409
80 | 32 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24410 | 424,411
80 | 32 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24412 | 424,413
80 | 32 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24414 | 424,415
80 | 32 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24416 | 424,417
80 | 32 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24418 | 424,419
80 | 32 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24420 | 424,421
80 | 32 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24422 | 424,423
80 | 32 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24432 | 424,433
80 | 32 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24434 | 424,435
80 | 32 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24436 | 424,437
80 | 32 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24438 | 424,439
80 | 32 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24440 | 424,441
80 | 32 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24442 | 424,443
80 | 32 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24444 | 424,445
80 | 32 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24446 | 424,447
80 | 33 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24526 | 424,527
80 | 33 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24528 | 424,529
80 | 33 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24530 | 424,531
80 | 33 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24532 | 424,533
80 | 33 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 24618 | 424,619
80 | 33 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 24534 | 424,535
80 | 33 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 24536 | 424,537
80 | 33 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 24538 | 424,539
80 | 33 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 24540 | 424,541
80 | 33 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 24542 | 424,543
80 | 33 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 24544 | 424,545
80 | 33 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24546 | 424,547
80 | 33 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24548 | 424,549
80 | 33 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24550 | 424,551
80 | 33 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24552 | 424,553
80 | 33 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24554 | 424,555
80 | 33 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24556 | 424,557
80 | 33 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24558 | 424,559
80 | 33 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24560 | 424,561
80 | 33 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24562 | 424,563
80 | 33 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24564 | 424,565
80 | 33 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24566 | 424,567
80 | 33 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24568 | 424,569
80 | 33 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24570 | 424,571
80 | 33 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24572 | 424,573
80 | 33 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24574 | 424,575
80 | 33 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24576 | 424,577
80 | 33 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24578 | 424,579
80 | 33 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24580 | 424,581
80 | 33 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24582 | 424,583
80 | 33 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24584 | 424,585
80 | 33 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24586 | 424,587
80 | 33 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24588 | 424,589
80 | 33 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24590 | 424,591
80 | 33 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24592 | 424,593
80 | 33 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24602 | 424,603
80 | 33 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24604 | 424,605
80 | 33 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24606 | 424,607
80 | 33 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24608 | 424,609
80 | 33 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24610 | 424,611
80 | 33 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24612 | 424,613
80 | 33 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24614 | 424,615
80 | 33 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24616 | 424,617
80 | 34 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24696 | 424,697
80 | 34 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24698 | 424,699
80 | 34 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24700 | 424,701
80 | 34 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24702 | 424,703
80 | 34 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 24788 | 424,789
80 | 34 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 24704 | 424,705
80 | 34 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 24706 | 424,707
80 | 34 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 24708 | 424,709
80 | 34 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 24710 | 424,711
80 | 34 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 24712 | 424,713
80 | 34 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 24714 | 424,715
80 | 34 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24716 | 424,717
80 | 34 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24718 | 424,719
80 | 34 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24720 | 424,721
80 | 34 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24722 | 424,723
80 | 34 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24724 | 424,725
80 | 34 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24726 | 424,727
80 | 34 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24728 | 424,729
80 | 34 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24730 | 424,731
80 | 34 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24732 | 424,733
80 | 34 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24734 | 424,735
80 | 34 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24736 | 424,737
80 | 34 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24738 | 424,739
80 | 34 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24740 | 424,741
80 | 34 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24742 | 424,743
80 | 34 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24744 | 424,745
80 | 34 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24746 | 424,747
80 | 34 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24748 | 424,749
80 | 34 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24750 | 424,751
80 | 34 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24752 | 424,753
80 | 34 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24754 | 424,755
80 | 34 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24756 | 424,757
80 | 34 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24758 | 424,759
80 | 34 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24760 | 424,761
80 | 34 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24762 | 424,763
80 | 34 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24772 | 424,773
80 | 34 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24774 | 424,775
80 | 34 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24776 | 424,777
80 | 34 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24778 | 424,779
80 | 34 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24780 | 424,781
80 | 34 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24782 | 424,783
80 | 34 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24784 | 424,785
80 | 34 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24786 | 424,787
80 | 35 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24866 | 424,867
80 | 35 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24868 | 424,869
80 | 35 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24870 | 424,871
80 | 35 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 24872 | 424,873
80 | 35 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 24958 | 424,959
80 | 35 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 24874 | 424,875
80 | 35 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 24876 | 424,877
80 | 35 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 24878 | 424,879
80 | 35 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 24880 | 424,881
80 | 35 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 24882 | 424,883
80 | 35 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 24884 | 424,885
80 | 35 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24886 | 424,887
80 | 35 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24888 | 424,889
80 | 35 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24890 | 424,891
80 | 35 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24892 | 424,893
80 | 35 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24894 | 424,895
80 | 35 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24896 | 424,897
80 | 35 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24898 | 424,899
80 | 35 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 24900 | 424,901
80 | 35 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24902 | 424,903
80 | 35 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24904 | 424,905
80 | 35 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24906 | 424,907
80 | 35 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24908 | 424,909
80 | 35 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24910 | 424,911
80 | 35 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24912 | 424,913
80 | 35 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 24914 | 424,915
80 | 35 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 24916 | 424,917
80 | 35 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24918 | 424,919
80 | 35 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24920 | 424,921
80 | 35 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24922 | 424,923
80 | 35 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 24924 | 424,925
80 | 35 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24926 | 424,927
80 | 35 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24928 | 424,929
80 | 35 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24930 | 424,931
80 | 35 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24932 | 424,933
80 | 35 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24942 | 424,943
80 | 35 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24944 | 424,945
80 | 35 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24946 | 424,947
80 | 35 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 24948 | 424,949
80 | 35 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24950 | 424,951
80 | 35 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24952 | 424,953
80 | 35 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24954 | 424,955
80 | 35 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 24956 | 424,957
80 | 36 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25036 | 425,037
80 | 36 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25038 | 425,039
80 | 36 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25040 | 425,041
80 | 36 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25042 | 425,043
80 | 36 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 25128 | 425,129
80 | 36 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 25044 | 425,045
80 | 36 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 25046 | 425,047
80 | 36 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 25048 | 425,049
80 | 36 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 25050 | 425,051
80 | 36 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 25052 | 425,053
80 | 36 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 25054 | 425,055
80 | 36 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25056 | 425,057
80 | 36 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25058 | 425,059
80 | 36 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25060 | 425,061
80 | 36 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25062 | 425,063
80 | 36 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25064 | 425,065
80 | 36 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25066 | 425,067
80 | 36 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25068 | 425,069
80 | 36 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25070 | 425,071
80 | 36 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25072 | 425,073
80 | 36 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25074 | 425,075
80 | 36 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25076 | 425,077
80 | 36 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25078 | 425,079
80 | 36 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25080 | 425,081
80 | 36 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25082 | 425,083
80 | 36 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25084 | 425,085
80 | 36 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25086 | 425,087
80 | 36 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25088 | 425,089
80 | 36 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25090 | 425,091
80 | 36 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25092 | 425,093
80 | 36 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25094 | 425,095
80 | 36 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25096 | 425,097
80 | 36 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25098 | 425,099
80 | 36 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25100 | 425,101
80 | 36 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25102 | 425,103
80 | 36 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25112 | 425,113
80 | 36 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25114 | 425,115
80 | 36 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25116 | 425,117
80 | 36 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25118 | 425,119
80 | 36 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25120 | 425,121
80 | 36 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25122 | 425,123
80 | 36 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25124 | 425,125
80 | 36 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25126 | 425,127
80 | 37 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25206 | 425,207
80 | 37 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25208 | 425,209
80 | 37 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25210 | 425,211
80 | 37 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25212 | 425,213
80 | 37 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 25298 | 425,299
80 | 37 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 25214 | 425,215
80 | 37 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 25216 | 425,217
80 | 37 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 25218 | 425,219
80 | 37 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 25220 | 425,221
80 | 37 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 25222 | 425,223
80 | 37 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 25224 | 425,225
80 | 37 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25226 | 425,227
80 | 37 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25228 | 425,229
80 | 37 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25230 | 425,231
80 | 37 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25232 | 425,233
80 | 37 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25234 | 425,235
80 | 37 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25236 | 425,237
80 | 37 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25238 | 425,239
80 | 37 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25240 | 425,241
80 | 37 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25242 | 425,243
80 | 37 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25244 | 425,245
80 | 37 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25246 | 425,247
80 | 37 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25248 | 425,249
80 | 37 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25250 | 425,251
80 | 37 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25252 | 425,253
80 | 37 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25254 | 425,255
80 | 37 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25256 | 425,257
80 | 37 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25258 | 425,259
80 | 37 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25260 | 425,261
80 | 37 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25262 | 425,263
80 | 37 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25264 | 425,265
80 | 37 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25266 | 425,267
80 | 37 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25268 | 425,269
80 | 37 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25270 | 425,271
80 | 37 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25272 | 425,273
80 | 37 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25282 | 425,283
80 | 37 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25284 | 425,285
80 | 37 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25286 | 425,287
80 | 37 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25288 | 425,289
80 | 37 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25290 | 425,291
80 | 37 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25292 | 425,293
80 | 37 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25294 | 425,295
80 | 37 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25296 | 425,297
80 | 38 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25376 | 425,377
80 | 38 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25378 | 425,379
80 | 38 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25380 | 425,381
80 | 38 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25382 | 425,383
80 | 38 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 25468 | 425,469
80 | 38 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 25384 | 425,385
80 | 38 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 25386 | 425,387
80 | 38 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 25388 | 425,389
80 | 38 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 25390 | 425,391
80 | 38 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 25392 | 425,393
80 | 38 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 25394 | 425,395
80 | 38 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25396 | 425,397
80 | 38 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25398 | 425,399
80 | 38 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25400 | 425,401
80 | 38 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25402 | 425,403
80 | 38 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25404 | 425,405
80 | 38 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25406 | 425,407
80 | 38 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25408 | 425,409
80 | 38 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25410 | 425,411
80 | 38 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25412 | 425,413
80 | 38 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25414 | 425,415
80 | 38 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25416 | 425,417
80 | 38 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25418 | 425,419
80 | 38 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25420 | 425,421
80 | 38 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25422 | 425,423
80 | 38 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25424 | 425,425
80 | 38 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25426 | 425,427
80 | 38 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25428 | 425,429
80 | 38 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25430 | 425,431
80 | 38 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25432 | 425,433
80 | 38 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25434 | 425,435
80 | 38 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25436 | 425,437
80 | 38 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25438 | 425,439
80 | 38 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25440 | 425,441
80 | 38 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25442 | 425,443
80 | 38 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25452 | 425,453
80 | 38 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25454 | 425,455
80 | 38 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25456 | 425,457
80 | 38 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25458 | 425,459
80 | 38 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25460 | 425,461
80 | 38 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25462 | 425,463
80 | 38 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25464 | 425,465
80 | 38 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25466 | 425,467
80 | 39 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25546 | 425,547
80 | 39 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25548 | 425,549
80 | 39 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25550 | 425,551
80 | 39 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25552 | 425,553
80 | 39 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 25638 | 425,639
80 | 39 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 25554 | 425,555
80 | 39 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 25556 | 425,557
80 | 39 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 25558 | 425,559
80 | 39 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 25560 | 425,561
80 | 39 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 25562 | 425,563
80 | 39 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 25564 | 425,565
80 | 39 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25566 | 425,567
80 | 39 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25568 | 425,569
80 | 39 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25570 | 425,571
80 | 39 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25572 | 425,573
80 | 39 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25574 | 425,575
80 | 39 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25576 | 425,577
80 | 39 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25578 | 425,579
80 | 39 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25580 | 425,581
80 | 39 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25582 | 425,583
80 | 39 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25584 | 425,585
80 | 39 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25586 | 425,587
80 | 39 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25588 | 425,589
80 | 39 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25590 | 425,591
80 | 39 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25592 | 425,593
80 | 39 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25594 | 425,595
80 | 39 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25596 | 425,597
80 | 39 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25598 | 425,599
80 | 39 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25600 | 425,601
80 | 39 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25602 | 425,603
80 | 39 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25604 | 425,605
80 | 39 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25606 | 425,607
80 | 39 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25608 | 425,609
80 | 39 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25610 | 425,611
80 | 39 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25612 | 425,613
80 | 39 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25622 | 425,623
80 | 39 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25624 | 425,625
80 | 39 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25626 | 425,627
80 | 39 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25628 | 425,629
80 | 39 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25630 | 425,631
80 | 39 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25632 | 425,633
80 | 39 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25634 | 425,635
80 | 39 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25636 | 425,637
80 | 40 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25716 | 425,717
80 | 40 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25718 | 425,719
80 | 40 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25720 | 425,721
80 | 40 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25722 | 425,723
80 | 40 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 25808 | 425,809
80 | 40 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 25724 | 425,725
80 | 40 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 25726 | 425,727
80 | 40 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 25728 | 425,729
80 | 40 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 25730 | 425,731
80 | 40 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 25732 | 425,733
80 | 40 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 25734 | 425,735
80 | 40 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25736 | 425,737
80 | 40 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25738 | 425,739
80 | 40 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25740 | 425,741
80 | 40 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25742 | 425,743
80 | 40 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25744 | 425,745
80 | 40 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25746 | 425,747
80 | 40 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25748 | 425,749
80 | 40 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25750 | 425,751
80 | 40 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25752 | 425,753
80 | 40 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25754 | 425,755
80 | 40 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25756 | 425,757
80 | 40 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25758 | 425,759
80 | 40 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25760 | 425,761
80 | 40 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25762 | 425,763
80 | 40 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25764 | 425,765
80 | 40 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25766 | 425,767
80 | 40 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25768 | 425,769
80 | 40 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25770 | 425,771
80 | 40 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25772 | 425,773
80 | 40 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25774 | 425,775
80 | 40 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25776 | 425,777
80 | 40 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25778 | 425,779
80 | 40 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25780 | 425,781
80 | 40 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25782 | 425,783
80 | 40 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25792 | 425,793
80 | 40 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25794 | 425,795
80 | 40 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25796 | 425,797
80 | 40 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25798 | 425,799
80 | 40 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25800 | 425,801
80 | 40 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25802 | 425,803
80 | 40 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25804 | 425,805
80 | 40 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25806 | 425,807
80 | 41 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25886 | 425,887
80 | 41 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25888 | 425,889
80 | 41 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25890 | 425,891
80 | 41 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 25892 | 425,893
80 | 41 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 25978 | 425,979
80 | 41 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 25894 | 425,895
80 | 41 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 25896 | 425,897
80 | 41 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 25898 | 425,899
80 | 41 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 25900 | 425,901
80 | 41 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 25902 | 425,903
80 | 41 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 25904 | 425,905
80 | 41 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25906 | 425,907
80 | 41 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25908 | 425,909
80 | 41 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25910 | 425,911
80 | 41 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25912 | 425,913
80 | 41 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25914 | 425,915
80 | 41 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25916 | 425,917
80 | 41 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25918 | 425,919
80 | 41 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 25920 | 425,921
80 | 41 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25922 | 425,923
80 | 41 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25924 | 425,925
80 | 41 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25926 | 425,927
80 | 41 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25928 | 425,929
80 | 41 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25930 | 425,931
80 | 41 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25932 | 425,933
80 | 41 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 25934 | 425,935
80 | 41 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 25936 | 425,937
80 | 41 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25938 | 425,939
80 | 41 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25940 | 425,941
80 | 41 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25942 | 425,943
80 | 41 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 25944 | 425,945
80 | 41 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25946 | 425,947
80 | 41 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25948 | 425,949
80 | 41 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25950 | 425,951
80 | 41 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25952 | 425,953
80 | 41 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25962 | 425,963
80 | 41 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25964 | 425,965
80 | 41 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25966 | 425,967
80 | 41 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 25968 | 425,969
80 | 41 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25970 | 425,971
80 | 41 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25972 | 425,973
80 | 41 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25974 | 425,975
80 | 41 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 25976 | 425,977
80 | 42 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26056 | 426,057
80 | 42 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26058 | 426,059
80 | 42 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26060 | 426,061
80 | 42 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26062 | 426,063
80 | 42 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 26148 | 426,149
80 | 42 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 26064 | 426,065
80 | 42 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 26066 | 426,067
80 | 42 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 26068 | 426,069
80 | 42 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 26070 | 426,071
80 | 42 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 26072 | 426,073
80 | 42 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 26074 | 426,075
80 | 42 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26076 | 426,077
80 | 42 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26078 | 426,079
80 | 42 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26080 | 426,081
80 | 42 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26082 | 426,083
80 | 42 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26084 | 426,085
80 | 42 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26086 | 426,087
80 | 42 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26088 | 426,089
80 | 42 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26090 | 426,091
80 | 42 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26092 | 426,093
80 | 42 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26094 | 426,095
80 | 42 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26096 | 426,097
80 | 42 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26098 | 426,099
80 | 42 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26100 | 426,101
80 | 42 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26102 | 426,103
80 | 42 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26104 | 426,105
80 | 42 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26106 | 426,107
80 | 42 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26108 | 426,109
80 | 42 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26110 | 426,111
80 | 42 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26112 | 426,113
80 | 42 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26114 | 426,115
80 | 42 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26116 | 426,117
80 | 42 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26118 | 426,119
80 | 42 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26120 | 426,121
80 | 42 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26122 | 426,123
80 | 42 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26132 | 426,133
80 | 42 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26134 | 426,135
80 | 42 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26136 | 426,137
80 | 42 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26138 | 426,139
80 | 42 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26140 | 426,141
80 | 42 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26142 | 426,143
80 | 42 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26144 | 426,145
80 | 42 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26146 | 426,147
80 | 43 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26226 | 426,227
80 | 43 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26228 | 426,229
80 | 43 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26230 | 426,231
80 | 43 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26232 | 426,233
80 | 43 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 26318 | 426,319
80 | 43 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 26234 | 426,235
80 | 43 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 26236 | 426,237
80 | 43 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 26238 | 426,239
80 | 43 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 26240 | 426,241
80 | 43 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 26242 | 426,243
80 | 43 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 26244 | 426,245
80 | 43 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26246 | 426,247
80 | 43 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26248 | 426,249
80 | 43 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26250 | 426,251
80 | 43 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26252 | 426,253
80 | 43 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26254 | 426,255
80 | 43 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26256 | 426,257
80 | 43 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26258 | 426,259
80 | 43 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26260 | 426,261
80 | 43 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26262 | 426,263
80 | 43 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26264 | 426,265
80 | 43 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26266 | 426,267
80 | 43 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26268 | 426,269
80 | 43 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26270 | 426,271
80 | 43 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26272 | 426,273
80 | 43 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26274 | 426,275
80 | 43 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26276 | 426,277
80 | 43 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26278 | 426,279
80 | 43 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26280 | 426,281
80 | 43 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26282 | 426,283
80 | 43 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26284 | 426,285
80 | 43 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26286 | 426,287
80 | 43 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26288 | 426,289
80 | 43 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26290 | 426,291
80 | 43 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26292 | 426,293
80 | 43 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26302 | 426,303
80 | 43 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26304 | 426,305
80 | 43 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26306 | 426,307
80 | 43 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26308 | 426,309
80 | 43 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26310 | 426,311
80 | 43 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26312 | 426,313
80 | 43 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26314 | 426,315
80 | 43 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26316 | 426,317
80 | 44 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26396 | 426,397
80 | 44 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26398 | 426,399
80 | 44 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26400 | 426,401
80 | 44 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26402 | 426,403
80 | 44 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 26488 | 426,489
80 | 44 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 26404 | 426,405
80 | 44 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 26406 | 426,407
80 | 44 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 26408 | 426,409
80 | 44 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 26410 | 426,411
80 | 44 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 26412 | 426,413
80 | 44 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 26414 | 426,415
80 | 44 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26416 | 426,417
80 | 44 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26418 | 426,419
80 | 44 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26420 | 426,421
80 | 44 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26422 | 426,423
80 | 44 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26424 | 426,425
80 | 44 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26426 | 426,427
80 | 44 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26428 | 426,429
80 | 44 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26430 | 426,431
80 | 44 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26432 | 426,433
80 | 44 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26434 | 426,435
80 | 44 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26436 | 426,437
80 | 44 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26438 | 426,439
80 | 44 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26440 | 426,441
80 | 44 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26442 | 426,443
80 | 44 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26444 | 426,445
80 | 44 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26446 | 426,447
80 | 44 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26448 | 426,449
80 | 44 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26450 | 426,451
80 | 44 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26452 | 426,453
80 | 44 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26454 | 426,455
80 | 44 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26456 | 426,457
80 | 44 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26458 | 426,459
80 | 44 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26460 | 426,461
80 | 44 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26462 | 426,463
80 | 44 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26472 | 426,473
80 | 44 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26474 | 426,475
80 | 44 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26476 | 426,477
80 | 44 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26478 | 426,479
80 | 44 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26480 | 426,481
80 | 44 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26482 | 426,483
80 | 44 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26484 | 426,485
80 | 44 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26486 | 426,487
80 | 45 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26566 | 426,567
80 | 45 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26568 | 426,569
80 | 45 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26570 | 426,571
80 | 45 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26572 | 426,573
80 | 45 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 26658 | 426,659
80 | 45 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 26574 | 426,575
80 | 45 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 26576 | 426,577
80 | 45 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 26578 | 426,579
80 | 45 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 26580 | 426,581
80 | 45 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 26582 | 426,583
80 | 45 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 26584 | 426,585
80 | 45 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26586 | 426,587
80 | 45 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26588 | 426,589
80 | 45 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26590 | 426,591
80 | 45 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26592 | 426,593
80 | 45 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26594 | 426,595
80 | 45 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26596 | 426,597
80 | 45 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26598 | 426,599
80 | 45 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26600 | 426,601
80 | 45 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26602 | 426,603
80 | 45 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26604 | 426,605
80 | 45 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26606 | 426,607
80 | 45 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26608 | 426,609
80 | 45 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26610 | 426,611
80 | 45 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26612 | 426,613
80 | 45 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26614 | 426,615
80 | 45 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26616 | 426,617
80 | 45 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26618 | 426,619
80 | 45 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26620 | 426,621
80 | 45 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26622 | 426,623
80 | 45 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26624 | 426,625
80 | 45 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26626 | 426,627
80 | 45 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26628 | 426,629
80 | 45 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26630 | 426,631
80 | 45 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26632 | 426,633
80 | 45 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26642 | 426,643
80 | 45 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26644 | 426,645
80 | 45 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26646 | 426,647
80 | 45 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26648 | 426,649
80 | 45 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26650 | 426,651
80 | 45 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26652 | 426,653
80 | 45 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26654 | 426,655
80 | 45 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26656 | 426,657
80 | 46 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26736 | 426,737
80 | 46 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26738 | 426,739
80 | 46 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26740 | 426,741
80 | 46 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26742 | 426,743
80 | 46 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 26828 | 426,829
80 | 46 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 26744 | 426,745
80 | 46 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 26746 | 426,747
80 | 46 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 26748 | 426,749
80 | 46 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 26750 | 426,751
80 | 46 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 26752 | 426,753
80 | 46 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 26754 | 426,755
80 | 46 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26756 | 426,757
80 | 46 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26758 | 426,759
80 | 46 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26760 | 426,761
80 | 46 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26762 | 426,763
80 | 46 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26764 | 426,765
80 | 46 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26766 | 426,767
80 | 46 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26768 | 426,769
80 | 46 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26770 | 426,771
80 | 46 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26772 | 426,773
80 | 46 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26774 | 426,775
80 | 46 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26776 | 426,777
80 | 46 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26778 | 426,779
80 | 46 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26780 | 426,781
80 | 46 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26782 | 426,783
80 | 46 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26784 | 426,785
80 | 46 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26786 | 426,787
80 | 46 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26788 | 426,789
80 | 46 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26790 | 426,791
80 | 46 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26792 | 426,793
80 | 46 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26794 | 426,795
80 | 46 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26796 | 426,797
80 | 46 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26798 | 426,799
80 | 46 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26800 | 426,801
80 | 46 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26802 | 426,803
80 | 46 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26812 | 426,813
80 | 46 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26814 | 426,815
80 | 46 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26816 | 426,817
80 | 46 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26818 | 426,819
80 | 46 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26820 | 426,821
80 | 46 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26822 | 426,823
80 | 46 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26824 | 426,825
80 | 46 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26826 | 426,827
80 | 47 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26906 | 426,907
80 | 47 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26908 | 426,909
80 | 47 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26910 | 426,911
80 | 47 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 26912 | 426,913
80 | 47 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 26998 | 426,999
80 | 47 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 26914 | 426,915
80 | 47 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 26916 | 426,917
80 | 47 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 26918 | 426,919
80 | 47 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 26920 | 426,921
80 | 47 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 26922 | 426,923
80 | 47 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 26924 | 426,925
80 | 47 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26926 | 426,927
80 | 47 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26928 | 426,929
80 | 47 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26930 | 426,931
80 | 47 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26932 | 426,933
80 | 47 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26934 | 426,935
80 | 47 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26936 | 426,937
80 | 47 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26938 | 426,939
80 | 47 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 26940 | 426,941
80 | 47 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26942 | 426,943
80 | 47 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26944 | 426,945
80 | 47 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26946 | 426,947
80 | 47 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26948 | 426,949
80 | 47 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26950 | 426,951
80 | 47 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26952 | 426,953
80 | 47 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 26954 | 426,955
80 | 47 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 26956 | 426,957
80 | 47 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26958 | 426,959
80 | 47 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26960 | 426,961
80 | 47 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26962 | 426,963
80 | 47 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 26964 | 426,965
80 | 47 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26966 | 426,967
80 | 47 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26968 | 426,969
80 | 47 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26970 | 426,971
80 | 47 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26972 | 426,973
80 | 47 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26982 | 426,983
80 | 47 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26984 | 426,985
80 | 47 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26986 | 426,987
80 | 47 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 26988 | 426,989
80 | 47 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26990 | 426,991
80 | 47 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26992 | 426,993
80 | 47 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26994 | 426,995
80 | 47 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 26996 | 426,997
80 | 48 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 27076 | 427,077
80 | 48 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 27078 | 427,079
80 | 48 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 27080 | 427,081
80 | 48 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 27082 | 427,083
80 | 48 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 27168 | 427,169
80 | 48 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 27084 | 427,085
80 | 48 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 27086 | 427,087
80 | 48 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 27088 | 427,089
80 | 48 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 27090 | 427,091
80 | 48 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 27092 | 427,093
80 | 48 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 27094 | 427,095
80 | 48 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27096 | 427,097
80 | 48 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27098 | 427,099
80 | 48 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27100 | 427,101
80 | 48 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27102 | 427,103
80 | 48 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27104 | 427,105
80 | 48 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27106 | 427,107
80 | 48 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27108 | 427,109
80 | 48 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27110 | 427,111
80 | 48 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 27112 | 427,113
80 | 48 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27114 | 427,115
80 | 48 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 27116 | 427,117
80 | 48 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27118 | 427,119
80 | 48 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 27120 | 427,121
80 | 48 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27122 | 427,123
80 | 48 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 27124 | 427,125
80 | 48 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27126 | 427,127
80 | 48 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 27128 | 427,129
80 | 48 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 27130 | 427,131
80 | 48 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 27132 | 427,133
80 | 48 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 27134 | 427,135
80 | 48 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27136 | 427,137
80 | 48 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27138 | 427,139
80 | 48 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27140 | 427,141
80 | 48 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27142 | 427,143
80 | 48 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27152 | 427,153
80 | 48 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27154 | 427,155
80 | 48 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27156 | 427,157
80 | 48 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27158 | 427,159
80 | 48 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 27160 | 427,161
80 | 48 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 27162 | 427,163
80 | 48 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 27164 | 427,165
80 | 48 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 27166 | 427,167
80 | 49 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 27246 | 427,247
80 | 49 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 27248 | 427,249
80 | 49 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 27250 | 427,251
80 | 49 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 27252 | 427,253
80 | 49 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 27338 | 427,339
80 | 49 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 27254 | 427,255
80 | 49 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 27256 | 427,257
80 | 49 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 27258 | 427,259
80 | 49 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 27260 | 427,261
80 | 49 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 27262 | 427,263
80 | 49 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 27264 | 427,265
80 | 49 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27266 | 427,267
80 | 49 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27268 | 427,269
80 | 49 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27270 | 427,271
80 | 49 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27272 | 427,273
80 | 49 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27274 | 427,275
80 | 49 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27276 | 427,277
80 | 49 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27278 | 427,279
80 | 49 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27280 | 427,281
80 | 49 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 27282 | 427,283
80 | 49 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27284 | 427,285
80 | 49 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 27286 | 427,287
80 | 49 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27288 | 427,289
80 | 49 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 27290 | 427,291
80 | 49 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27292 | 427,293
80 | 49 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 27294 | 427,295
80 | 49 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27296 | 427,297
80 | 49 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 27298 | 427,299
80 | 49 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 27300 | 427,301
80 | 49 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 27302 | 427,303
80 | 49 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 27304 | 427,305
80 | 49 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27306 | 427,307
80 | 49 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27308 | 427,309
80 | 49 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27310 | 427,311
80 | 49 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27312 | 427,313
80 | 49 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27322 | 427,323
80 | 49 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27324 | 427,325
80 | 49 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27326 | 427,327
80 | 49 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27328 | 427,329
80 | 49 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 27330 | 427,331
80 | 49 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 27332 | 427,333
80 | 49 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 27334 | 427,335
80 | 49 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 27336 | 427,337
80 | 50 | 9 | Profile | Base | Guaranteed Soak Deviation 1 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 27416 | 427,417
80 | 50 | 10 | Profile | Base | Guaranteed Soak Deviation 2 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 27418 | 427,419
80 | 50 | 11 | Profile | Base | Guaranteed Soak Deviation 3 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 27420 | 427,421
80 | 50 | 12 | Profile | Base | Guaranteed Soak Deviation 4 | Set the value of the deviation band that will be used in all profile step types. The process value for control loop must enter the deviation band before the step can proceed. | 0.0 to 9,999.000 | 10.0 | IEEE Float | R/W | 27422 | 427,423
80 | 50 | 19 | Profile | Base |  | Set step edit action. | Edit (1770), Add (1375), Insert (1771), Delete (1772) | Edit (1770) | Enumeration | R/W | 27508 | 427,509
80 | 50 | 21 | Profile | Base | Step Type | Set the step type. | Soak (87), Ramp Time (1928), Ramp Rate (81), Wait For (1542), Instant Change (1927), Jump (116), End (27) | Soak (87) | Enumeration | R/W | 27424 | 427,425
80 | 50 | 22 | Profile | Base | Hours | Set the duration of the step (hours portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 999 | 0 | Unsigned 16-bit | R/W | 27426 | 427,427
80 | 50 | 23 | Profile | Base | Minutes | Set the duration of the step (minutes portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 27428 | 427,429
80 | 50 | 24 | Profile | Base | Seconds | Set the duration of the step (seconds portion) when step types are Soak, Ramp Time, Ramp Rate or Instant Change. | 0 to 59 | 0 | Unsigned 8-bit | R/W | 27430 | 427,431
80 | 50 | 25 | Profile | Base | Jump Step | Set a previous step to jump to when step type is Jump. |  | 1 | Unsigned 8-bit | R/W | 27432 | 427,433
80 | 50 | 26 | Profile | Base | Jump Count | Set the jump count when step type is Jump. | 0 to 9,999 | 1 | Unsigned 16-bit | R/W | 27434 | 427,435
80 | 50 | 27 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27436 | 427,437
80 | 50 | 28 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27438 | 427,439
80 | 50 | 29 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27440 | 427,441
80 | 50 | 30 | Profile | Base | Rate | Set the ramp rate when step type is Ramp Rate. | 0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27442 | 427,443
80 | 50 | 31 | Profile | Base | Target Set Point Loop 1 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27444 | 427,445
80 | 50 | 32 | Profile | Base | Target Set Point Loop 2 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27446 | 427,447
80 | 50 | 33 | Profile | Base | Target Set Point Loop 3 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27448 | 427,449
80 | 50 | 34 | Profile | Base | Target Set Point Loop 4 | Set the target set point when step type is Ramp Time. | -99,999.0 to 99,999.0 | 0.0 | IEEE Float | R/W | 27450 | 427,451
80 | 50 | 35 | Profile | Base | Wait For Process 1 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 27452 | 427,453
80 | 50 | 36 | Profile | Base | Wait For Process 1 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27454 | 427,455
80 | 50 | 37 | Profile | Base | Wait For Process 2 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 27456 | 427,457
80 | 50 | 38 | Profile | Base | Wait For Process 2 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27458 | 427,459
80 | 50 | 39 | Profile | Base | Wait For Process 3 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 27460 | 427,461
80 | 50 | 40 | Profile | Base | Wait For Process 3 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27462 | 427,463
80 | 50 | 41 | Profile | Base | Wait For Process 4 Condition | Set condition for Wait-For step type. | None (61), On (63), Off (62), Above (1964), Below (1965) | None (61) | Enumeration | R/W | 27464 | 427,465
80 | 50 | 42 | Profile | Base | Wait For Process 4 Value | Set value that must be met for Wait-For step type. | -99,999.0 to 9,999.000 | 0.0 | IEEE Float | R/W | 27466 | 427,467
80 | 50 | 43 | Profile | Base | Guaranteed Soak Enable 1 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 27468 | 427,469
80 | 50 | 44 | Profile | Base | Guaranteed Soak Enable 2 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 27470 | 427,471
80 | 50 | 45 | Profile | Base | Guaranteed Soak Enable 3 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 27472 | 427,473
80 | 50 | 46 | Profile | Base | Guaranteed Soak Enable 4 | Set to enable GSD in each step. | Off (62), On (63) | Off (62) | Enumeration | R/W | 27474 | 427,475
80 | 50 | 47 | Profile | Base | Event 1 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27476 | 427,477
80 | 50 | 48 | Profile | Base | Event 2 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27478 | 427,479
80 | 50 | 49 | Profile | Base | Event 3 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27480 | 427,481
80 | 50 | 50 | Profile | Base | Event 4 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27482 | 427,483
80 | 50 | 69 | Profile | Base | Event 5 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27492 | 427,493
80 | 50 | 70 | Profile | Base | Event 6 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27494 | 427,495
80 | 50 | 71 | Profile | Base | Event 7 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27496 | 427,497
80 | 50 | 72 | Profile | Base | Event 8 | Program condition of event outputs at beginning of each step. | Off (62), On (63), Unchanged (1557) | Unchanged (1557) | Enumeration | R/W | 27498 | 427,499
80 | 50 | 73 | Profile | Base | End Action Loop 1 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 27500 | 427,501
80 | 50 | 74 | Profile | Base | End Action Loop 2 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 27502 | 427,503
80 | 50 | 75 | Profile | Base | End Action Loop 3 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 27504 | 427,505
80 | 50 | 76 | Profile | Base | End Action Loop 4 | Set what control loop does after profile exits operation. | User (100), Off (62), Hold (47) | Unchanged (1557) | Enumeration | R/W | 27506 | 427,507
91 | 1 | 1 | Message | Base | Message Enable | Set to enable message. | No (59), Yes (106) | No (59) | Enumeration | R/W | 37546 | 437,547
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37548 | 437,549
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37549 | 437,550
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37550 | 437,551
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37551 | 437,552
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37552 | 437,553
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37553 | 437,554
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37554 | 437,555
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37555 | 437,556
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37556 | 437,557
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37557 | 437,558
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37558 | 437,559
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37559 | 437,560
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37560 | 437,561
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37561 | 437,562
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37562 | 437,563
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37563 | 437,564
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37564 | 437,565
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37565 | 437,566
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37566 | 437,567
91 | 1 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37567 | 437,568
91 | 2 | 1 | Message | Base | Message Enable | Set to enable message. | No (59), Yes (106) | No (59) | Enumeration | R/W | 37706 | 437,707
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37708 | 437,709
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37709 | 437,710
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37710 | 437,711
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37711 | 437,712
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37712 | 437,713
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37713 | 437,714
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37714 | 437,715
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37715 | 437,716
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37716 | 437,717
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37717 | 437,718
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37718 | 437,719
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37719 | 437,720
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37720 | 437,721
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37721 | 437,722
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37722 | 437,723
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37723 | 437,724
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37724 | 437,725
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37725 | 437,726
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37726 | 437,727
91 | 2 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37727 | 437,728
91 | 3 | 1 | Message | Base | Message Enable | Set to enable message. | No (59), Yes (106) | No (59) | Enumeration | R/W | 37866 | 437,867
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37868 | 437,869
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37869 | 437,870
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37870 | 437,871
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37871 | 437,872
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37872 | 437,873
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37873 | 437,874
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37874 | 437,875
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37875 | 437,876
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37876 | 437,877
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37877 | 437,878
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37878 | 437,879
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37879 | 437,880
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37880 | 437,881
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37881 | 437,882
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37882 | 437,883
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37883 | 437,884
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37884 | 437,885
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37885 | 437,886
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37886 | 437,887
91 | 3 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 37887 | 437,888
91 | 4 | 1 | Message | Base | Message Enable | Set to enable message. | No (59), Yes (106) | No (59) | Enumeration | R/W | 38026 | 438,027
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38028 | 438,029
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38029 | 438,030
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38030 | 438,031
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38031 | 438,032
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38032 | 438,033
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38033 | 438,034
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38034 | 438,035
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38035 | 438,036
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38036 | 438,037
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38037 | 438,038
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38038 | 438,039
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38039 | 438,040
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38040 | 438,041
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38041 | 438,042
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38042 | 438,043
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38043 | 438,044
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38044 | 438,045
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38045 | 438,046
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38046 | 438,047
91 | 4 | 2 | Message | Base | Message | Set message to be displayed based on trigger. | 1 byte (UTF-8) |  | String | R/W | 38047 | 438,048

## Modbus Map 2
Class Name | Module | Member Name | Description | Range/Enumerations | Default Value | Data Type | Access | Relative Address | Absolute Address | Legacy Models
Device | Base | Model | Monitor the hardware ID. | 5270 | 5270 | 16-bit unsigned | R | 0 | 400,001 | F4S, F4D, F4P
Device | Base | Software Number | Monitor the software ID. | 1 to 99 (1 is standard software) | no default | 16-bit unsigned | R | 3 | 400,004 | F4S, F4D, F4P
Device | Base | Software Revision | Monitor the software release version. | 0 to 99 | no default | 16-bit unsigned | R | 4 | 400,005 | F4S, F4D, F4P
Device | Base | Save Changes to EE | Save Changes to EE | Save (0) | no default | 16-bit unsigned | W | 25 | 400,026 | F4S, F4D, F4P
Device | Base | Software Build Number | Monitor the software build number. | 100 to 32767 (in hundredths) | no default | 16-bit unsigned | R | 30 | 400,031 | F4S, F4D, F4P
Control Loop | Base | Decimal Point, Analog Input 1 | Monitor the value for control loop 1, inner loop sensor. | -32768 to 32767 (in integer, tenths, hundredths or thousandths) | no default | 16-bit signed | R | 100 | 400,101 | F4S, F4D, F4P
Control Loop | Base | Input 1 Error Status | Monitor the error status of sensor 1. | None (0), AtoD Under Flow (1), Sensor Under Range (2), Sensor Over Range (3), AtoD Over Flow (4), AtoD Timeout (5), Open Loop (6) | no default | 16-bit unsigned | R | 101 | 400,102 | F4S, F4D, F4P
Control Loop | Base | Input 2 Value | Monitor the value for control loop 2 sensor, | (-32768 to 32767) in integer, tenths, hundredths or thousandths | no default | 16-bit signed | R | 104 | 400,105 | F4S, F4D, F4P
Control Loop | Base | Input 2 Error Status | Monitor the error status of sensor 2. | None (0), AtoD Under Flow (1), Sensor Under Range (2), Sensor Over Range (3), AtoD Over Flow (4), AtoD Timeout (5), Open Loop (6) | no default | 16-bit unsigned | R | 105 | 400,106 | F4S, F4D, F4P
Control Loop | Base | Set Point 1, Value | Set the static closed loop set point for control loop 1. | -32768 to 32767 (in integer, tenths, hundredths or thousandths) | 75 | 16-bit signed | R/W | 300 | 400,301 | F4S, F4D, F4P
Control Loop | Base | Idle Set Point, Channel 1 | Set idle set point value to use when active for control loop 1. | -32768 to 32767 (in integer, tenths, hundredths or thousandths) | 75 | 16-bit signed | R/W | 308 | 400,309 | F4S, F4D
Control Loop | Base | Set Point 2, Value | Set the static closed loop set point for control loop 2. | -32768 to 32767 (in integer, tenths, hundredths or thousandths) | no default | 16-bit signed | R | 319 | 400,320 | F4S, F4D
Control Loop | Base | Idle Set Point, Channel 2 | Set idle set point value to use when active for control loop 2. | -32768 to 32767 (in integer, tenths, hundredths or thousandths) | 75 | 16-bit signed | R/W | 327 | 400,328 | F4S, F4D
Control Loop | Base | Decimal Point, Analog Input 1 | Specify resolution to display. | 0 (0), 0.0 (1), 0.00 (2), 0.000 (3) | 0 (0) | 16-bit unsigned | R/W | 606 | 400,607 | F4S, F4D, F4P
Control Loop | Base | Decimal Point, Analog Input 2 | Specify resolution to display. | 0 (0), 0.0 (1), 0.00 (2), 0.000 (3) | 0 (0) | 16-bit unsigned | R/W | 616 | 400,617 | F4S, F4D, F4P
Device | Base | Modbus Units | Specify the units used through Modbus | F (0), C (1) | F (0) | 16-bit unsigned | R/W | 901 | 400,902 | F4S, F4D
Control Loop | Base | Ramp to Set Point Mode | Specify the ramp action. | Off (0), Startup (1), Startup or Change (2) | Off (0) | 16-bit unsigned | R/W | 1100 | 401,101 | F4P
Control Loop | Base | Ramp to Set Point Rate | Specify the rate to ramp when active. | 1 to 999 (degrees or units per minute or hour) | 1 | 16-bit unsigned | R/W | 1101 | 401,102 | F4P
Control Loop | Base | Ramp to Set Point Scale | Specify the ramp scale to apply. | Minutes (0), Hours (1) | Minutes (0) | 16-bit unsigned | R/W | 1102 | 401,103 | F4P
Profile | Base | Resume a Profile, Key Press Simulation | Request to resume a profile on hold. | Resume a Profile (1) | no default | 16-bit unsigned | W | 1209 | 401,210 | F4S, F4D
Profile | Base | Hold a Profile, Key Press Simulation | Request to hold a profile. | Hold a Profile (1) | no default | 16-bit unsigned | W | 1210 | 401,211 | F4S, F4D
Profile | Base | Terminate a Profile, Key Press Simulation | Request to terminate a running profile. | Terminate a Profile (1) | no default | 16-bit unsigned | W | 1217 | 401,218 | F4S, F4D
Profile | Base | Digital Output 1, Condition | Specify level of digital output when active. | Low (0), High (1) | Low (0) | 16-bit unsigned | R/W | 2000 | 402,001 | F4S, F4D
Profile | Base | Digital Output 2, Condition | Specify level of digital output when active. | Low (0), High (1) | Low (0) | 16-bit unsigned | R/W | 2010 | 402,011 | F4S, F4D
Profile | Base | Digital Output 3, Condition | Specify level of digital output when active. | Low (0), High (1) | Low (0) | 16-bit unsigned | R/W | 2020 | 402,021 | F4S, F4D
Profile | Base | Digital Output 4, Condition | Specify level of digital output when active. | Low (0), High (1) | Low (0) | 16-bit unsigned | R/W | 2030 | 402,031 | F4S, F4D
Profile | Base | Digital Output 5, Condition | Specify level of digital output when active. | Low (0), High (1) | Low (0) | 16-bit unsigned | R/W | 2040 | 402,041 | F4S, F4D
Profile | Base | Digital Output 6, Condition | Specify level of digital output when active. | Low (0), High (1) | Low (0) | 16-bit unsigned | R/W | 2050 | 402,051 | F4S, F4D
Profile | Base | Digital Output 7, Condition | Specify level of digital output when active. | Low (0), High (1) | Low (0) | 16-bit unsigned | R/W | 2060 | 402,061 | F4S, F4D
Profile | Base | Digital Output 8, Condition | Specify level of digital output when active. | Low (0), High (1) | Low (0) | 16-bit unsigned | R/W | 2070 | 402,071 | F4S, F4D
Profile | Base | Profile Number | Specify which profile number to load into memory. | 1 to 40 | 0 | 16-bit unsigned | R/W | 4000 | 404,001 | F4S, F4D
Profile | Base | Profile Step Number | Specify which profile step to load into memory. | 1 to 256 | 1 | 16-bit unsigned | R/W | 4001 | 404,002 | F4S, F4D
Profile | Base | Profile Edit Action | Specify profile edit action. | Delete Current Profile (3), Delete Current Step (4), Start Profile (5), Delete All Profiles (255) |  | 16-bit unsigned | R/W | 4002 | 404,003 | F4S, F4D
Profile | Base | Event Output 1, Ramp Rate or Ramp Time or Soak Steps | Specify to activate the output. | Off (0), On (1) | Off (0) | 16-bit unsigned | R/W | 4030 | 404,031 | F4S, F4D
Profile | Base | Event Output 2, Ramp Rate or Ramp Time or Soak Steps | Specify to activate the output. | Off (0), On (1) | Off (0) | 16-bit unsigned | R/W | 4031 | 404,032 | F4S, F4D
Profile | Base | Event Output 3, Ramp Rate or Ramp Time or Soak Steps | Specify to activate the output. | Off (0), On (1) | Off (0) | 16-bit unsigned | R/W | 4032 | 404,033 | F4S, F4D
Profile | Base | Event Output 4, Ramp Rate or Ramp Time or Soak Steps | Specify to activate the output. | Off (0), On (1) | Off (0) | 16-bit unsigned | R/W | 4033 | 404,034 | F4S, F4D
Profile | Base | Event Output 5, Ramp Rate or Ramp Time or Soak Steps | Specify to activate the output. | Off (0), On (1) | Off (0) | 16-bit unsigned | R/W | 4034 | 404,035 | F4S, F4D
Profile | Base | Event Output 6, Ramp Rate or Ramp Time or Soak Steps | Specify to activate the output. | Off (0), On (1) | Off (0) | 16-bit unsigned | R/W | 4035 | 404,036 | F4S, F4D
Profile | Base | Event Output 7, Ramp Rate or Ramp Time or Soak Steps | Specify to activate the output. | Off (0), On (1) | Off (0) | 16-bit unsigned | R/W | 4036 | 404,037 | F4S, F4D
Profile | Base | Event Output 8, Ramp Rate or Ramp Time or Soak Steps | Specify to activate the output. | Off (0), On (1) | Off (0) | 16-bit unsigned | R/W | 4037 | 404,038 | F4S, F4D
Profile | Base | Digital Output 1, Current Status | Monitor the state of the output. | Off (0), On (1) | no default | 16-bit unsigned | R | 4111 | 404,112 | F4S, F4D
Profile | Base | Digital Output 2, Current Status | Monitor the state of the output. | Off (0), On (1) | no default | 16-bit unsigned | R | 4112 | 404,113 | F4S, F4D
Profile | Base | Digital Output 3, Current Status | Monitor the state of the output. | Off (0), On (1) | no default | 16-bit unsigned | R | 4113 | 404,114 | F4S, F4D
Profile | Base | Digital Output 4, Current Status | Monitor the state of the output. | Off (0), On (1) | no default | 16-bit unsigned | R | 4114 | 404,115 | F4S, F4D
Profile | Base | Digital Output 5, Current Status | Monitor the state of the output. | Off (0), On (1) | no default | 16-bit unsigned | R | 4115 | 404,116 | F4S, F4D
Profile | Base | Digital Output 6, Current Status | Monitor the state of the output. | Off (0), On (1) | no default | 16-bit unsigned | R | 4116 | 404,117 | F4S, F4D
Profile | Base | Digital Output 7, Current Status | Monitor the state of the output. | Off (0), On (1) | no default | 16-bit unsigned | R | 4117 | 404,118 | F4S, F4D
Profile | Base | Digital Output 8, Current Status | Monitor the state of the output. | Off (0), On (1) | no default | 16-bit unsigned | R | 4118 | 404,119 | F4S, F4D
Control Loop | Base | Set Point Channel 1, Ramp Rate, Ramp Time or Soak Step, Current Profile Status | Monitor the requested set point in the current running step. | -32768 to 32767 (in integer, tenths, hundreths or thousandths) | no default | 16-bit signed | R | 4122 | 404,123 | F4S, F4D
Control Loop | Base | Set Point Channel 2, Ramp Rate, Ramp Time or Soak Step, Current Profile Status | Monitor the requested set point in the current running step. | -32768 to 32767 (in integer, tenths, hundreths or thousandths) | no default | 16-bit signed | R | 4123 | 404,124 | F4S, F4D
Control Loop | Base | Set Point Channel 1, Ramp Rate, Ramp Time or Soak Step, Current Profile Status | Monitor the requested set point in the current running step. | -32768 to 32767 (in integer, tenths, hundreths or thousandths) | no default | 16-bit signed | R | 4190 | 404,191 | F4S, F4D

## Modbus Map 3
Class Name | Module | Member Name | Description | Range/Enumerations | Default Value | Data Type | Access | Relative Address | Absolute Address | Legacy Models
Device | Base | Model | Monitor the hardware ID. | 5270 | 5270 | 16-bit unsigned | R | 0 | 400,001 | F4S, F4D, F4P
Device | Base | Software Number | Monitor the software ID. | 1 to 99 (1 is standard software) | no default | 16-bit unsigned | R | 3 | 400,004 | F4S, F4D, F4P
Device | Base | Software Revision | Monitor the software release version. | 0 to 99 | no default | 16-bit unsigned | R | 4 | 400,005 | F4S, F4D, F4P
Device | Base | Save Changes to EE | Save Changes to EE | Save (0) | no default | 16-bit unsigned | W | 25 | 400,026 | F4S, F4D, F4P
Device | Base | Software Build Number | Monitor the software build number. | 100 to 32767 (in hundreths) | no default | 16-bit unsigned | R | 30 | 400,031 | F4S, F4D, F4P
Cascade | Base | Input 1 Value | Monitor the value for control loop 1, inner loop sensor. | -32768 to 32767 (in integer, tenths, hundreths or thousandths) | no default | 16-bit signed | R | 100 | 400,101 | F4S, F4D, F4P
Cascade | Base | Input 1 Error Status | Monitor the error status of sensor 1. | None (0), AtoD Under Flow (1), Sensor Under Range (2), Sensor Over Range (3), AtoD Over Flow (4), AtoD Timeout (5), Open Loop (6) | no default | 16-bit unsigned | R | 101 | 400,102 | F4S, F4D, F4P
Control Loop | Base | Input 2 Value | Monitor the value for control loop 2 sensor, | (-32768 to 32767) in integer, tenths, hundreths or thousandths | no default | 16-bit signed | R | 104 | 400,105 | F4S, F4D, F4P
Control Loop | Base | Input 2 Error Status | Monitor the error status of sensor 2. | None (0), AtoD Under Flow (1), Sensor Under Range (2), Sensor Over Range (3), AtoD Over Flow (4), AtoD Timeout (5), Open Loop (6) | no default | 16-bit unsigned | R | 105 | 400,106 | F4S, F4D, F4P
Cascade | Base | Input 1 Value | Monitor the value for control loop 1, outer loop sensor. |  |  | 16-bit signed | R | 108 | 400,109 | F4S, F4D, F4P
Cascade | Base | Input 1 Error Status | Monitor the error status of outer loop sensor 1. |  |  | 16-bit unsigned | R | 109 | 400,110 | F4S, F4D, F4P
Cascade | Base | Set Point 1, Value | Set the static closed loop set point for control loop 1. | -32768 to 32767 (in integer, tenths, hundreths or thousandths) | 75 | 16-bit signed | R/W | 300 | 400,301 | F4S, F4D, F4P
Control Loop | Base | Idle Set Point, Channel 1 | Set idle set point value to use when active for control loop 1. | -32768 to 32767 (in integer, tenths, hundreths or thousandths) | 75 | 16-bit signed | R/W | 308 | 400,309 | F4S, F4D
Control Loop | Base | Set Point 2, Value | Set the static closed loop set point for control loop 2. | -32768 to 32767 (in integer, tenths, hundreths or thousandths) | no default | 16-bit signed | R | 319 | 400,320 | F4S, F4D
Control Loop | Base | Idle Set Point, Channel 2 | Set idle set point value to use when active for control loop 2. | -32768 to 32767 (in integer, tenths, hundreths or thousandths) | 75 | 16-bit signed | R/W | 327 | 400,328 | F4S, F4D
Cascade | Base | Decimal Point, Analog Input 1 | Specify resolution to display. | 0 (0), 0.0 (1), 0.00 (2), 0.000 (3) | 0 (0) | 16-bit unsigned | R/W | 606 | 400,607 | F4S, F4D, F4P
Control Loop | Base | Decimal Point, Analog Input 2 | Specify resolution to display. | 0 (0), 0.0 (1), 0.00 (2), 0.000 (3) | 0 (0) | 16-bit unsigned | R/W | 616 | 400,617 | F4S, F4D, F4P
Cascade | Base | Input 1 Value | Monitor the value for control loop 1, outer loop sensor. |  |  | 16-bit signed | R | 626 | 400,627 | F4S, F4D, F4P
Device | Base | Modbus Units | Specify the units used through Modbus | F (0), C (1) | F (0) | 16-bit unsigned | R/W | 901 | 400,902 | F4S, F4D
Control Loop | Base | Ramp to Set Point Mode | Specify the ramp action. | Off (0), Startup (1), Startup or Change (2) | Off (0) | 16-bit unsigned | R/W | 1100 | 401,101 | F4P
Control Loop | Base | Ramp to Set Point Rate | Specify the rate to ramp when active. | 1 to 999 (derees or units per minute or hour | 1 | 16-bit unsigned | R/W | 1101 | 401,102 | F4P
Control Loop | Base | Ramp to Set Point Scale | Specify the ramp scale to apply. | Minutes (0), Hours (1) | Minutes (0) | 16-bit unsigned | R/W | 1102 | 401,103 | F4P
Profile | Base | Resume a Profile, Key Press Simulation | Request to resume a profile on hold. | Resume a Profile (1) | no default | 16-bit unsigned | W | 1209 | 401,210 | F4S, F4D
Profile | Base | Hold a Profile, Key Press Simulation | Request to hold a profile. | Hold a Profile (1) | no default | 16-bit unsigned | W | 1210 | 401,211 | F4S, F4D
Profile | Base | Terminate a Profile, Key Press Simulation | Request to terminate a running profile. | Terminate a Profile (1) | no default | 16-bit unsigned | W | 1217 | 401,218 | F4S, F4D
Cascade | Base | Inner Set Point Channel 1 |  |  |  | 16-bit signed | R | 1922 | 401,923 | F4S, F4D, F4P
Profile | Base | Digital Output 1, Condition | Specify level of digital output when active. | Low (0), High (1) | High (1) | 16-bit unsigned | R/W | 2000 | 402,001 | F4S, F4D
Profile | Base | Digital Output 2, Condition | Specify level of digital output when active. | Low (0), High (1) | High (1) | 16-bit unsigned | R/W | 2010 | 402,011 | F4S, F4D
Profile | Base | Digital Output 3, Condition | Specify level of digital output when active. | Low (0), High (1) | High (1) | 16-bit unsigned | R/W | 2020 | 402,021 | F4S, F4D
Profile | Base | Digital Output 4, Condition | Specify level of digital output when active. | Low (0), High (1) | High (1) | 16-bit unsigned | R/W | 2030 | 402,031 | F4S, F4D
Profile | Base | Digital Output 5, Condition | Specify level of digital output when active. | Low (0), High (1) | High (1) | 16-bit unsigned | R/W | 2040 | 402,041 | F4S, F4D
Profile | Base | Digital Output 6, Condition | Specify level of digital output when active. | Low (0), High (1) | High (1) | 16-bit unsigned | R/W | 2050 | 402,051 | F4S, F4D
Profile | Base | Digital Output 7, Condition | Specify level of digital output when active. | Low (0), High (1) | High (1) | 16-bit unsigned | R/W | 2060 | 402,061 | F4S, F4D
Profile | Base | Digital Output 8, Condition | Specify level of digital output when active. | Low (0), High (1) | High (1) | 16-bit unsigned | R/W | 2070 | 402,071 | F4S, F4D
Profile | Base | Profile Number | Specify which profile number to load into memory. | 1 to 40 | 0 | 16-bit unsigned | R/W | 4000 | 404,001 | F4S, F4D
Profile | Base | Profile Step Number | Specify which profile step to load into memory. | 1 to 256 | 1 | 16-bit unsigned | R/W | 4001 | 404,002 | F4S, F4D
Profile | Base | Profile Edit Action | Specify profile edit action. | Delete Current Profile (3), Delete Current Step (4), Start Profile (5), Delete All Profiles (255) |  | 16-bit unsigned | R/W | 4002 | 404,003 | F4S, F4D
Profile | Base | Event Output 1, Ramp Rate or Ramp Time or Soak Steps | Specify to activate the output. | Off (0), On (1) | Off (0) | 16-bit unsigned | R/W | 4030 | 404,031 | F4S, F4D
Profile | Base | Event Output 2, Ramp Rate or Ramp Time or Soak Steps | Specify to activate the output. | Off (0), On (1) | Off (0) | 16-bit unsigned | R/W | 4031 | 404,032 | F4S, F4D
Profile | Base | Event Output 3, Ramp Rate or Ramp Time or Soak Steps | Specify to activate the output. | Off (0), On (1) | Off (0) | 16-bit unsigned | R/W | 4032 | 404,033 | F4S, F4D
Profile | Base | Event Output 4, Ramp Rate or Ramp Time or Soak Steps | Specify to activate the output. | Off (0), On (1) | Off (0) | 16-bit unsigned | R/W | 4033 | 404,034 | F4S, F4D
Profile | Base | Event Output 5, Ramp Rate or Ramp Time or Soak Steps | Specify to activate the output. | Off (0), On (1) | Off (0) | 16-bit unsigned | R/W | 4034 | 404,035 | F4S, F4D
Profile | Base | Event Output 6, Ramp Rate or Ramp Time or Soak Steps | Specify to activate the output. | Off (0), On (1) | Off (0) | 16-bit unsigned | R/W | 4035 | 404,036 | F4S, F4D
Profile | Base | Event Output 7, Ramp Rate or Ramp Time or Soak Steps | Specify to activate the output. | Off (0), On (1) | Off (0) | 16-bit unsigned | R/W | 4036 | 404,037 | F4S, F4D
Profile | Base | Event Output 8, Ramp Rate or Ramp Time or Soak Steps | Specify to activate the output. | Off (0), On (1) | Off (0) | 16-bit unsigned | R/W | 4037 | 404,038 | F4S, F4D
Profile | Base | Digital Output 1, Current Status | Monitor the state of the output. | Off (0), On (1) | no default | 16-bit unsigned | R | 4111 | 404,112 | F4S, F4D
Profile | Base | Digital Output 2, Current Status | Monitor the state of the output. | Off (0), On (1) | no default | 16-bit unsigned | R | 4112 | 404,113 | F4S, F4D
Profile | Base | Digital Output 3, Current Status | Monitor the state of the output. | Off (0), On (1) | no default | 16-bit unsigned | R | 4113 | 404,114 | F4S, F4D
Profile | Base | Digital Output 4, Current Status | Monitor the state of the output. | Off (0), On (1) | no default | 16-bit unsigned | R | 4114 | 404,115 | F4S, F4D
Profile | Base | Digital Output 5, Current Status | Monitor the state of the output. | Off (0), On (1) | no default | 16-bit unsigned | R | 4115 | 404,116 | F4S, F4D
Profile | Base | Digital Output 6, Current Status | Monitor the state of the output. | Off (0), On (1) | no default | 16-bit unsigned | R | 4116 | 404,117 | F4S, F4D
Profile | Base | Digital Output 7, Current Status | Monitor the state of the output. | Off (0), On (1) | no default | 16-bit unsigned | R | 4117 | 404,118 | F4S, F4D
Profile | Base | Digital Output 8, Current Status | Monitor the state of the output. | Off (0), On (1) | no default | 16-bit unsigned | R | 4118 | 404,119 | F4S, F4D
Cascade | Base | Outer Set Point Channel 1, Ramp Rate, Ramp Time or Soak Step, Current Profile Status | Monitor the requested set point in the current running step. | -32768 to 32767 (in integer, tenths, hundreths or thousandths) | no default | 16-bit signed | R | 4122 | 404,123 | F4S, F4D, F4P
Control Loop | Base | Set Point Channel 2, Ramp Rate, Ramp Time or Soak Step, Current Profile Status | Monitor the requested set point in the current running step. | -32768 to 32767 (in integer, tenths, hundreths or thousandths) | no default | 16-bit signed | R | 4123 | 404,124 | F4S, F4D, F4P
Cascade | Base | Outer Loop Set Point Channel 1, Ramp Rate, Ramp Time or Soak Step, Current Profile Status | Monitor the requested set point in the current running step. | -32768 to 32767 (in integer, tenths, hundreths or thousandths) | no default | 16-bit signed | R | 4190 | 404,191 | F4S, F4D, F4P

## SCPI
Description | Read/Write | Command | Command Type | Notes | Additional Notes
Read Identification | R | *IDN? | IEEE 488.2 | returns manufacturer, serial number, firmware level | For SCPI Commands: the first colon and items in [] are optional
Read communications temperature units | R | UNIT:TEMPerature? | Display Units | always present | For SCPI Commands: letters in upper case are mandatory, lower case characters are optional
Set communications temperature units to °C | W | UNIT:TEMPeratureC | Display Units | always present | For SCPI Commands: replace # with instance targeted (1 for loop 1, 2 for loop 2, etc.)
Set communications temperature units to °F | W | UNIT:TEMPeratureF | Display Units | always present | SCPI uses port 5025 for connection.
Read displayed temperature units | R | UNIT:TEMPerature:DISPlay? | Display Units | always present | SCPI Read is a SCPI command that gets data from the F4T/D4T (i.e. a command that ends with a "?").
Set diisplayed temperature units to °C | W | UNIT:TEMPerature:DISPlay C | Display Units | always present | SCPI Write is a SCPI command that sets data in the F4T/D4T (i.e. a command that ends with a value).
Set displayed temperature units to °F | W | UNIT:TEMPerature:DISPlay F | Display Units | always present | Socket Send is when the socket/connection sends data, regardless of a SCPI Read or Write, to the F4T/D4T.
Read PV(Control loop) | R | SOURce:CLOop#:PVALue? | Control Loop | # = 1 to 4 if control loop present | Socket Receive is when the socket/connection gets data from the F4T/D4T.
Read input error | R | SOURce:CLOop#:ERRor? | Control Loop | # = 1 to 4 if control loop present | When communicating to the F4T/D4T via SCPI over sockets, a Socket Receive needs to follow a Socket Send. This is because the F4T/D4T responds to all incoming SCPI traffic as a form of acknowledgment.
Read SP | R | SOURce:CLOop#:SPOint? | Control Loop | # = 1 to 4 if control loop present | When a SCPI Read occurs, a Socket Send sends the command to the F4T/D4T. A Socket Receive then needs to occur to read all the requested value.
Write SP | W | SOURce:CLOop#:SPOint <numeric value> | Control Loop | # = 1 to 4 if control loop present | When a SCPI Write occurs, a Socket Send sends the command to the F4T/D4T. A Socket Receive then needs to occur to read the new line character "\n" that with which the F4T/D4T responds.
Read Idle SP | R | SOURce:CLOop#:IDLE? | Control Loop | # = 1 to 4 if control loop present
Write Idle SP | W | SOURce:CLOop#:IDLE <numeric value> | Control Loop | # = 1 to 4 if control loop present
Set ramping off | W | SOURce:CLOop#:RACTion OFF | Control Loop | # = 1 to 4 if control loop present
Set ramping on PWR applied | W | SOURce:CLOop#:RACTion STARTUP | Control Loop | # = 1 to 4 if control loop present
Set ramping on SP change | W | SOURce:CLOop#:RACTion SETPOINT | Control Loop | # = 1 to 4 if control loop present
Set ramping on both SP and PWR events | W | SOURce:CLOop#:RACTion BOTH | Control Loop | # = 1 to 4 if control loop present
Write ramp scale to minutes | W | SOURce:CLOop#:RSCAle MINUTES | Control Loop | # = 1 to 4 if control loop present
Write ramp scale to hours | W | SOURce:CLOop#:RSCAle HOURS | Control Loop | # = 1 to 4 if control loop present
Read ramp rate | R | SOURce:CLOop#:RRATe? | Control Loop | # = 1 to 4 if control loop present
Read ramp rate | R | SOURce:CLOop#:RTIMe? | Control Loop | # = 1 to 4 if control loop present
Write ramp rate | W | SOURce:CLOop#:RRATe <numeric value> | Control Loop | # = 1 to 4 if control loop present
Write ramp rate | W | SOURce:CLOop#:RTIMe <numeric value> | Control Loop | # = 1 to 4 if control loop present
Read cascade setpoint | R | SOURce:CAScade#:SPOint? | Cascade Control Loop | # = 1 to 2 if cascade loop present
Set cascade setpoint | W | SOURce:CAScade#:SPOint <numeric value> | Cascade Control Loop | # = 1 to 2 if cascade loop present
Read outer loop process value | R | SOURce:CAScade#:OUTer:PVALue? | Cascade Control Loop | # = 1 to 2 if cascade loop present
Read outer loop input error | R | SOURce:CAScade#:OUTer:ERRor? | Cascade Control Loop | # = 1 to 2 if cascade loop present
Read inner loop process value | R | SOURce:CAScade#:INNer:PVALue? | Cascade Control Loop | # = 1 to 2 if cascade loop present
Read inner loop input error | R | SOURce:CAScade#:INNer:ERRor? | Cascade Control Loop | # = 1 to 2 if cascade loop present
Read outer loop set point | R | SOURce:CAScade#:OUTer:SPOint? | Cascade Control Loop | # = 1 to 2 if cascade loop present
Read inner loop set point | R | SOURce:CAScade#:INNer:SPOint? | Cascade Control Loop | # = 1 to 2 if cascade loop present
Read cascade loop function | R | SOURce:CAScade#:FUNCtion? | Cascade Control Loop | # = 1 to 2 if cascade loop present
Set cascade loop function to PROCESS | W | SOURce:CAScade#:FUNCtion PROCESS | Cascade Control Loop | # = 1 to 2 if cascade loop present
Set cascade loop function to DEVIATION | W | SOURce:CAScade#:FUNCtion DEVIATION | Cascade Control Loop | # = 1 to 2 if cascade loop present
Read cascade range low | R | SOURce:CAScade#:RANGe:LOW? | Cascade Control Loop | # = 1 to 2 if cascade loop present
Set cascade range low | W | SOURce:CAScade#:RANGe:LOW <numeric value> | Cascade Control Loop | # = 1 to 2 if cascade loop present
Read cascade range high | R | SOURce:CAScade#:RANGe:HIGH? | Cascade Control Loop | # = 1 to 2 if cascade loop present
Set cascade range high | W | SOURce:CAScade#:RANGe:HIGH <numeric value> | Cascade Control Loop | # = 1 to 2 if cascade loop present
Read cascade control mode | R | SOURce:CAScade#:CONTrol? | Cascade Control Loop | # = 1 to 2 if cascade loop present
Set cascade control mode to OFF | W | SOURce:CAScade#:CONTrol OFF | Cascade Control Loop | # = 1 to 2 if cascade loop present
Set cascade control mode to COOL | W | SOURce:CAScade#:CONTrol COOL | Cascade Control Loop | # = 1 to 2 if cascade loop present
Set cascade control mode to HEAT | W | SOURce:CAScade#:CONTrol HEAT | Cascade Control Loop | # = 1 to 2 if cascade loop present
Set cascade control mode to BOTH | W | SOURce:CAScade#:CONTrol BOTH | Cascade Control Loop | # = 1 to 2 if cascade loop present
Read cascade simple set point control | R | SOURce:CAScade#:SSPoint:CONTrol? | Cascade Control Loop | # = 1 to 2 if cascade loop present
Set cascade simple set point control OFF | W | SOURce:CAScade#:SSPoint:CONTrol OFF | Cascade Control Loop | # = 1 to 2 if cascade loop present
Set cascade simple set point control ON | W | SOURce:CAScade#:SSPoint:CONTrol ON | Cascade Control Loop | # = 1 to 2 if cascade loop present
Read softkey state | R | KEY#[:STATe]? | Softkey | softkey implemented
Write to toggle softkey state | W | KEY#[:STATe] PRESs | Softkey | softkey implemented
Read softkey name | R | KEY#:NAME? | Softkey | softkey implemented
Read active profile number | R | PROGram[:SELected]:NUMBer? | Profile | profile option available and created
Select a profile | W | PROGram[:SELected]:NUMBer <integer value> | Profile | profile option available and created
Read selected profile name | R | PROGram[:SELected]:NAME? | Profile | profile option available and created
Read profile state | R | PROGram[:SELected]:STATe? | Profile | profile option available and created
Start profile | W | PROGram[:SELected]:STATe START | Profile | profile option available and created
Stop running profile | W | PROGram[:SELected]:STATE STOP | Profile | profile option available and created
Pause running profile | W | PROGram[:SELected]:STATE PAUSE | Profile | profile option available and created
Resume paused profile | W | PROGram[:SELected]:STATE RESUME | Profile | profile option available and created
Read current process profile set point | R | PROGram[:SELected]:SPOint? | Profile | profile option available and created
Read active profile number | R | PROGram[:SELected]:STEP? | Profile | profile option available and created
Read current profile step type | R | PROGram[:SELected]:STEP TYPE? | Profile | profile option available and created
Read profile step time elapsed | R | PROGram[:SELected]:TIME ELApsed? | Profile | profile option available and created
Read profile step time remaining | R | PROGram[:SELected]:TIME REMain? | Profile | profile option available and created
Select a profile step | W | PROGram[:SELected]:STEP <integer value> | Profile | profile option available and created
Read event output state | R | OUTPut#[:STATe]? | Profile | # = 1 to 8 if output event output present
Set event output on | W | OUTPut#[:STATe] ON | Profile | # = 1 to 8 if output event output present
Set event output off | W | OUTPut#[:STATe] OFF | Profile | # = 1 to 8 if output event output present
Read event output name | R | OUTPut#:NAME? | Profile | # = 1 to 8 if output event output present

## EtherNet IP
Class ID | Instance ID | Attribute ID | Class Name | Module | Attribute Name | Description | Range/Enumerations | Default Value | Data Type | Access | Max Instances | Implicit
101 | 1 | 1 | Device | Base | Hardware ID | Monitor the hardware ID. | 0 to 65,535 | 124 | DINT | R | 1 | No
101 | 1 | 2 | Device | Base | Software ID | Monitor the software ID. | 0 to 2,147,483,647 |  | DINT | R | 1 | No
101 | 1 | 3 | Device | Base | Software Release Version | Monitor the software release version. For example, if the About screen is showing 04:06:0008, 4 will be returned. | 0 to 2,147,483,647 |  | DINT | R | 1 | No
101 | 1 | 4 | Device | Base | Software Prototype Version | Monitor the prototype version if prototype. For example, if the About screen is showing 04:06:0008, 6 will be returned. | 0 to 2,147,483,647 |  | DINT | R | 1 | No
101 | 1 | 5 | Device | Base | Software Build Number | Monitor the software build number. For example, if the About screen is showing 04:06:0008, 8 will be returned. | 0 to 2,147,483,647 |  | DINT | R | 1 | No
101 | 1 | 6 | Device | Base | Firmware Branch Number | Monitor the firmware branch number. | 0 to 2,147,483,647 |  | DINT | R | 1 | No
101 | 1 | 7 | Device | Base | Serial Number | Monitor the serial number. | 0 to 2,147,483,647 |  | DINT | R | 1 | No
101 | 1 | 8 | Device | Base | Date of Manufacture | Monitor the date the hardware was manufactured. Serial number in format YYDDD | 0 to 2,147,483,647 |  | DINT | R | 1 | No
101 | 1 | 9 | Device | Base | Part Number | Monitor the model number of the base. | 15 bytes (UTF-8) | F4T1A1A1A1A5000 | SHORT_STRING | R | 1 | No
101 | 1 | 11 | Device | Base | Device Name | Set the name to assign the base. | 32 bytes (UTF-8) | F4T | SHORT_STRING | R/W | 1 | No
101 | 1 | 13 | Device | Base | Restore Settings From | Set to restore factory settings. | None (61), Factory (31) | None (61) | UINT | R/W | 1 | No
101 | 1 | 16 | Device | Base | Device Status | Monitor the base for failure. | OK (138), Fail (32) |  | UINT | R | 1 | No
101 | 1 | 17 | Device | Base | Software Revision |  | 5 bytes (UTF-8) |  | SHORT_STRING | R | 1 | No
101 | 1 | 34 | Device | Base | AC Line Frequency | Set the frequency used for variable time base control. | 50 Hz (3), 60 Hz (4) | 60 Hz (4) | UINT | R/W | 1 | No
102 | 1 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 1 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 1 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 1 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 1 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 1 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 1 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 1 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 2 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 2 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 2 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 2 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 2 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 2 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 2 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 2 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 3 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 3 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 3 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 3 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 3 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 3 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 3 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 3 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 4 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 4 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 4 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 4 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 4 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 4 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 4 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 4 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 5 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 5 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 5 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 5 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 5 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 5 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 5 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 5 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 6 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 6 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 6 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 6 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 6 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 6 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 6 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 6 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 7 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 7 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 7 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 7 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 7 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 7 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 7 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 7 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 8 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 8 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 8 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 8 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 8 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 8 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 8 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 8 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 9 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 9 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 9 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 9 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 9 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 9 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 9 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 9 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 10 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 10 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 10 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 10 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 10 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 10 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 10 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 10 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 11 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 11 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 11 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 11 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 11 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 11 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 11 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 11 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 12 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 12 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 12 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 12 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 12 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 12 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 12 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 12 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 13 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 13 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 13 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 13 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 13 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 13 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 13 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 13 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 14 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 14 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 14 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 14 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 14 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 14 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 14 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 14 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 15 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 15 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 15 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 15 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 15 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 15 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 15 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 15 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 16 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 16 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 16 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 16 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 16 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 16 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 16 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 16 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 17 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 17 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 17 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 17 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 17 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 17 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 17 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 17 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 18 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 18 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 18 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 18 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 18 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 18 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 18 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 18 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 19 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 19 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 19 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 19 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 19 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 19 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 19 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 19 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 20 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 20 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 20 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 20 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 20 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 20 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 20 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 20 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 21 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 21 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 21 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 21 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 21 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 21 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 21 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 21 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 22 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 22 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 22 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 22 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 22 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 22 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 22 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 22 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 23 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 23 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 23 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 23 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 23 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 23 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 23 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 23 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
102 | 24 | 1 | Variable | Base | Data Type | Set variable type. | Analog (1215), Digital (1220) | Analog (1215) | UINT | R/W | 24 | Yes
102 | 24 | 2 | Variable | Base | Digital | Set the digital value when the type is digital. | On (63), Off (62) | Off (62) | UINT | R/W | 24 | Yes
102 | 24 | 3 | Variable | Base | Analog | Set the analog value when type is analog. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
102 | 24 | 4 | Variable | Base | Output Value | Monitor the variable output value. |  |  | REAL | R | 24 | Yes
102 | 24 | 5 | Variable | Base | Error |  | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) | None (61) | UINT | R/W | 24 | No
102 | 24 | 6 | Variable | Base | Analog |  | -3.4e38 to 3.4e38 | 0.0 | REAL | R/W | 24 | No
102 | 24 | 7 | Variable | Base | Units | Set the units assigned for analog stored value. | Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538), None (61) | Absolute Temperature (1540) | UINT | R/W | 24 | Yes
102 | 24 | 10 | Variable | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 24 | No
103 | 1 | 5 | Display | Base | Display Units | Set display units for touchscreen. | F (30), C (15) | F (30) | UINT | R/W | 1 | Yes
103 | 1 | 25 | Display | Base | Display Units |  | F (30), C (15) | F (30) | UINT | R/W | 1 | No
103 | 1 | 37 | Display | Base | Language |  | English (255), German (256), French (257), Italian (258), Spanish (259) | English (255) | UINT | R/W | 1 | No
112 | 1 | 2 | Limit | 1 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | REAL | R/W | 51 | Yes
112 | 1 | 3 | Limit | 1 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | REAL | R/W | 51 | Yes
112 | 1 | 4 | Limit | 1 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | REAL | R/W | 51 | Yes
112 | 1 | 5 | Limit | 1 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 51 | Yes
112 | 1 | 6 | Limit | 1 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | UINT | R | 51 | Yes
112 | 1 | 7 | Limit | 1 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | UINT | R | 51 | Yes
112 | 1 | 9 | Limit | 1 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | REAL | R/W | 51 | Yes
112 | 1 | 10 | Limit | 1 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | REAL | R/W | 51 | Yes
112 | 1 | 11 | Limit | 1 | Low Limit Set Point |  |  |  | REAL | R | 51 | No
112 | 1 | 12 | Limit | 1 | High Limit Set Point |  |  |  | REAL | R | 51 | No
112 | 1 | 13 | Limit | 1 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | UINT | R | 51 | No
112 | 1 | 14 | Limit | 1 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 51 | Yes
112 | 1 | 15 | Limit | 1 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | UINT | R/W | 51 | No
112 | 1 | 16 | Limit | 1 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | USINT | R/W | 51 | No
112 | 1 | 17 | Limit | 1 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | USINT | R/W | 51 | No
112 | 1 | 18 | Limit | 1 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | UINT | R | 51 | No
112 | 1 | 19 | Limit | 1 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | UINT | R/W | 51 | No
112 | 1 | 20 | Limit | 1 | Source Instance B | Set the source Instance for the Limit sensor. | 1 to 1 | 1 | USINT | R/W | 51 | No
112 | 1 | 21 | Limit | 1 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | USINT | R/W | 51 | No
112 | 1 | 22 | Limit | 1 | Source Value B | Monitor the IN receiver source value. |  |  | REAL | R | 51 | No
112 | 1 | 25 | Limit | 1 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 51 | No
112 | 1 | 26 | Limit | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
112 | 11 | 2 | Limit | 2 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | REAL | R/W | 51 | Yes
112 | 11 | 3 | Limit | 2 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | REAL | R/W | 51 | Yes
112 | 11 | 4 | Limit | 2 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | REAL | R/W | 51 | Yes
112 | 11 | 5 | Limit | 2 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 51 | Yes
112 | 11 | 6 | Limit | 2 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | UINT | R | 51 | Yes
112 | 11 | 7 | Limit | 2 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | UINT | R | 51 | Yes
112 | 11 | 9 | Limit | 2 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | REAL | R/W | 51 | Yes
112 | 11 | 10 | Limit | 2 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | REAL | R/W | 51 | Yes
112 | 11 | 11 | Limit | 2 | Low Limit Set Point |  |  |  | REAL | R | 51 | No
112 | 11 | 12 | Limit | 2 | High Limit Set Point |  |  |  | REAL | R | 51 | No
112 | 11 | 13 | Limit | 2 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | UINT | R | 51 | No
112 | 11 | 14 | Limit | 2 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 51 | Yes
112 | 11 | 15 | Limit | 2 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | UINT | R/W | 51 | No
112 | 11 | 16 | Limit | 2 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | USINT | R/W | 51 | No
112 | 11 | 17 | Limit | 2 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | USINT | R/W | 51 | No
112 | 11 | 18 | Limit | 2 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | UINT | R | 51 | No
112 | 11 | 19 | Limit | 2 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | UINT | R/W | 51 | No
112 | 11 | 20 | Limit | 2 | Source Instance B | Set the source Instance for the Limit sensor. | 11 to 11 | 11 | USINT | R/W | 51 | No
112 | 11 | 21 | Limit | 2 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | USINT | R/W | 51 | No
112 | 11 | 22 | Limit | 2 | Source Value B | Monitor the IN receiver source value. |  |  | REAL | R | 51 | No
112 | 11 | 25 | Limit | 2 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 51 | No
112 | 11 | 26 | Limit | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
112 | 21 | 2 | Limit | 3 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | REAL | R/W | 51 | Yes
112 | 21 | 3 | Limit | 3 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | REAL | R/W | 51 | Yes
112 | 21 | 4 | Limit | 3 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | REAL | R/W | 51 | Yes
112 | 21 | 5 | Limit | 3 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 51 | Yes
112 | 21 | 6 | Limit | 3 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | UINT | R | 51 | Yes
112 | 21 | 7 | Limit | 3 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | UINT | R | 51 | Yes
112 | 21 | 9 | Limit | 3 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | REAL | R/W | 51 | Yes
112 | 21 | 10 | Limit | 3 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | REAL | R/W | 51 | Yes
112 | 21 | 11 | Limit | 3 | Low Limit Set Point |  |  |  | REAL | R | 51 | No
112 | 21 | 12 | Limit | 3 | High Limit Set Point |  |  |  | REAL | R | 51 | No
112 | 21 | 13 | Limit | 3 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | UINT | R | 51 | No
112 | 21 | 14 | Limit | 3 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 51 | Yes
112 | 21 | 15 | Limit | 3 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | UINT | R/W | 51 | No
112 | 21 | 16 | Limit | 3 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | USINT | R/W | 51 | No
112 | 21 | 17 | Limit | 3 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | USINT | R/W | 51 | No
112 | 21 | 18 | Limit | 3 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | UINT | R | 51 | No
112 | 21 | 19 | Limit | 3 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | UINT | R/W | 51 | No
112 | 21 | 20 | Limit | 3 | Source Instance B | Set the source Instance for the Limit sensor. | 21 to 21 | 21 | USINT | R/W | 51 | No
112 | 21 | 21 | Limit | 3 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | USINT | R/W | 51 | No
112 | 21 | 22 | Limit | 3 | Source Value B | Monitor the IN receiver source value. |  |  | REAL | R | 51 | No
112 | 21 | 25 | Limit | 3 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 51 | No
112 | 21 | 26 | Limit | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
112 | 31 | 2 | Limit | 4 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | REAL | R/W | 51 | Yes
112 | 31 | 3 | Limit | 4 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | REAL | R/W | 51 | Yes
112 | 31 | 4 | Limit | 4 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | REAL | R/W | 51 | Yes
112 | 31 | 5 | Limit | 4 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 51 | Yes
112 | 31 | 6 | Limit | 4 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | UINT | R | 51 | Yes
112 | 31 | 7 | Limit | 4 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | UINT | R | 51 | Yes
112 | 31 | 9 | Limit | 4 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | REAL | R/W | 51 | Yes
112 | 31 | 10 | Limit | 4 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | REAL | R/W | 51 | Yes
112 | 31 | 11 | Limit | 4 | Low Limit Set Point |  |  |  | REAL | R | 51 | No
112 | 31 | 12 | Limit | 4 | High Limit Set Point |  |  |  | REAL | R | 51 | No
112 | 31 | 13 | Limit | 4 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | UINT | R | 51 | No
112 | 31 | 14 | Limit | 4 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 51 | Yes
112 | 31 | 15 | Limit | 4 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | UINT | R/W | 51 | No
112 | 31 | 16 | Limit | 4 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | USINT | R/W | 51 | No
112 | 31 | 17 | Limit | 4 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | USINT | R/W | 51 | No
112 | 31 | 18 | Limit | 4 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | UINT | R | 51 | No
112 | 31 | 19 | Limit | 4 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | UINT | R/W | 51 | No
112 | 31 | 20 | Limit | 4 | Source Instance B | Set the source Instance for the Limit sensor. | 31 to 31 | 31 | USINT | R/W | 51 | No
112 | 31 | 21 | Limit | 4 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | USINT | R/W | 51 | No
112 | 31 | 22 | Limit | 4 | Source Value B | Monitor the IN receiver source value. |  |  | REAL | R | 51 | No
112 | 31 | 25 | Limit | 4 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 51 | No
112 | 31 | 26 | Limit | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
112 | 41 | 2 | Limit | 5 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | REAL | R/W | 51 | Yes
112 | 41 | 3 | Limit | 5 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | REAL | R/W | 51 | Yes
112 | 41 | 4 | Limit | 5 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | REAL | R/W | 51 | Yes
112 | 41 | 5 | Limit | 5 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 51 | Yes
112 | 41 | 6 | Limit | 5 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | UINT | R | 51 | Yes
112 | 41 | 7 | Limit | 5 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | UINT | R | 51 | Yes
112 | 41 | 9 | Limit | 5 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | REAL | R/W | 51 | Yes
112 | 41 | 10 | Limit | 5 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | REAL | R/W | 51 | Yes
112 | 41 | 11 | Limit | 5 | Low Limit Set Point |  |  |  | REAL | R | 51 | No
112 | 41 | 12 | Limit | 5 | High Limit Set Point |  |  |  | REAL | R | 51 | No
112 | 41 | 13 | Limit | 5 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | UINT | R | 51 | No
112 | 41 | 14 | Limit | 5 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 51 | Yes
112 | 41 | 15 | Limit | 5 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | UINT | R/W | 51 | No
112 | 41 | 16 | Limit | 5 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | USINT | R/W | 51 | No
112 | 41 | 17 | Limit | 5 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | USINT | R/W | 51 | No
112 | 41 | 18 | Limit | 5 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | UINT | R | 51 | No
112 | 41 | 19 | Limit | 5 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | UINT | R/W | 51 | No
112 | 41 | 20 | Limit | 5 | Source Instance B | Set the source Instance for the Limit sensor. | 41 to 41 | 41 | USINT | R/W | 51 | No
112 | 41 | 21 | Limit | 5 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | USINT | R/W | 51 | No
112 | 41 | 22 | Limit | 5 | Source Value B | Monitor the IN receiver source value. |  |  | REAL | R | 51 | No
112 | 41 | 25 | Limit | 5 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 51 | No
112 | 41 | 26 | Limit | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
112 | 51 | 2 | Limit | 6 | Hysteresis | Set the Limit Hysteresis value before reset may occur. | 0.001 to 9,999.000 | 3.0 | REAL | R/W | 51 | Yes
112 | 51 | 3 | Limit | 6 | Low Limit Set Point | Set the Low Limit Set Point that causes the limit to trip. |  | 0.0 | REAL | R/W | 51 | Yes
112 | 51 | 4 | Limit | 6 | High Limit Set Point | Set the High Limit Set Point that causes the limit to trip. |  | 0.0 | REAL | R/W | 51 | Yes
112 | 51 | 5 | Limit | 6 | Sides | Set the Limit Sides. | Both (13), High (37), Low (53) | Both (13) | UINT | R/W | 51 | Yes
112 | 51 | 6 | Limit | 6 | Limit State | Monitor the Limit State. | Off (62), None (61), Limit High (51), Limit Low (52), Error (28) |  | UINT | R | 51 | Yes
112 | 51 | 7 | Limit | 6 | Output Value | Monitor the Limit Output Value. | On (63), Off (62) |  | UINT | R | 51 | Yes
112 | 51 | 9 | Limit | 6 | Maximum Set Point | Set the Maximum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | 99,999.0 | REAL | R/W | 51 | Yes
112 | 51 | 10 | Limit | 6 | Minimum Set Point | Set the Minimum Set Point that may be entered by user. | -99,999.0 to 99,999.0 | -99,999.0 | REAL | R/W | 51 | Yes
112 | 51 | 11 | Limit | 6 | Low Limit Set Point |  |  |  | REAL | R | 51 | No
112 | 51 | 12 | Limit | 6 | High Limit Set Point |  |  |  | REAL | R | 51 | No
112 | 51 | 13 | Limit | 6 | Limit Status | Monitor the Limit Status. | Fail (32), Safe (1667) |  | UINT | R | 51 | No
112 | 51 | 14 | Limit | 6 | Clear Limit | Request the Limit to be reset when tripped. | Clear (129), Ignore (204) | Ignore (204) | UINT | R/W | 51 | Yes
112 | 51 | 15 | Limit | 6 | Source Function A | Set the RST source receiver for the Limit reset. | None (61), Digital I/O (1142), Function Key (1001), Variable (245) | None (61) | UINT | R/W | 51 | No
112 | 51 | 16 | Limit | 6 | Source Instance A | Set the RST source Instance receiver for the Limit reset. | 1 to 250 | 1 | USINT | R/W | 51 | No
112 | 51 | 17 | Limit | 6 | Source Zone A | Set the RST zone receiver of source for the Limit reset. | 0 to 24 | 0 | USINT | R/W | 51 | No
112 | 51 | 18 | Limit | 6 | Source Value A | Monitor the reset source Value. | On (63), Off (62) |  | UINT | R | 51 | No
112 | 51 | 19 | Limit | 6 | Source Function B | Set the Source for the Limit sensor. | Analog Input (142) | Analog Input (142) | UINT | R/W | 51 | No
112 | 51 | 20 | Limit | 6 | Source Instance B | Set the source Instance for the Limit sensor. | 51 to 51 | 51 | USINT | R/W | 51 | No
112 | 51 | 21 | Limit | 6 | Source Zone B | Set the Zone for the Limit sensor. | 0 to 0 | 0 | USINT | R/W | 51 | No
112 | 51 | 22 | Limit | 6 | Source Value B | Monitor the IN receiver source value. |  |  | REAL | R | 51 | No
112 | 51 | 25 | Limit | 6 | Error | Monitor for Limit Errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 51 | No
112 | 51 | 26 | Limit | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
115 | 1 | 1 | Current | 1 | Current Read | Monitor current of S&H transmitter. |  |  | REAL | R | 51 | Yes
115 | 1 | 2 | Current | 1 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | UINT | R | 51 | Yes
115 | 1 | 3 | Current | 1 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | UINT | R | 51 | Yes
115 | 1 | 4 | Current | 1 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | UINT | R/W | 51 | Yes
115 | 1 | 5 | Current | 1 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | UINT | R/W | 51 | Yes
115 | 1 | 7 | Current | 1 | Load Current RMS | Monitor current of CUR transmitter. |  |  | REAL | R | 51 | Yes
115 | 1 | 8 | Current | 1 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | REAL | R/W | 51 | Yes
115 | 1 | 9 | Current | 1 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
115 | 1 | 10 | Current | 1 | Current Gain | Monitor the Gain setting. |  | 0.17 | REAL | R | 51 | No
115 | 1 | 11 | Current | 1 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
115 | 1 | 12 | Current | 1 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | UINT | R/W | 51 | No
115 | 1 | 13 | Current | 1 | Current Open Detect Point |  |  |  | UDINT | R | 51 | No
115 | 1 | 14 | Current | 1 | Current Short Detect Point |  |  |  | UDINT | R | 51 | No
115 | 1 | 16 | Current | 1 | Current Expected On Cycles |  |  |  | UDINT | R | 51 | No
115 | 1 | 17 | Current | 1 | Current Conducted Waves |  |  |  | UDINT | R | 51 | No
115 | 1 | 18 | Current | 1 | Current Measurement Period |  |  |  | UDINT | R | 51 | No
115 | 1 | 19 | Current | 1 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | USINT | R/W | 51 | Yes
115 | 1 | 20 | Current | 1 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | REAL | R | 51 | No
115 | 1 | 21 | Current | 1 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | UINT | R | 51 | No
115 | 1 | 22 | Current | 1 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | REAL | R/W | 51 | Yes
115 | 1 | 37 | Current | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
115 | 11 | 1 | Current | 2 | Current Read | Monitor current of S&H transmitter. |  |  | REAL | R | 51 | Yes
115 | 11 | 2 | Current | 2 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | UINT | R | 51 | Yes
115 | 11 | 3 | Current | 2 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | UINT | R | 51 | Yes
115 | 11 | 4 | Current | 2 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | UINT | R/W | 51 | Yes
115 | 11 | 5 | Current | 2 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | UINT | R/W | 51 | Yes
115 | 11 | 7 | Current | 2 | Load Current RMS | Monitor current of CUR transmitter. |  |  | REAL | R | 51 | Yes
115 | 11 | 8 | Current | 2 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | REAL | R/W | 51 | Yes
115 | 11 | 9 | Current | 2 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
115 | 11 | 10 | Current | 2 | Current Gain | Monitor the Gain setting. |  | 0.17 | REAL | R | 51 | No
115 | 11 | 11 | Current | 2 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
115 | 11 | 12 | Current | 2 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | UINT | R/W | 51 | No
115 | 11 | 13 | Current | 2 | Current Open Detect Point |  |  |  | UDINT | R | 51 | No
115 | 11 | 14 | Current | 2 | Current Short Detect Point |  |  |  | UDINT | R | 51 | No
115 | 11 | 16 | Current | 2 | Current Expected On Cycles |  |  |  | UDINT | R | 51 | No
115 | 11 | 17 | Current | 2 | Current Conducted Waves |  |  |  | UDINT | R | 51 | No
115 | 11 | 18 | Current | 2 | Current Measurement Period |  |  |  | UDINT | R | 51 | No
115 | 11 | 19 | Current | 2 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | USINT | R/W | 51 | Yes
115 | 11 | 20 | Current | 2 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | REAL | R | 51 | No
115 | 11 | 21 | Current | 2 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | UINT | R | 51 | No
115 | 11 | 22 | Current | 2 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | REAL | R/W | 51 | Yes
115 | 11 | 37 | Current | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
115 | 21 | 1 | Current | 3 | Current Read | Monitor current of S&H transmitter. |  |  | REAL | R | 51 | Yes
115 | 21 | 2 | Current | 3 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | UINT | R | 51 | Yes
115 | 21 | 3 | Current | 3 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | UINT | R | 51 | Yes
115 | 21 | 4 | Current | 3 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | UINT | R/W | 51 | Yes
115 | 21 | 5 | Current | 3 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | UINT | R/W | 51 | Yes
115 | 21 | 7 | Current | 3 | Load Current RMS | Monitor current of CUR transmitter. |  |  | REAL | R | 51 | Yes
115 | 21 | 8 | Current | 3 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | REAL | R/W | 51 | Yes
115 | 21 | 9 | Current | 3 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
115 | 21 | 10 | Current | 3 | Current Gain | Monitor the Gain setting. |  | 0.17 | REAL | R | 51 | No
115 | 21 | 11 | Current | 3 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
115 | 21 | 12 | Current | 3 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | UINT | R/W | 51 | No
115 | 21 | 13 | Current | 3 | Current Open Detect Point |  |  |  | UDINT | R | 51 | No
115 | 21 | 14 | Current | 3 | Current Short Detect Point |  |  |  | UDINT | R | 51 | No
115 | 21 | 16 | Current | 3 | Current Expected On Cycles |  |  |  | UDINT | R | 51 | No
115 | 21 | 17 | Current | 3 | Current Conducted Waves |  |  |  | UDINT | R | 51 | No
115 | 21 | 18 | Current | 3 | Current Measurement Period |  |  |  | UDINT | R | 51 | No
115 | 21 | 19 | Current | 3 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | USINT | R/W | 51 | Yes
115 | 21 | 20 | Current | 3 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | REAL | R | 51 | No
115 | 21 | 21 | Current | 3 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | UINT | R | 51 | No
115 | 21 | 22 | Current | 3 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | REAL | R/W | 51 | Yes
115 | 21 | 37 | Current | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
115 | 31 | 1 | Current | 4 | Current Read | Monitor current of S&H transmitter. |  |  | REAL | R | 51 | Yes
115 | 31 | 2 | Current | 4 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | UINT | R | 51 | Yes
115 | 31 | 3 | Current | 4 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | UINT | R | 51 | Yes
115 | 31 | 4 | Current | 4 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | UINT | R/W | 51 | Yes
115 | 31 | 5 | Current | 4 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | UINT | R/W | 51 | Yes
115 | 31 | 7 | Current | 4 | Load Current RMS | Monitor current of CUR transmitter. |  |  | REAL | R | 51 | Yes
115 | 31 | 8 | Current | 4 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | REAL | R/W | 51 | Yes
115 | 31 | 9 | Current | 4 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
115 | 31 | 10 | Current | 4 | Current Gain | Monitor the Gain setting. |  | 0.17 | REAL | R | 51 | No
115 | 31 | 11 | Current | 4 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
115 | 31 | 12 | Current | 4 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | UINT | R/W | 51 | No
115 | 31 | 13 | Current | 4 | Current Open Detect Point |  |  |  | UDINT | R | 51 | No
115 | 31 | 14 | Current | 4 | Current Short Detect Point |  |  |  | UDINT | R | 51 | No
115 | 31 | 16 | Current | 4 | Current Expected On Cycles |  |  |  | UDINT | R | 51 | No
115 | 31 | 17 | Current | 4 | Current Conducted Waves |  |  |  | UDINT | R | 51 | No
115 | 31 | 18 | Current | 4 | Current Measurement Period |  |  |  | UDINT | R | 51 | No
115 | 31 | 19 | Current | 4 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | USINT | R/W | 51 | Yes
115 | 31 | 20 | Current | 4 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | REAL | R | 51 | No
115 | 31 | 21 | Current | 4 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | UINT | R | 51 | No
115 | 31 | 22 | Current | 4 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | REAL | R/W | 51 | Yes
115 | 31 | 37 | Current | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
115 | 41 | 1 | Current | 5 | Current Read | Monitor current of S&H transmitter. |  |  | REAL | R | 51 | Yes
115 | 41 | 2 | Current | 5 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | UINT | R | 51 | Yes
115 | 41 | 3 | Current | 5 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | UINT | R | 51 | Yes
115 | 41 | 4 | Current | 5 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | UINT | R/W | 51 | Yes
115 | 41 | 5 | Current | 5 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | UINT | R/W | 51 | Yes
115 | 41 | 7 | Current | 5 | Load Current RMS | Monitor current of CUR transmitter. |  |  | REAL | R | 51 | Yes
115 | 41 | 8 | Current | 5 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | REAL | R/W | 51 | Yes
115 | 41 | 9 | Current | 5 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
115 | 41 | 10 | Current | 5 | Current Gain | Monitor the Gain setting. |  | 0.17 | REAL | R | 51 | No
115 | 41 | 11 | Current | 5 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
115 | 41 | 12 | Current | 5 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | UINT | R/W | 51 | No
115 | 41 | 13 | Current | 5 | Current Open Detect Point |  |  |  | UDINT | R | 51 | No
115 | 41 | 14 | Current | 5 | Current Short Detect Point |  |  |  | UDINT | R | 51 | No
115 | 41 | 16 | Current | 5 | Current Expected On Cycles |  |  |  | UDINT | R | 51 | No
115 | 41 | 17 | Current | 5 | Current Conducted Waves |  |  |  | UDINT | R | 51 | No
115 | 41 | 18 | Current | 5 | Current Measurement Period |  |  |  | UDINT | R | 51 | No
115 | 41 | 19 | Current | 5 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | USINT | R/W | 51 | Yes
115 | 41 | 20 | Current | 5 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | REAL | R | 51 | No
115 | 41 | 21 | Current | 5 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | UINT | R | 51 | No
115 | 41 | 22 | Current | 5 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | REAL | R/W | 51 | Yes
115 | 41 | 37 | Current | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
115 | 51 | 1 | Current | 6 | Current Read | Monitor current of S&H transmitter. |  |  | REAL | R | 51 | Yes
115 | 51 | 2 | Current | 6 | Current Error | Monitor the most recent load fault. | None (61), Shorted (127), Open (65) | None (61) | UINT | R | 51 | Yes
115 | 51 | 3 | Current | 6 | Heater Error | Monitor if load current flow is within the High and Low Set Points. | None (61), High (37), Low (53) | None (61) | UINT | R | 51 | Yes
115 | 51 | 4 | Current | 6 | Indicate Reading | Set Indicate Reading to display solid-state relay (SSR) failure and heater failure messages. | No (59), Yes (106) | No (59) | UINT | R/W | 51 | Yes
115 | 51 | 5 | Current | 6 | Sides | Set which side or sides will be monitored. | Off (62), High (37), Low (53), Both (13) | Off (62) | UINT | R/W | 51 | Yes
115 | 51 | 7 | Current | 6 | Load Current RMS | Monitor current of CUR transmitter. |  |  | REAL | R | 51 | Yes
115 | 51 | 8 | Current | 6 | High Set Point | Set the current value that will trigger a high heater error state. | -99,999.0 to 99,999.0 | 50.0 | REAL | R/W | 51 | Yes
115 | 51 | 9 | Current | 6 | Low Set Point | Set the current value that will trigger a low heater error state. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
115 | 51 | 10 | Current | 6 | Current Gain | Monitor the Gain setting. |  | 0.17 | REAL | R | 51 | No
115 | 51 | 11 | Current | 6 | Heater Offset | Set the current reading with an offset value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 51 | Yes
115 | 51 | 12 | Current | 6 | Detection Threshold | Do not change without factory input. | 3 to 59 | 9 | UINT | R/W | 51 | No
115 | 51 | 13 | Current | 6 | Current Open Detect Point |  |  |  | UDINT | R | 51 | No
115 | 51 | 14 | Current | 6 | Current Short Detect Point |  |  |  | UDINT | R | 51 | No
115 | 51 | 16 | Current | 6 | Current Expected On Cycles |  |  |  | UDINT | R | 51 | No
115 | 51 | 17 | Current | 6 | Current Conducted Waves |  |  |  | UDINT | R | 51 | No
115 | 51 | 18 | Current | 6 | Current Measurement Period |  |  |  | UDINT | R | 51 | No
115 | 51 | 19 | Current | 6 | Monitored Output | Set which output is controlling heater monitored by CT input. | 1 to 250 | 1 | USINT | R/W | 51 | Yes
115 | 51 | 20 | Current | 6 | Current Actual Power | Monitor PID power applied by monitored output. |  |  | REAL | R | 51 | No
115 | 51 | 21 | Current | 6 | Current Input Error Status | Monitor current for error. | None (61), Fail (32) |  | UINT | R | 51 | No
115 | 51 | 22 | Current | 6 | Input Scaling | Set scaling to match the transformer's high range. | 0 to 99,999.0 | 50.0 | REAL | R/W | 51 | Yes
115 | 51 | 37 | Current | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 51 | No
118 | 1 | 1 | Analog Output | 1 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 1 | 2 | Analog Output | 1 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 1 | 4 | Analog Output | 1 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 1 | 5 | Analog Output | 1 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 1 | 6 | Analog Output | 1 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 1 | 7 | Analog Output | 1 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 1 | 8 | Analog Output | 1 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 1 | 9 | Analog Output | 1 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 1 | 10 | Analog Output | 1 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 1 | 11 | Analog Output | 1 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 1 | 12 | Analog Output | 1 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 1 | 15 | Analog Output | 1 | Counts |  |  |  | UINT | R | 53 | No
118 | 1 | 16 | Analog Output | 1 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 1 | 17 | Analog Output | 1 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 1 | 18 | Analog Output | 1 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 1 | 19 | Analog Output | 1 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 1 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 1 | 25 | Analog Output | 1 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 2 | 1 | Analog Output | 1 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 2 | 2 | Analog Output | 1 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 2 | 4 | Analog Output | 1 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 2 | 5 | Analog Output | 1 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 2 | 6 | Analog Output | 1 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 2 | 7 | Analog Output | 1 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 2 | 8 | Analog Output | 1 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 2 | 9 | Analog Output | 1 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 2 | 10 | Analog Output | 1 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 2 | 11 | Analog Output | 1 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 2 | 12 | Analog Output | 1 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 2 | 15 | Analog Output | 1 | Counts |  |  |  | UINT | R | 53 | No
118 | 2 | 16 | Analog Output | 1 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 2 | 17 | Analog Output | 1 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 2 | 18 | Analog Output | 1 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 2 | 19 | Analog Output | 1 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 2 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 2 | 25 | Analog Output | 1 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 3 | 1 | Analog Output | 1 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 3 | 2 | Analog Output | 1 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 3 | 4 | Analog Output | 1 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 3 | 5 | Analog Output | 1 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 3 | 6 | Analog Output | 1 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 3 | 7 | Analog Output | 1 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 3 | 8 | Analog Output | 1 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 3 | 9 | Analog Output | 1 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 3 | 10 | Analog Output | 1 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 3 | 11 | Analog Output | 1 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 3 | 12 | Analog Output | 1 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 3 | 15 | Analog Output | 1 | Counts |  |  |  | UINT | R | 53 | No
118 | 3 | 16 | Analog Output | 1 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 3 | 17 | Analog Output | 1 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 3 | 18 | Analog Output | 1 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 3 | 19 | Analog Output | 1 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 3 | 24 | Analog Output | 1 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 3 | 25 | Analog Output | 1 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 11 | 1 | Analog Output | 2 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 11 | 2 | Analog Output | 2 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 11 | 4 | Analog Output | 2 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 11 | 5 | Analog Output | 2 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 11 | 6 | Analog Output | 2 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 11 | 7 | Analog Output | 2 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 11 | 8 | Analog Output | 2 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 11 | 9 | Analog Output | 2 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 11 | 10 | Analog Output | 2 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 11 | 11 | Analog Output | 2 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 11 | 12 | Analog Output | 2 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 11 | 15 | Analog Output | 2 | Counts |  |  |  | UINT | R | 53 | No
118 | 11 | 16 | Analog Output | 2 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 11 | 17 | Analog Output | 2 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 11 | 18 | Analog Output | 2 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 11 | 19 | Analog Output | 2 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 11 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 11 | 25 | Analog Output | 2 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 12 | 1 | Analog Output | 2 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 12 | 2 | Analog Output | 2 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 12 | 4 | Analog Output | 2 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 12 | 5 | Analog Output | 2 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 12 | 6 | Analog Output | 2 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 12 | 7 | Analog Output | 2 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 12 | 8 | Analog Output | 2 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 12 | 9 | Analog Output | 2 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 12 | 10 | Analog Output | 2 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 12 | 11 | Analog Output | 2 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 12 | 12 | Analog Output | 2 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 12 | 15 | Analog Output | 2 | Counts |  |  |  | UINT | R | 53 | No
118 | 12 | 16 | Analog Output | 2 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 12 | 17 | Analog Output | 2 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 12 | 18 | Analog Output | 2 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 12 | 19 | Analog Output | 2 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 12 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 12 | 25 | Analog Output | 2 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 13 | 1 | Analog Output | 2 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 13 | 2 | Analog Output | 2 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 13 | 4 | Analog Output | 2 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 13 | 5 | Analog Output | 2 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 13 | 6 | Analog Output | 2 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 13 | 7 | Analog Output | 2 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 13 | 8 | Analog Output | 2 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 13 | 9 | Analog Output | 2 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 13 | 10 | Analog Output | 2 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 13 | 11 | Analog Output | 2 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 13 | 12 | Analog Output | 2 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 13 | 15 | Analog Output | 2 | Counts |  |  |  | UINT | R | 53 | No
118 | 13 | 16 | Analog Output | 2 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 13 | 17 | Analog Output | 2 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 13 | 18 | Analog Output | 2 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 13 | 19 | Analog Output | 2 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 13 | 24 | Analog Output | 2 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 13 | 25 | Analog Output | 2 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 21 | 1 | Analog Output | 3 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 21 | 2 | Analog Output | 3 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 21 | 4 | Analog Output | 3 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 21 | 5 | Analog Output | 3 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 21 | 6 | Analog Output | 3 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 21 | 7 | Analog Output | 3 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 21 | 8 | Analog Output | 3 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 21 | 9 | Analog Output | 3 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 21 | 10 | Analog Output | 3 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 21 | 11 | Analog Output | 3 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 21 | 12 | Analog Output | 3 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 21 | 15 | Analog Output | 3 | Counts |  |  |  | UINT | R | 53 | No
118 | 21 | 16 | Analog Output | 3 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 21 | 17 | Analog Output | 3 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 21 | 18 | Analog Output | 3 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 21 | 19 | Analog Output | 3 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 21 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 21 | 25 | Analog Output | 3 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 22 | 1 | Analog Output | 3 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 22 | 2 | Analog Output | 3 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 22 | 4 | Analog Output | 3 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 22 | 5 | Analog Output | 3 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 22 | 6 | Analog Output | 3 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 22 | 7 | Analog Output | 3 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 22 | 8 | Analog Output | 3 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 22 | 9 | Analog Output | 3 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 22 | 10 | Analog Output | 3 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 22 | 11 | Analog Output | 3 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 22 | 12 | Analog Output | 3 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 22 | 15 | Analog Output | 3 | Counts |  |  |  | UINT | R | 53 | No
118 | 22 | 16 | Analog Output | 3 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 22 | 17 | Analog Output | 3 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 22 | 18 | Analog Output | 3 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 22 | 19 | Analog Output | 3 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 22 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 22 | 25 | Analog Output | 3 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 23 | 1 | Analog Output | 3 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 23 | 2 | Analog Output | 3 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 23 | 4 | Analog Output | 3 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 23 | 5 | Analog Output | 3 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 23 | 6 | Analog Output | 3 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 23 | 7 | Analog Output | 3 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 23 | 8 | Analog Output | 3 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 23 | 9 | Analog Output | 3 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 23 | 10 | Analog Output | 3 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 23 | 11 | Analog Output | 3 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 23 | 12 | Analog Output | 3 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 23 | 15 | Analog Output | 3 | Counts |  |  |  | UINT | R | 53 | No
118 | 23 | 16 | Analog Output | 3 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 23 | 17 | Analog Output | 3 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 23 | 18 | Analog Output | 3 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 23 | 19 | Analog Output | 3 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 23 | 24 | Analog Output | 3 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 23 | 25 | Analog Output | 3 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 31 | 1 | Analog Output | 4 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 31 | 2 | Analog Output | 4 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 31 | 4 | Analog Output | 4 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 31 | 5 | Analog Output | 4 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 31 | 6 | Analog Output | 4 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 31 | 7 | Analog Output | 4 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 31 | 8 | Analog Output | 4 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 31 | 9 | Analog Output | 4 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 31 | 10 | Analog Output | 4 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 31 | 11 | Analog Output | 4 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 31 | 12 | Analog Output | 4 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 31 | 15 | Analog Output | 4 | Counts |  |  |  | UINT | R | 53 | No
118 | 31 | 16 | Analog Output | 4 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 31 | 17 | Analog Output | 4 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 31 | 18 | Analog Output | 4 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 31 | 19 | Analog Output | 4 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 31 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 31 | 25 | Analog Output | 4 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 32 | 1 | Analog Output | 4 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 32 | 2 | Analog Output | 4 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 32 | 4 | Analog Output | 4 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 32 | 5 | Analog Output | 4 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 32 | 6 | Analog Output | 4 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 32 | 7 | Analog Output | 4 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 32 | 8 | Analog Output | 4 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 32 | 9 | Analog Output | 4 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 32 | 10 | Analog Output | 4 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 32 | 11 | Analog Output | 4 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 32 | 12 | Analog Output | 4 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 32 | 15 | Analog Output | 4 | Counts |  |  |  | UINT | R | 53 | No
118 | 32 | 16 | Analog Output | 4 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 32 | 17 | Analog Output | 4 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 32 | 18 | Analog Output | 4 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 32 | 19 | Analog Output | 4 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 32 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 32 | 25 | Analog Output | 4 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 33 | 1 | Analog Output | 4 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 33 | 2 | Analog Output | 4 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 33 | 4 | Analog Output | 4 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 33 | 5 | Analog Output | 4 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 33 | 6 | Analog Output | 4 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 33 | 7 | Analog Output | 4 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 33 | 8 | Analog Output | 4 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 33 | 9 | Analog Output | 4 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 33 | 10 | Analog Output | 4 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 33 | 11 | Analog Output | 4 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 33 | 12 | Analog Output | 4 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 33 | 15 | Analog Output | 4 | Counts |  |  |  | UINT | R | 53 | No
118 | 33 | 16 | Analog Output | 4 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 33 | 17 | Analog Output | 4 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 33 | 18 | Analog Output | 4 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 33 | 19 | Analog Output | 4 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 33 | 24 | Analog Output | 4 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 33 | 25 | Analog Output | 4 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 41 | 1 | Analog Output | 5 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 41 | 2 | Analog Output | 5 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 41 | 4 | Analog Output | 5 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 41 | 5 | Analog Output | 5 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 41 | 6 | Analog Output | 5 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 41 | 7 | Analog Output | 5 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 41 | 8 | Analog Output | 5 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 41 | 9 | Analog Output | 5 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 41 | 10 | Analog Output | 5 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 41 | 11 | Analog Output | 5 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 41 | 12 | Analog Output | 5 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 41 | 15 | Analog Output | 5 | Counts |  |  |  | UINT | R | 53 | No
118 | 41 | 16 | Analog Output | 5 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 41 | 17 | Analog Output | 5 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 41 | 18 | Analog Output | 5 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 41 | 19 | Analog Output | 5 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 41 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 41 | 25 | Analog Output | 5 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 42 | 1 | Analog Output | 5 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 42 | 2 | Analog Output | 5 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 42 | 4 | Analog Output | 5 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 42 | 5 | Analog Output | 5 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 42 | 6 | Analog Output | 5 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 42 | 7 | Analog Output | 5 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 42 | 8 | Analog Output | 5 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 42 | 9 | Analog Output | 5 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 42 | 10 | Analog Output | 5 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 42 | 11 | Analog Output | 5 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 42 | 12 | Analog Output | 5 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 42 | 15 | Analog Output | 5 | Counts |  |  |  | UINT | R | 53 | No
118 | 42 | 16 | Analog Output | 5 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 42 | 17 | Analog Output | 5 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 42 | 18 | Analog Output | 5 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 42 | 19 | Analog Output | 5 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 42 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 42 | 25 | Analog Output | 5 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 43 | 1 | Analog Output | 5 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 43 | 2 | Analog Output | 5 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 43 | 4 | Analog Output | 5 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 43 | 5 | Analog Output | 5 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 43 | 6 | Analog Output | 5 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 43 | 7 | Analog Output | 5 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 43 | 8 | Analog Output | 5 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 43 | 9 | Analog Output | 5 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 43 | 10 | Analog Output | 5 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 43 | 11 | Analog Output | 5 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 43 | 12 | Analog Output | 5 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 43 | 15 | Analog Output | 5 | Counts |  |  |  | UINT | R | 53 | No
118 | 43 | 16 | Analog Output | 5 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 43 | 17 | Analog Output | 5 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 43 | 18 | Analog Output | 5 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 43 | 19 | Analog Output | 5 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 43 | 24 | Analog Output | 5 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 43 | 25 | Analog Output | 5 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 51 | 1 | Analog Output | 6 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 51 | 2 | Analog Output | 6 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 51 | 4 | Analog Output | 6 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 51 | 5 | Analog Output | 6 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 51 | 6 | Analog Output | 6 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 51 | 7 | Analog Output | 6 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 51 | 8 | Analog Output | 6 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 51 | 9 | Analog Output | 6 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 51 | 10 | Analog Output | 6 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 51 | 11 | Analog Output | 6 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 51 | 12 | Analog Output | 6 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 51 | 15 | Analog Output | 6 | Counts |  |  |  | UINT | R | 53 | No
118 | 51 | 16 | Analog Output | 6 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 51 | 17 | Analog Output | 6 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 51 | 18 | Analog Output | 6 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 51 | 19 | Analog Output | 6 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 51 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 51 | 25 | Analog Output | 6 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 52 | 1 | Analog Output | 6 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 52 | 2 | Analog Output | 6 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 52 | 4 | Analog Output | 6 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 52 | 5 | Analog Output | 6 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 52 | 6 | Analog Output | 6 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 52 | 7 | Analog Output | 6 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 52 | 8 | Analog Output | 6 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 52 | 9 | Analog Output | 6 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 52 | 10 | Analog Output | 6 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 52 | 11 | Analog Output | 6 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 52 | 12 | Analog Output | 6 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 52 | 15 | Analog Output | 6 | Counts |  |  |  | UINT | R | 53 | No
118 | 52 | 16 | Analog Output | 6 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 52 | 17 | Analog Output | 6 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 52 | 18 | Analog Output | 6 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 52 | 19 | Analog Output | 6 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 52 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 52 | 25 | Analog Output | 6 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
118 | 53 | 1 | Analog Output | 6 | Output Type | Set whether the physical analog output supplies a voltage or current signal. | Volts (104), Milliamps (112) | Volts (104) | UINT | R/W | 53 | Yes
118 | 53 | 2 | Analog Output | 6 | Function | Set source that drives output. | Off (62), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | Off (62) | UINT | R/W | 53 | No
118 | 53 | 4 | Analog Output | 6 | Output Function Instance | Set source instance that drives output. | 1 to 250 | 1 | USINT | R/W | 53 | No
118 | 53 | 5 | Analog Output | 6 | Electrical Output Offset | Set an electrical offset value for a process output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | No
118 | 53 | 6 | Analog Output | 6 | Electrical Output Slope | Set the electrical slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 53 | 7 | Analog Output | 6 | Calibration Offset | Set the units output offset for calibration. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 53 | 8 | Analog Output | 6 | Calibration Slope | Set the units slope for calibration. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 53 | No
118 | 53 | 9 | Analog Output | 6 | Scale Low | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range Low setting. | -100.0 to 100.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 53 | 10 | Analog Output | 6 | Scale High | Set the desired value for the output in electrical units (mA DC or VDC) when the input to the block equals the Range High setting. | -100.0 to 100.0 | 10.0 | REAL | R/W | 53 | Yes
118 | 53 | 11 | Analog Output | 6 | Range Low | Set the value for the input to the block at which the Scale Low setting is the desired output value. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 53 | Yes
118 | 53 | 12 | Analog Output | 6 | Range High | Set the value for the input to the block at which the Scale High setting is the desired output value. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 53 | Yes
118 | 53 | 15 | Analog Output | 6 | Counts |  |  |  | UINT | R | 53 | No
118 | 53 | 16 | Analog Output | 6 | Analog Output Electrical Value | Monitor the electrical value produced by the output. |  |  | REAL | R | 53 | No
118 | 53 | 17 | Analog Output | 6 | Analog Output Control Operation | Do not change without factory input. | Electrical (1276), Counts (1037) | Electrical (1276) | UINT | R/W | 53 | No
118 | 53 | 18 | Analog Output | 6 | Source Value A | Monitor the source value driving the output. |  |  | REAL | R | 53 | No
118 | 53 | 19 | Analog Output | 6 | Source Zone A | Set the Zone for the source driving this output. | 0 to 24 | 0 | USINT | R/W | 53 | No
118 | 53 | 24 | Analog Output | 6 | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 53 | No
118 | 53 | 25 | Analog Output | 6 | Output Type | Monitor the output type. | 2 (1), 3 (2) |  | UINT | R | 53 | No
119 | 1 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 2 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 3 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 4 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 5 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 6 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 7 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 8 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 9 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 10 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 11 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 12 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 13 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 14 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 15 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 16 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 17 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 18 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 19 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 20 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 21 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 22 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 23 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 24 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 26 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 27 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 28 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 29 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 30 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 31 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 32 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 33 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 34 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 35 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 36 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 37 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 38 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 39 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 40 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 41 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 42 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 43 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 44 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 45 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 46 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 47 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 48 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 49 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 50 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 51 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 52 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 53 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 54 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 55 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 56 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 57 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 58 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 59 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 60 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 61 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 62 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 63 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 64 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 65 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 66 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 67 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 68 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 69 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 70 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 71 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 72 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 73 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 74 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 75 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 76 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 77 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 78 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 79 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 80 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 81 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 82 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 83 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 84 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 85 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 86 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 87 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 88 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 89 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 90 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 91 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 92 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 93 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 94 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 95 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 96 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 97 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 98 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 99 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 100 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 101 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 102 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 103 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 104 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 105 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 106 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 107 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 108 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 109 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 110 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 111 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 112 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 113 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 114 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 115 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 116 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 117 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 118 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 119 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 120 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 121 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 122 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 123 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 1 | 124 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 1 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 2 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 3 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 4 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 5 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 6 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 7 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 8 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 9 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 10 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 11 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 12 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 13 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 14 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 15 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 16 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 17 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 18 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 19 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 20 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 21 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 22 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 23 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 24 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 25 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 26 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 27 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 28 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 29 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 30 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 31 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 32 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 33 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 34 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 35 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 36 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 37 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 38 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 39 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 40 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 41 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 42 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 43 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 44 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 45 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 46 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 47 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 48 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 49 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 50 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 51 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 52 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 53 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 54 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 55 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 56 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 57 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 58 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 59 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 60 | Assembly Setup | Base | Member | Register to place pointer used in Modbus Settable Memory Block. | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 61 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 62 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 63 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 64 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 65 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 66 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 67 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 68 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 69 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 70 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 71 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 72 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 73 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 74 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 75 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 76 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 77 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 78 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 79 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 80 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 81 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 82 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 83 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 84 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 85 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 86 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 87 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 88 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 89 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 90 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 91 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 92 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 93 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 94 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 95 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 96 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 97 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 98 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 99 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 100 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 101 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 102 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 103 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 104 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 105 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 106 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 107 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 108 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 109 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 110 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 111 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 112 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 113 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 114 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 115 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 116 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 117 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 118 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 119 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 120 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 121 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 122 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 123 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
119 | 25 | 124 | Assembly Setup | Base | Member |  | 3 to 3 | 1, 1, 255 | Struct of 8-bit CIA | R/W | 2 | No
120 | 1 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 2 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 3 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 4 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 5 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 6 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 7 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 8 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 9 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 10 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 11 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 12 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 13 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 14 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 15 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 16 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 17 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 18 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 19 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 20 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 21 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 22 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 23 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 24 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 26 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 27 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 28 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 29 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 30 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 31 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 32 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 33 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 34 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 35 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 36 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 37 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 38 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 39 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 40 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 41 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 42 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 43 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 44 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 45 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 46 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 47 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 48 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 49 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 50 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 51 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 52 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 53 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 54 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 55 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 56 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 57 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 58 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 59 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 60 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 61 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 62 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 63 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 64 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 65 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 66 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 67 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 68 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 69 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 70 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 71 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 72 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 73 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 74 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 75 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 76 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 77 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 78 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 79 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 80 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 81 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 82 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 83 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 84 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 85 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 86 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 87 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 88 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 89 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 90 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 91 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 92 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 93 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 94 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 95 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 96 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 97 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 98 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 99 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 100 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 101 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 102 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 103 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 104 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 105 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 106 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 107 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 108 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 109 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 110 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 111 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 112 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 113 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 114 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 115 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 116 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 117 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 118 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 119 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 120 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 121 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 122 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 123 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 1 | 124 | Assembly | Base |  |  | 1 to 1 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 1 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 2 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 3 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 4 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 5 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 6 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 7 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 8 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 9 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 10 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 11 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 12 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 13 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 14 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 15 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 16 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 17 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 18 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 19 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 20 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 21 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 22 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 23 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 24 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 25 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 26 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 27 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 28 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 29 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 30 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 31 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 32 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 33 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 34 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 35 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 36 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 37 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 38 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 39 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 40 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 41 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 42 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 43 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 44 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 45 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 46 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 47 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 48 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 49 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 50 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 51 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 52 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 53 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 54 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 55 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 56 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 57 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 58 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 59 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 60 | Assembly | Base |  | Register to place data from point used in Modbus Settable Memory Block | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 61 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 62 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 63 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 64 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 65 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 66 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 67 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 68 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 69 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 70 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 71 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 72 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 73 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 74 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 75 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 76 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 77 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 78 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 79 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 80 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 81 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 82 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 83 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 84 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 85 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 86 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 87 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 88 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 89 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 90 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 91 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 92 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 93 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 94 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 95 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 96 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 97 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 98 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 99 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 100 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 101 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 102 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 103 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 104 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 105 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 106 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 107 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 108 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 109 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 110 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 111 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 112 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 113 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 114 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 115 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 116 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 117 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 118 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 119 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 120 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 121 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 122 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 123 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
120 | 25 | 124 | Assembly | Base |  |  | 25 to 25 | Default of Parameter Pointer | Data from Parameter Pointer | Access of Parameter Pointer | 2 | No
125 | 1 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 1 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 1 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 1 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 1 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 1 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 1 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 1 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 1 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 1 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 1 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 1 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 1 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 1 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 1 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 1 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 1 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 1 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 1 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 1 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 1 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 1 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 1 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 1 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 1 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 1 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 1 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 1 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 1 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 1 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 1 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 1 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 2 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 2 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 2 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 2 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 2 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 2 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 2 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 2 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 2 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 2 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 2 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 2 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 2 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 2 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 2 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 2 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 2 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 2 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 2 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 2 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 2 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 2 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 2 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 2 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 2 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 2 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 2 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 2 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 2 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 2 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 2 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 2 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 3 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 3 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 3 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 3 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 3 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 3 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 3 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 3 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 3 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 3 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 3 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 3 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 3 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 3 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 3 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 3 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 3 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 3 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 3 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 3 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 3 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 3 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 3 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 3 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 3 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 3 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 3 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 3 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 3 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 3 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 3 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 3 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 4 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 4 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 4 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 4 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 4 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 4 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 4 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 4 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 4 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 4 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 4 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 4 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 4 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 4 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 4 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 4 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 4 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 4 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 4 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 4 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 4 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 4 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 4 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 4 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 4 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 4 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 4 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 4 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 4 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 4 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 4 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 4 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 5 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 5 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 5 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 5 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 5 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 5 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 5 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 5 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 5 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 5 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 5 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 5 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 5 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 5 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 5 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 5 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 5 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 5 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 5 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 5 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 5 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 5 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 5 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 5 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 5 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 5 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 5 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 5 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 5 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 5 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 5 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 5 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 6 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 6 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 6 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 6 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 6 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 6 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 6 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 6 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 6 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 6 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 6 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 6 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 6 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 6 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 6 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 6 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 6 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 6 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 6 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 6 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 6 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 6 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 6 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 6 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 6 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 6 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 6 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 6 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 6 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 6 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 6 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 6 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 7 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 7 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 7 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 7 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 7 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 7 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 7 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 7 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 7 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 7 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 7 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 7 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 7 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 7 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 7 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 7 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 7 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 7 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 7 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 7 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 7 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 7 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 7 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 7 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 7 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 7 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 7 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 7 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 7 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 7 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 7 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 7 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 8 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 8 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 8 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 8 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 8 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 8 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 8 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 8 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 8 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 8 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 8 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 8 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 8 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 8 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 8 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 8 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 8 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 8 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 8 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 8 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 8 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 8 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 8 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 8 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 8 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 8 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 8 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 8 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 8 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 8 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 8 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 8 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 9 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 9 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 9 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 9 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 9 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 9 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 9 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 9 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 9 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 9 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 9 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 9 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 9 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 9 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 9 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 9 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 9 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 9 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 9 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 9 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 9 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 9 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 9 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 9 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 9 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 9 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 9 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 9 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 9 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 9 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 9 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 9 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 10 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 10 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 10 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 10 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 10 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 10 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 10 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 10 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 10 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 10 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 10 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 10 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 10 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 10 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 10 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 10 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 10 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 10 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 10 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 10 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 10 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 10 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 10 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 10 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 10 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 10 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 10 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 10 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 10 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 10 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 10 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 10 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 11 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 11 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 11 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 11 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 11 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 11 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 11 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 11 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 11 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 11 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 11 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 11 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 11 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 11 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 11 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 11 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 11 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 11 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 11 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 11 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 11 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 11 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 11 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 11 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 11 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 11 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 11 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 11 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 11 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 11 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 11 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 11 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 12 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 12 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 12 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 12 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 12 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 12 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 12 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 12 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 12 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 12 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 12 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 12 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 12 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 12 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 12 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 12 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 12 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 12 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 12 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 12 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 12 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 12 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 12 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 12 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 12 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 12 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 12 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 12 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 12 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 12 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 12 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 12 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 13 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 13 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 13 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 13 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 13 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 13 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 13 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 13 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 13 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 13 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 13 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 13 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 13 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 13 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 13 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 13 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 13 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 13 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 13 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 13 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 13 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 13 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 13 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 13 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 13 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 13 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 13 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 13 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 13 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 13 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 13 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 13 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 14 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 14 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 14 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 14 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 14 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 14 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 14 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 14 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 14 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 14 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 14 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 14 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 14 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 14 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 14 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 14 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 14 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 14 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 14 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 14 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 14 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 14 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 14 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 14 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 14 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 14 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 14 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 14 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 14 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 14 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 14 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 14 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 15 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 15 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 15 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 15 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 15 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 15 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 15 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 15 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 15 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 15 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 15 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 15 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 15 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 15 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 15 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 15 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 15 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 15 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 15 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 15 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 15 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 15 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 15 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 15 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 15 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 15 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 15 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 15 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 15 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 15 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 15 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 15 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 16 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 16 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 16 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 16 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 16 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 16 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 16 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 16 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 16 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 16 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 16 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 16 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 16 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 16 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 16 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 16 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 16 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 16 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 16 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 16 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 16 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 16 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 16 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 16 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 16 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 16 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 16 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 16 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 16 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 16 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 16 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 16 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 17 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 17 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 17 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 17 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 17 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 17 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 17 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 17 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 17 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 17 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 17 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 17 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 17 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 17 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 17 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 17 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 17 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 17 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 17 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 17 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 17 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 17 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 17 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 17 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 17 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 17 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 17 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 17 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 17 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 17 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 17 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 17 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 18 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 18 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 18 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 18 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 18 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 18 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 18 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 18 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 18 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 18 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 18 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 18 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 18 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 18 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 18 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 18 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 18 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 18 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 18 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 18 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 18 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 18 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 18 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 18 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 18 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 18 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 18 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 18 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 18 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 18 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 18 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 18 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 19 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 19 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 19 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 19 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 19 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 19 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 19 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 19 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 19 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 19 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 19 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 19 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 19 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 19 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 19 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 19 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 19 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 19 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 19 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 19 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 19 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 19 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 19 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 19 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 19 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 19 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 19 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 19 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 19 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 19 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 19 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 19 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 20 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 20 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 20 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 20 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 20 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 20 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 20 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 20 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 20 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 20 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 20 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 20 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 20 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 20 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 20 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 20 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 20 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 20 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 20 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 20 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 20 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 20 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 20 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 20 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 20 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 20 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 20 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 20 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 20 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 20 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 20 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 20 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 21 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 21 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 21 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 21 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 21 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 21 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 21 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 21 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 21 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 21 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 21 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 21 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 21 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 21 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 21 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 21 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 21 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 21 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 21 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 21 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 21 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 21 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 21 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 21 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 21 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 21 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 21 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 21 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 21 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 21 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 21 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 21 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 22 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 22 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 22 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 22 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 22 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 22 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 22 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 22 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 22 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 22 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 22 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 22 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 22 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 22 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 22 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 22 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 22 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 22 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 22 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 22 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 22 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 22 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 22 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 22 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 22 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 22 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 22 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 22 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 22 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 22 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 22 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 22 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 23 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 23 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 23 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 23 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 23 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 23 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 23 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 23 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 23 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 23 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 23 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 23 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 23 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 23 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 23 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 23 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 23 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 23 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 23 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 23 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 23 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 23 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 23 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 23 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 23 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 23 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 23 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 23 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 23 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 23 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 23 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 23 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
125 | 24 | 1 | Math | Base | Source Function A | Set the Source A for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 24 | 2 | Math | Base | Source Function B | Set the Source B for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 24 | 3 | Math | Base | Source Function C | Set the Source C for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 24 | 4 | Math | Base | Source Function D | Set the Source D for the receiver in the Math block. | None (61), Analog Input (142), Current (22), Cool Power (161), Heat Power (160), Power (73), Linearization (238), Math (240), Process Value (241), Set Point Closed (242), Set Point Open (243), Variable (245), Condition (10001), Encoder (1740), Profile Number (1779), Cascade Cool Power (1795), Cascade Heat Power (1794), Cascade Power (1796), Cascade Set Point Closed (1797), Cascade Set Point Open (1798) | None (61) | UINT | R/W | 24 | No
125 | 24 | 5 | Math | Base | Source Function E | Set the Source E for the receiver in the Math block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
125 | 24 | 6 | Math | Base | Source Instance A | Set the Source Instance A for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 24 | 7 | Math | Base | Source Instance B | Set the Source Instance B for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 24 | 8 | Math | Base | Source Instance C | Set the Source Instance C for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 24 | 9 | Math | Base | Source Instance D | Set the Source Instance D for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 24 | 10 | Math | Base | Source Instance E | Set the Source Instance E for the receiver in the Math block. | 1 to 250 | 1 | USINT | R/W | 24 | No
125 | 24 | 11 | Math | Base | Source Zone A | Set the Source Zone A for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 24 | 12 | Math | Base | Source Zone B | Set the Source Zone B for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 24 | 13 | Math | Base | Source Zone C | Set the Source Zone C for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 24 | 14 | Math | Base | Source Zone D | Set the Source Zone D for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 24 | 15 | Math | Base | Source Zone E | Set the Source Zone E for the receiver in the Math block. | 0 to 24 | 0 | USINT | R/W | 24 | No
125 | 24 | 16 | Math | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 24 | No
125 | 24 | 17 | Math | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 24 | No
125 | 24 | 18 | Math | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 24 | No
125 | 24 | 19 | Math | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 24 | No
125 | 24 | 20 | Math | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) | None | UINT | R | 24 | No
125 | 24 | 21 | Math | Base | Function | Set the Function of the Math block. | Off (62), Average (1367), Process Scale (1371), Deviation Scale (1372), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Sample and Hold (1381), Pressure to Altitude (1649), Dew Point (1650) | Off (62) | UINT | R/W | 24 | Yes
125 | 24 | 22 | Math | Base | Output Value | Monitor the output value of the Math block. |  |  | REAL | R | 24 | Yes
125 | 24 | 23 | Math | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 24 | 24 | Math | Base | Scale Low | Set the value of input X at which the Range Low setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 24 | 25 | Math | Base | Scale High | Set the value of input X at which the Range High setting is the desired result of scaling. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 24 | 26 | Math | Base | Range Low | Set the desired result of scaling at the point where input X equals the Scale Low setting. Or Set the value of input X at which the Low Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 24 | 27 | Math | Base | Range High | Set the desired result of scaling at the point where input X equals the Scale High setting. Or Set the value of input X at which the High Range setting plus the DEV value is the desired output. | -99,999.0 to 99,999.0 | 1.0 | REAL | R/W | 24 | Yes
125 | 24 | 28 | Math | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 24 | Yes
125 | 24 | 29 | Math | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
125 | 24 | 30 | Math | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 24 | Yes
125 | 24 | 31 | Math | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 24 | Yes
125 | 24 | 32 | Math | Base | Units | Set the source units. | Source (1539), None (61), Absolute Temperature (1540), Relative Temperature (1541), Power (73), Process (75), Relative Humidity (1538) | Source (1539) | UINT | R/W | 24 | Yes
126 | 1 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 1 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 1 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 1 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 1 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 8 | No
126 | 1 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 1 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 1 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 1 | 9 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 1 | 10 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 1 | 11 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 1 | 12 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 1 | 13 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 1 | 14 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 1 | 15 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 1 | 16 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 8 | No
126 | 1 | 17 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 8 | No
126 | 1 | 18 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 8 | No
126 | 1 | 19 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 8 | No
126 | 1 | 20 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 8 | No
126 | 1 | 21 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | UINT | R/W | 8 | Yes
126 | 1 | 22 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | REAL | R | 8 | Yes
126 | 1 | 23 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
126 | 1 | 24 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 8 | Yes
126 | 1 | 25 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | REAL | R/W | 8 | Yes
126 | 1 | 26 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 8 | Yes
126 | 1 | 27 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 8 | No
126 | 1 | 28 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 8 | Yes
126 | 1 | 29 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 8 | Yes
126 | 1 | 30 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | REAL | R/W | 8 | Yes
126 | 1 | 33 | Process Value | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 8 | No
126 | 2 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 2 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 2 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 2 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 2 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 8 | No
126 | 2 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 2 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 2 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 2 | 9 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 2 | 10 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 2 | 11 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 2 | 12 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 2 | 13 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 2 | 14 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 2 | 15 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 2 | 16 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 8 | No
126 | 2 | 17 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 8 | No
126 | 2 | 18 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 8 | No
126 | 2 | 19 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 8 | No
126 | 2 | 20 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 8 | No
126 | 2 | 21 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | UINT | R/W | 8 | Yes
126 | 2 | 22 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | REAL | R | 8 | Yes
126 | 2 | 23 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
126 | 2 | 24 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 8 | Yes
126 | 2 | 25 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | REAL | R/W | 8 | Yes
126 | 2 | 26 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 8 | Yes
126 | 2 | 27 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 8 | No
126 | 2 | 28 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 8 | Yes
126 | 2 | 29 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 8 | Yes
126 | 2 | 30 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | REAL | R/W | 8 | Yes
126 | 2 | 33 | Process Value | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 8 | No
126 | 3 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 3 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 3 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 3 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 3 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 8 | No
126 | 3 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 3 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 3 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 3 | 9 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 3 | 10 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 3 | 11 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 3 | 12 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 3 | 13 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 3 | 14 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 3 | 15 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 3 | 16 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 8 | No
126 | 3 | 17 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 8 | No
126 | 3 | 18 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 8 | No
126 | 3 | 19 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 8 | No
126 | 3 | 20 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 8 | No
126 | 3 | 21 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | UINT | R/W | 8 | Yes
126 | 3 | 22 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | REAL | R | 8 | Yes
126 | 3 | 23 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
126 | 3 | 24 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 8 | Yes
126 | 3 | 25 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | REAL | R/W | 8 | Yes
126 | 3 | 26 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 8 | Yes
126 | 3 | 27 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 8 | No
126 | 3 | 28 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 8 | Yes
126 | 3 | 29 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 8 | Yes
126 | 3 | 30 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | REAL | R/W | 8 | Yes
126 | 3 | 33 | Process Value | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 8 | No
126 | 4 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 4 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 4 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 4 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 4 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 8 | No
126 | 4 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 4 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 4 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 4 | 9 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 4 | 10 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 4 | 11 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 4 | 12 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 4 | 13 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 4 | 14 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 4 | 15 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 4 | 16 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 8 | No
126 | 4 | 17 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 8 | No
126 | 4 | 18 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 8 | No
126 | 4 | 19 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 8 | No
126 | 4 | 20 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 8 | No
126 | 4 | 21 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | UINT | R/W | 8 | Yes
126 | 4 | 22 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | REAL | R | 8 | Yes
126 | 4 | 23 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
126 | 4 | 24 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 8 | Yes
126 | 4 | 25 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | REAL | R/W | 8 | Yes
126 | 4 | 26 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 8 | Yes
126 | 4 | 27 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 8 | No
126 | 4 | 28 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 8 | Yes
126 | 4 | 29 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 8 | Yes
126 | 4 | 30 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | REAL | R/W | 8 | Yes
126 | 4 | 33 | Process Value | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 8 | No
126 | 5 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 5 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 5 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 5 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 5 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 8 | No
126 | 5 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 5 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 5 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 5 | 9 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 5 | 10 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 5 | 11 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 5 | 12 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 5 | 13 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 5 | 14 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 5 | 15 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 5 | 16 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 8 | No
126 | 5 | 17 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 8 | No
126 | 5 | 18 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 8 | No
126 | 5 | 19 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 8 | No
126 | 5 | 20 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 8 | No
126 | 5 | 21 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | UINT | R/W | 8 | Yes
126 | 5 | 22 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | REAL | R | 8 | Yes
126 | 5 | 23 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
126 | 5 | 24 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 8 | Yes
126 | 5 | 25 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | REAL | R/W | 8 | Yes
126 | 5 | 26 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 8 | Yes
126 | 5 | 27 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 8 | No
126 | 5 | 28 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 8 | Yes
126 | 5 | 29 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 8 | Yes
126 | 5 | 30 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | REAL | R/W | 8 | Yes
126 | 5 | 33 | Process Value | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 8 | No
126 | 6 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 6 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 6 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 6 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 6 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 8 | No
126 | 6 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 6 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 6 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 6 | 9 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 6 | 10 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 6 | 11 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 6 | 12 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 6 | 13 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 6 | 14 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 6 | 15 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 6 | 16 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 8 | No
126 | 6 | 17 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 8 | No
126 | 6 | 18 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 8 | No
126 | 6 | 19 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 8 | No
126 | 6 | 20 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 8 | No
126 | 6 | 21 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | UINT | R/W | 8 | Yes
126 | 6 | 22 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | REAL | R | 8 | Yes
126 | 6 | 23 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
126 | 6 | 24 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 8 | Yes
126 | 6 | 25 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | REAL | R/W | 8 | Yes
126 | 6 | 26 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 8 | Yes
126 | 6 | 27 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 8 | No
126 | 6 | 28 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 8 | Yes
126 | 6 | 29 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 8 | Yes
126 | 6 | 30 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | REAL | R/W | 8 | Yes
126 | 6 | 33 | Process Value | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 8 | No
126 | 7 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 7 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 7 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 7 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 7 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 8 | No
126 | 7 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 7 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 7 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 7 | 9 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 7 | 10 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 7 | 11 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 7 | 12 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 7 | 13 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 7 | 14 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 7 | 15 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 7 | 16 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 8 | No
126 | 7 | 17 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 8 | No
126 | 7 | 18 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 8 | No
126 | 7 | 19 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 8 | No
126 | 7 | 20 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 8 | No
126 | 7 | 21 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | UINT | R/W | 8 | Yes
126 | 7 | 22 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | REAL | R | 8 | Yes
126 | 7 | 23 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
126 | 7 | 24 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 8 | Yes
126 | 7 | 25 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | REAL | R/W | 8 | Yes
126 | 7 | 26 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 8 | Yes
126 | 7 | 27 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 8 | No
126 | 7 | 28 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 8 | Yes
126 | 7 | 29 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 8 | Yes
126 | 7 | 30 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | REAL | R/W | 8 | Yes
126 | 7 | 33 | Process Value | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 8 | No
126 | 8 | 1 | Process Value | Base | Source Function A | Set the Source A for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 8 | 2 | Process Value | Base | Source Function B | Set the Source B for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 8 | 3 | Process Value | Base | Source Function C | Set the Source C for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 8 | 4 | Process Value | Base | Source Function D | Set the Source D for the receiver in the Process Value block. | None (61), Analog Input (142), Linearization (238), Math (240), Process Value (241), Variable (245) | None (61) | UINT | R/W | 8 | No
126 | 8 | 5 | Process Value | Base | Source Function E | Set the Source E for the receiver in the Process Value block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Logic (239), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 8 | No
126 | 8 | 6 | Process Value | Base | Source Instance A | Set the Source Instance A for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 8 | 7 | Process Value | Base | Source Instance B | Set the Source Instance B for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 8 | 8 | Process Value | Base | Source Instance C | Set the Source Instance C for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 8 | 9 | Process Value | Base | Source Instance D | Set the Source Instance D for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 8 | 10 | Process Value | Base | Source Instance E | Set the Source Instance E for the receiver in the Process Value block. | 1 to 250 | 1 | USINT | R/W | 8 | No
126 | 8 | 11 | Process Value | Base | Source Zone A | Set the Source Zone A for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 8 | 12 | Process Value | Base | Source Zone B | Set the Source Zone B for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 8 | 13 | Process Value | Base | Source Zone C | Set the Source Zone C for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 8 | 14 | Process Value | Base | Source Zone D | Set the Source Zone D for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 8 | 15 | Process Value | Base | Source Zone E | Set the Source Zone E for the receiver in the Process Value block. | 0 to 24 | 0 | USINT | R/W | 8 | No
126 | 8 | 16 | Process Value | Base | Source Value A | Monitor the Source Value A driving this receiver. |  |  | REAL | R | 8 | No
126 | 8 | 17 | Process Value | Base | Source Value B | Monitor the Source Value B driving this receiver. |  |  | REAL | R | 8 | No
126 | 8 | 18 | Process Value | Base | Source Value C | Monitor the Source Value C driving this receiver. |  |  | REAL | R | 8 | No
126 | 8 | 19 | Process Value | Base | Source Value D | Monitor the Source Value D driving this receiver. |  |  | REAL | R | 8 | No
126 | 8 | 20 | Process Value | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 8 | No
126 | 8 | 21 | Process Value | Base | Function | Set the Function of the Process Value block. | Off (62), Sensor Backup (1201), Average (1367), Crossover (1368), Wet Bulb / Dry Bulb (1369), Switch Over (1370), Differential (1373), Ratio (1374), Add (1375), Multiply (1376), Absolute Difference (1377), Minimum (1378), Maximum (1379), Square Root (1380), Vaisala RH Compensation (1648), Pressure to Altitude (1649) | Off (62) | UINT | R/W | 8 | Yes
126 | 8 | 22 | Process Value | Base | Output Value | Monitor the output value of the Process Value block. |  |  | REAL | R | 8 | Yes
126 | 8 | 23 | Process Value | Base | Offset | Set value added to the result of the calculation. | -99,999.0 to 99,999.0 | 0.0 | REAL | R/W | 8 | Yes
126 | 8 | 24 | Process Value | Base | Crossover Point | Set the middle of the band over which the function transitions between inputs A and B. | -99,999.0 to 99,999.0 | 100.0 | REAL | R/W | 8 | Yes
126 | 8 | 25 | Process Value | Base | Crossover Band | Set the width of the transition between input A and B. | -99,999.0 to 99,999.0 | 10.0 | REAL | R/W | 8 | Yes
126 | 8 | 26 | Process Value | Base | Filter | Set the amount of filtering to apply. | 0.0 to 60.0 | 0.0 | REAL | R/W | 8 | Yes
126 | 8 | 27 | Process Value | Base | Error | Monitor the Math block for input or calculation errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 8 | No
126 | 8 | 28 | Process Value | Base | Pressure Units | Set the units of pressure input. | PSI (1671), mbar (1672), Torr (1673), Pascal (1674), Atmosphere (1675) | PSI (1671) | UINT | R/W | 8 | Yes
126 | 8 | 29 | Process Value | Base | Altitude Units | Set the units for the altitude output. | Feet (1676), Kilofeet (1677) | Kilofeet (1677) | UINT | R/W | 8 | Yes
126 | 8 | 30 | Process Value | Base | Barometric Pressure | Set the units of the barometric output.. | 10.0 to 16.0 | 14.7 | REAL | R/W | 8 | Yes
126 | 8 | 33 | Process Value | Base | Name | Set name assigned to function block. | 20 bytes (UTF-8) |  | SHORT_STRING | R/W | 8 | No
127 | 1 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 1 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 1 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 1 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 1 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 1 | 6 | Logic | Base | Source Function F | Set the Source F for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 1 | 7 | Logic | Base | Source Function G | Set the Source G for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 1 | 8 | Logic | Base | Source Function H | Set the Source H for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 1 | 9 | Logic | Base | Source Instance A | Set the Source Instance A for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 1 | 10 | Logic | Base | Source Instance B | Set the Source Instance B for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 1 | 11 | Logic | Base | Source Instance C | Set the Source Instance C for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 1 | 12 | Logic | Base | Source Instance D | Set the Source Instance D for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 1 | 13 | Logic | Base | Source Instance E | Set the Source Instance E for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 1 | 14 | Logic | Base | Source Instance F | Set the Source Instance F for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 1 | 15 | Logic | Base | Source Instance G | Set the Source Instance G for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 1 | 16 | Logic | Base | Source Instance H | Set the Source Instance H for the receiver in the Logic block. | 1 to 250 | 1 | USINT | R/W | 24 | No
127 | 1 | 17 | Logic | Base | Source Zone A | Set the Source Zone A for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 1 | 18 | Logic | Base | Source Zone B | Set the Source Zone B for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 1 | 19 | Logic | Base | Source Zone C | Set the Source Zone C for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 1 | 20 | Logic | Base | Source Zone D | Set the Source Zone D for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 1 | 21 | Logic | Base | Source Zone E | Set the Source Zone E for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 1 | 22 | Logic | Base | Source Zone F | Set the Source Zone F for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 1 | 23 | Logic | Base | Source Zone G | Set the Source Zone G for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 1 | 24 | Logic | Base | Source Zone H | Set the Source Zone H for the receiver in the Logic block. | 0 to 24 | 0 | USINT | R/W | 24 | No
127 | 1 | 25 | Logic | Base | Source Value A | Monitor the Source Value A driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 1 | 26 | Logic | Base | Source Value B | Monitor the Source Value B driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 1 | 27 | Logic | Base | Source Value C | Monitor the Source Value C driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 1 | 28 | Logic | Base | Source Value D | Monitor the Source Value D driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 1 | 29 | Logic | Base | Source Value E | Monitor the Source Value E driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 1 | 30 | Logic | Base | Source Value F | Monitor the Source Value F driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 1 | 31 | Logic | Base | Source Value G | Monitor the Source Value G driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 1 | 32 | Logic | Base | Source Value H | Monitor the Source Value H driving this receiver. | On (63), Off (62) |  | UINT | R | 24 | No
127 | 1 | 33 | Logic | Base | Function | Set the Function of the Logic block. | Off (62), And (1426), Nand (1427), Or (1442), Nor (1443), Equal To (1437), Not Equal To (1438), Latch (1444), RS Flip Flop (1693) | Off (62) | UINT | R/W | 24 | Yes
127 | 1 | 34 | Logic | Base | Output Value | Monitor the output value of the Logic block. | On (63), Off (62) |  | UINT | R | 24 | Yes
127 | 1 | 35 | Logic | Base | Error Handling | Set Error Handling to select the output's value and error status when the function cannot definitively determine the result. | True Good (1476), True Bad (1477), False Good (1478), False Bad (1479) | False Bad (1479) | UINT | R/W | 24 | Yes
127 | 1 | 36 | Logic | Base | Error | Monitor the Logic block for input or logic errors. | None (61), Open (65), Shorted (127), Measurement Error (140), Bad Calibration Data (139), Ambient Error (9), RTD Error (141), Fail (32), Math Error (1423), Not Sourced (246), Stale (1617) |  | UINT | R | 24 | No
127 | 2 | 1 | Logic | Base | Source Function A | Set the Source A for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 2 | 2 | Logic | Base | Source Function B | Set the Source B for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 2 | 3 | Logic | Base | Source Function C | Set the Source C for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 2 | 4 | Logic | Base | Source Function D | Set the Source D for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No
127 | 2 | 5 | Logic | Base | Source Function E | Set the Source E for the receiver in the Logic block. | None (61), Alarm (6), Compare (230), Counter (231), Digital I/O (1142), Profile Event Out A (233), Profile Event Out B (234), Profile Event Out C (235), Profile Event Out D (236), Profile Event Out E (247), Profile Event Out F (248), Profile Event Out G (249), Profile Event Out H (250), Function Key (1001), Limit (126), Logic (239), Special Function Output 1 (1532), Special Function Output 2 (1533), Special Function Output 3 (1534), Special Function Output 4 (1535), Timer (244), Variable (245), Condition (10001), Profile Running (1780), Profile Paused (1781), Control Loop Control Mode Is Off (2120), Cascade Control Mode Is Off (2121) | None (61) | UINT | R/W | 24 | No